## Summary
File created by JSOLCHAGA on 6/20/2024 at 8:18:06 AM using Violations Posting Automator_v16.3.accdb.
PowerWorld Cases: | 23SSWG_2026_SUM1_U1_Final_10092023_v91
23SSWG_2027_MIN_U1_Final_10092023_v71
23SSWG_2027_SUM1_U1_Final_10092023_v93
23SSWG_2029_SUM1_U1_Final_10092023_v92
23SSWG_2030_SUM1_U1_Final_10092023_v96
23SSWG_2030_SUM1_U1_Final_10092023_v97_EHV_Option10

## Voltage Deviations
Owner | Zone | Bus | Contingency | kV | Category | 2026sum% | 2027min% | 2027sum% | 2029sum% | 2030sum% | 2030sum_EHV% | Notes
TAEPTC | SOUTHERN | ACME7A (81005) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Change Bus Low Volts | - | - | - | - | 9.5286 | - | -
TAEPTC | SOUTHERN | ACME7A (81005) | L_005915SO_TEX__345A-008715RADIANT7AC1 | 345 | Change Bus High Volts | - | - | - | - | 8.1223 | - | -
TAEPTC | SOUTHERN | ACME7A (81005) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Change Bus Low Volts | - | - | - | - | 8.113 | - | -
TAEPTC | SOUTHERN | ACME7A (81005) | L_008676STATIC7A-081003HABER7AC1 | 345 | Change Bus Low Volts | - | - | - | - | 8.8819 | - | -
TAEPTC | SOUTHERN | ACME7A (81005) | P7-1_E1>>T3944Z_ERC | 345 | Change Bus High Volts | - | - | - | - | 8.1345 | - | -
TONCOR | NORTH_CE | AIRLIQD_P8 (2283) | BEPC_306 | 138 | Change Bus Low Volts | - | 8.4438 | - | - | - | - | -
TONCOR | NORTH_CE | AIRLIQD_P8 (2283) | L_000442RAILPORT-001908VENUSC1 | 138 | Change Bus Low Volts | - | 8.002 | - | - | - | - | -
TONCOR | NORTH_CE | AIRLIQD_P8 (2283) | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | Change Bus Low Volts | - | 8.4967 | - | - | - | - | -
TBPUB | SOUTHERN | AIRPORT (59460) | E_NEDIN_CC1_TRAIN | 138 | Change Bus Low Volts | - | - | - | 8.2651 | - | - | -
TONCOR | NORTH_CE | AIRPRD1_8 (2306) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Change Bus Low Volts | - | 8.1729 | 10.0991 | - | - | - | -
TRAYBN | NORTH_CE | ALHUB_RC (6826) | L_002370COLLINSS1_8-002380WESTRIDGE1_8C1 | 138 | Change Bus Low Volts | 9.6263 | - | 9.3968 | - | - | 9.6436 | -
TONCOR | FAR_WEST | ANDRANCH_8 (1082) | L_011094RETONE_8-011189QUARRYFLD_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 9.0617 | 8.5133 | -
TONCOR | FAR_WEST | ANDRANCHT_8 (1081) | L_011094RETONE_8-011189QUARRYFLD_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 9.0617 | 8.5133 | -
TRAYBN | NORTH_CE | ANNA_RC (6819) | L_002340MELSSA_P8-002374ANNASW_8C1 | 138 | Change Bus Low Volts | 9.7354 | - | 8.8663 | - | 8.433 | 8.9178 | -
TRAYBN | NORTH_CE | ANNA_RC (6819) | L_002340MELSSA_P8-002704ANNASE_8C1 | 138 | Change Bus Low Volts | 8.647 | - | - | 9.23 | - | - | -
TONCOR | NORTH_CE | ANNASE_8 (2704) | L_002340MELSSA_P8-002374ANNASW_8C1 | 138 | Change Bus Low Volts | 9.7932 | - | 8.9175 | - | 8.4806 | 8.9685 | -
TONCOR | NORTH_CE | ANNASE_8 (2704) | L_002340MELSSA_P8-002704ANNASE_8C1 | 138 | Change Bus Low Volts | 8.7001 | - | - | 9.2852 | - | - | -
TONCOR | FAR_WEST | AQUIFER_8 (11377) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.8505 | - | -
TONCOR | NORTH_CE | ASHGRVE_8 (12313) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Change Bus Low Volts | - | - | - | 8.5282 | - | - | -
TONCOR | EAST | ATHENS_8 (3238) | L_003233NEWATHENS_8-003238ATHENS_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.8161 | - | -
TONCOR | SOUTH_CE | AVERY_8 (3517) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Change Bus Low Volts | - | - | - | 10.3021 | - | - | -
TAEPTN | FAR_WEST | BARL4A (6655) | L_006655BARL4A-060385SOLSTICE4AC1 | 138 | Change Bus Low Volts | 9.9763 | - | - | - | - | - | -
TONCOR | FAR_WEST | BARSTOWNW_8 (1086) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 10.9794 | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | Change Bus High Volts | - | - | 8.7831 | - | - | - | -
TONCOR | SOUTH_CE | BIRDNEST_8 (3661) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Change Bus Low Volts | - | - | - | 8.8733 | - | - | -
TONCOR | FAR_WEST | BLAIRLAKE_8 (11238) | L_011242CRTNYCRK_8-060792ATHEY4AC1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.5945 | -
TONCOR | FAR_WEST | BRECK_8 (11141) | L_011183TUNSTLL_8-011199RDRUNNER_T8C1 | 138 | Change Bus Low Volts | - | - | 8.5212 | - | - | - | -
TBTU | EAST | BRYN_KOPPE (32860) | L_032780BRYN_RELLIS-032853BRYN_SMETANAC1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.2992 | -
TBTU | EAST | BRYN_KOPPE (32860) | L_032878BRYN_GRNPRAI-032895BRYN_WBRN138C1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.3077 | -
TBTU | EAST | BRYN_SNOO138 (32857) | BRYN_9995DC | 138 | Change Bus Low Volts | - | - | 8.1321 | 8.3337 | - | - | -
TBTU | EAST | BRYN_WBRN138 (32895) | L_032878BRYN_GRNPRAI-032895BRYN_WBRN138C1 | 138 | Change Bus Low Volts | - | - | - | - | - | 9.604 | -
TONCOR | NORTH_CE | BRYNST2_8 (2908) | L_012442PARKD_2EN8-012446MDLTM2_8C1 | 138 | Change Bus Low Volts | 8.9732 | - | - | - | - | - | -
TONCOR | NORTH_CE | BRYNST2_8 (2908) | L_012446MDLTM2_8-012904ENETOH2_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.6544 | - | -
TAEPTC | SOUTHERN | CANDELA7A (8709) | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | Change Bus Low Volts | - | - | - | 8.1754 | - | - | -
TETRTX | SOUTHERN | CARVL4A (85010) | L_008458B_DAVIS4A-085010CARVL4AC1 | 138 | Change Bus Low Volts | - | - | - | - | 8.8217 | - | -
TAEPTN | FAR_WEST | CHERRYCR4A (60206) | L_060385SOLSTICE4A-060808HOEFSROA4AC1 | 138 | Change Bus Low Volts | - | - | 9.6393 | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_8 (2290) | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | Change Bus Low Volts | - | 9.0612 | - | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_8 (2290) | L_000442RAILPORT-001908VENUSC1 | 138 | Change Bus Low Volts | - | 9.0787 | - | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_N_8 (2280) | BEPC_306 | 138 | Change Bus Low Volts | - | 8.5504 | - | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_N_8 (2280) | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | Change Bus Low Volts | - | 8.0873 | - | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_N_8 (2280) | L_000442RAILPORT-001908VENUSC1 | 138 | Change Bus Low Volts | - | 8.1029 | - | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_N_8 (2280) | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | Change Bus Low Volts | - | 8.6037 | - | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_W_8 (2291) | BEPC_306 | 138 | Change Bus Low Volts | - | 8.8944 | - | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_W_8 (2291) | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | Change Bus Low Volts | - | 8.3965 | - | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_W_8 (2291) | L_000442RAILPORT-001908VENUSC1 | 138 | Change Bus Low Volts | - | 8.4126 | - | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_W_8 (2291) | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | Change Bus Low Volts | - | 8.9463 | - | - | - | - | -
TAEPTC | SOUTHERN | CLLCOTTE4A (8027) | L_008027CLLCOTTE4A-008452LON_HILL4AC1 | 138 | Change Bus Low Volts | 9.5014 | - | 9.5595 | - | - | - | -
TONCOR | FAR_WEST | COSDEN_8 (1332) | XFMR-RANGER_5 | 138 | Change Bus Low Volts | - | 8.6802 | - | - | - | - | -
TONCOR | NORTH_CE | COTTONWD_8 (2304) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Change Bus Low Volts | - | 8.2264 | 10.0256 | - | - | 10.5576 | -
TONCOR | FAR_WEST | COYANOSA_8 (1239) | L_011242CRTNYCRK_8-060792ATHEY4AC1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.3114 | -
TAEPTC | SOUTHERN | CRUNCH7A (81004) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Change Bus Low Volts | - | - | - | - | 9.4566 | - | -
TAEPTC | SOUTHERN | CRUNCH7A (81004) | L_005915SO_TEX__345A-008715RADIANT7AC1 | 345 | Change Bus High Volts | - | - | - | - | 8.0665 | - | -
TAEPTC | SOUTHERN | CRUNCH7A (81004) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Change Bus Low Volts | - | - | - | - | 8.0522 | - | -
TAEPTC | SOUTHERN | CRUNCH7A (81004) | L_008676STATIC7A-081003HABER7AC1 | 345 | Change Bus Low Volts | - | - | - | - | 8.8151 | - | -
TAEPTC | SOUTHERN | CRUNCH7A (81004) | L_081003HABER7A-081005ACME7AC1 | 345 | Change Bus High Volts | - | - | - | - | 13.4934 | - | -
TAEPTC | SOUTHERN | CRUNCH7A (81004) | P7-1_E1>>T3944Z_ERC | 345 | Change Bus High Volts | - | - | - | - | 8.0786 | - | -
TONCOR | NORTH_CE | DUBLIN1_8 (1636) | NEW-COMCHE-STEPHENVILLE (SINGLE B TO B ) B-1 | 138 | Change Bus Low Volts | - | - | - | - | 10.1884 | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_023834ELBOW_8-900100Other_131C1 | 138 | Change Bus High Volts | 10.9665 | 11.2994 | - | - | 8.1834 | - | -
TONCOR | NORTH_CE | ENETOH2_8 (12904) | L_012442PARKD_2EN8-012446MDLTM2_8C1 | 138 | Change Bus Low Volts | 8.9711 | - | - | - | - | - | -
TONCOR | NORTH_CE | ENETOH2_8 (12904) | L_012446MDLTM2_8-012904ENETOH2_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.6518 | - | -
TRAYBN | NORTH_CE | EPCO_RC (6890) | L_002370COLLINSS1_8-002380WESTRIDGE1_8C1 | 138 | Change Bus Low Volts | 8.431 | - | 8.2062 | 8.3029 | 8.2034 | 8.422 | -
TBPUB | SOUTHERN | FILTER_P (59420) | E_NEDIN_CC1_TRAIN | 138 | Change Bus Low Volts | - | - | - | 8.2079 | - | - | -
TBPUB | SOUTHERN | FM_802 (59400) | E_NEDIN_CC1_TRAIN | 138 | Change Bus Low Volts | - | - | - | 8.0513 | - | - | -
TONCOR | FAR_WEST | GENRUBR_8 (1053) | L_001027ODESEHV_8-001052REXALL_8C1 | 138 | Change Bus Low Volts | - | 8.2612 | 8.9827 | 9.7464 | 8.0886 | 8.3894 | -
TONCOR | FAR_WEST | GENRUBR_8 (1053) | L_001052REXALL_8-001053GENRUBR_8C1 | 138 | Change Bus Low Volts | - | - | 8.7383 | 9.2103 | - | - | -
RELLIS | NORTH_CE | GERDAU_8 (152285) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Change Bus Low Volts | - | 8.2261 | 10.0253 | - | - | 10.5572 | -
TONCOR | FAR_WEST | GLASSCNTYN_8 (1334) | L_001333MCDONALD_8-001334GLASSCNTYN_8C1 | 138 | Change Bus Low Volts | - | 9.0715 | - | 8.1179 | 8.0825 | - | -
TONCOR | NORTH_CE | GODLEY_8 (2281) | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | Change Bus Low Volts | - | - | 8.0122 | - | - | - | -
TONCOR | NORTH_CE | GODLEY_8 (2281) | L_000442RAILPORT-001908VENUSC1 | 138 | Change Bus Low Volts | - | - | 8.2364 | - | - | - | -
TLCRA | FAR_WEST | HAYTER4A (60444) | L_060385SOLSTICE4A-060444HAYTER4AC1 | 138 | Change Bus Low Volts | 11.1832 | - | - | - | - | - | -
TSTEC | SOUTHERN | HIWAY511SUB8 (5767) | E_NEDIN_CC1_TRAIN | 138 | Change Bus Low Volts | - | - | - | 8.1872 | - | - | -
TONCOR | FAR_WEST | HOBLTZL_8 (2299) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Change Bus Low Volts | - | 8.8384 | 10.857 | - | - | - | -
TONCOR | SOUTH_CE | HUTTO_SUB1_8 (3657) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Change Bus Low Volts | - | - | - | 10.2409 | - | - | -
TONCOR | SOUTH_CE | HUTTO_SUB2_8 (3656) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Change Bus Low Volts | - | - | - | 10.2391 | - | - | -
TLCRA | SOUTH_CE | L_CHEAPS8_1Y (7243) | L_007243L_CHEAPS8_1Y-007251L_LINDEN8_1YC1 | 138 | Change Bus Low Volts | - | 8.4548 | - | - | - | - | -
TLCRA | SOUTH_CE | L_CHEAPS8_1Y (7243) | LCRA TSC_T579 | 138 | Change Bus Low Volts | - | 8.4447 | - | - | - | - | -
TLCRA | FAR_WEST | L_HAYTER8_1Y (78925) | L_060385SOLSTICE4A-060444HAYTER4AC1 | 138 | Change Bus Low Volts | 11.1832 | - | - | - | - | - | -
TLCRA | SOUTH_CE | L_HORNSB5_1Y (7047) | L_007047L_HORNSB5_1Y-007738L_WHISVA5_1YC1 | 345 | Change Bus High Volts | - | - | - | 8.2788 | 8.3005 | - | -
TLCRA | SOUTH_CE | L_HORNSB5_1Y (7047) | LCRA TSC_T510_T738_1 | 345 | Change Bus High Volts | - | - | - | 8.3055 | 8.5391 | - | -
TLCRA | SOUTH_CE | L_HORNSB5_1Y (7047) | LCRATSC_4_WHISVA_HORNSB | 345 | Change Bus High Volts | - | - | - | 8.288 | 8.4021 | - | -
TONCOR | FAR_WEST | LEANCLAY_8 (11078) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.9857 | -
TONCOR | FAR_WEST | LILDEWEY_8 (10029) | L_001328QUARTZSAND_8-010029LILDEWEY_8C1 | 138 | Change Bus Low Volts | 9.297 | - | - | - | - | - | -
TONCOR | FAR_WEST | LILLUTHER_8 (10032) | L_010032LILLUTHER_8-023835VLMOOR_8C1 | 138 | Change Bus Low Volts | - | 9.0324 | - | - | - | - | -
TONCOR | FAR_WEST | LILVLMOOR_8 (10034) | L_010034LILVLMOOR_8-023835VLMOOR_8C1 | 138 | Change Bus Low Volts | - | - | 8.5991 | - | - | - | -
TONCOR | NORTH_CE | LNCST1_8 (3066) | L_002429WATMLL_8-003065REINDEER_8C1 | 138 | Change Bus Low Volts | - | - | - | 8.0392 | - | - | -
TONCOR | FAR_WEST | LUTHER_8 (23831) | L_010032LILLUTHER_8-023831LUTHER_8C1 | 138 | Change Bus Low Volts | - | 8.9947 | - | - | - | - | -
TONCOR | FAR_WEST | LUTHER_8 (23831) | L_010032LILLUTHER_8-023835VLMOOR_8C1 | 138 | Change Bus Low Volts | - | 8.9919 | - | - | - | - | -
TONCOR | FAR_WEST | LUTHER_8 (23831) | LUTHER - VEALMOOR 138 KV LINE 2026 SUM - FUTURE (SINGLE B TO B) | 138 | Change Bus Low Volts | - | 8.9952 | - | - | - | - | -
TONCOR | SOUTH_CE | MALLARD_8 (3693) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Change Bus Low Volts | - | - | - | 9.9383 | - | - | -
TGSEC | FAR_WEST | MARTIN_8 (9486) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Change Bus Low Volts | - | - | 10.1771 | - | - | - | -
TONCOR | FAR_WEST | MAVRKDRW_8 (11082) | L_001097CULBERSON_8-011082MAVRKDRW_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.0464 | 9.3961 | -
TONCOR | FAR_WEST | MCHALAM_8 (11086) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.9638 | -
TONCOR | NORTH_CE | MDLTH_N_8 (2313) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Change Bus Low Volts | - | - | - | 8.5281 | - | - | -
TONCOR | NORTH_CE | MDLTH_S_8 (2308) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Change Bus Low Volts | - | - | 9.1771 | - | - | 9.523 | -
TONCOR | NORTH_CE | MDLTHTXI1_8 (2307) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Change Bus Low Volts | - | 8.0792 | 9.9937 | - | - | - | -
TONCOR | NORTH_CE | MDLTHTXI1_8 (2307) | L_002305AIRPRD_T8-002307MDLTHTXI1_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.6795 | - | -
TONCOR | NORTH_CE | MEXIA2_1_8 (3632) | L_003632MEXIA2_1_8-003634GROES_SE1_8C1 | 138 | Change Bus Low Volts | - | 12.4033 | - | - | - | - | -
TRAYBN | NORTH_CE | MLSSA_RC (6873) | L_002340MELSSA_P8-002374ANNASW_8C1 | 138 | Change Bus Low Volts | 10.4752 | - | 9.5243 | - | 9.047 | 9.5696 | -
TONCOR | NORTH_CE | NEWBRCH_8 (12307) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Change Bus Low Volts | - | - | 9.8851 | - | - | 10.4057 | -
TONCOR | NORTH_CE | NEWBRCH_8 (12307) | L_002305AIRPRD_T8-002307MDLTHTXI1_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.5774 | - | -
TONCOR | SOUTH_CE | NEWSWEDEN_8 (3710) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Change Bus Low Volts | - | - | - | 8.2869 | - | - | -
TSTEC | SOUTHERN | OAKSSW8 (5713) | L_005390SOMERSET-005718ROSSVILLESB8C1 | 138 | Change Bus Low Volts | - | - | 8.0277 | - | - | - | -
TONCOR | FAR_WEST | OLEFIN_T8 (11281) | L_001027ODESEHV_8-001052REXALL_8C1 | 138 | Change Bus Low Volts | - | 8.2419 | 8.9495 | 9.7113 | 8.0552 | 8.3596 | -
TONCOR | FAR_WEST | OLEFIN_T8 (11281) | L_001052REXALL_8-001053GENRUBR_8C1 | 138 | Change Bus Low Volts | - | - | 8.7062 | 9.1761 | - | - | -
TONCOR | FAR_WEST | OLEFIN_T8 (11281) | L_001053GENRUBR_8-011281OLEFIN_T8C1 | 138 | Change Bus Low Volts | - | - | 8.706 | 9.1727 | - | - | -
TONCOR | FAR_WEST | OLFNNSHL_8 (1054) | L_001027ODESEHV_8-001052REXALL_8C1 | 138 | Change Bus Low Volts | - | 8.2419 | 8.9495 | 9.7113 | 8.0552 | 8.3596 | -
TONCOR | FAR_WEST | OLFNNSHL_8 (1054) | L_001052REXALL_8-001053GENRUBR_8C1 | 138 | Change Bus Low Volts | - | - | 8.7062 | 9.1761 | - | - | -
TONCOR | FAR_WEST | OLFNNSHL_8 (1054) | L_001053GENRUBR_8-011281OLEFIN_T8C1 | 138 | Change Bus Low Volts | - | - | 8.706 | 9.1727 | - | - | -
1 | FAR_WEST | ONC900002_TAP (1299) | L_011094RETONE_8-011189QUARRYFLD_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.6845 | 8.1683 | -
1 | FAR_WEST | ONC900005_TAP (11610) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.4133 | -
1 | FAR_WEST | ONC900009_TAP (11612) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.529 | -
1 | FAR_WEST | Other_119 (900111) | L_001086BARSTOWNW_8-011105PECONE_P8C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.0189 | - | -
1 | FAR_WEST | Other_119 (900111) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.8952 | -
1 | FAR_WEST | Other_132 (900043) | L_023834ELBOW_8-900043Other_132C1 | 138 | Change Bus High Volts | 11.5063 | 11.6324 | 8.5733 | 8.2763 | 8.9154 | - | -
1 | FAR_WEST | Other_132 (900043) | L_023834ELBOW_8-900100Other_131C1 | 138 | Change Bus High Volts | 10.9532 | 11.2821 | - | - | 8.1757 | - | -
1 | FAR_WEST | Other_14 (900002) | L_011094RETONE_8-011189QUARRYFLD_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.776 | 8.2538 | -
1 | FAR_WEST | Other_43_SO (900023) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 9.979 | - | -
1 | FAR_WEST | Other_43_SO (900023) | L_001086BARSTOWNW_8-011105PECONE_P8C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.3769 | - | -
1 | FAR_WEST | Other_43_SO (900023) | L_001097CULBERSON_8-011082MAVRKDRW_8C1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.2062 | -
1 | FAR_WEST | Other_43_SO (900023) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Change Bus Low Volts | - | - | - | - | - | 9.2817 | -
1 | FAR_WEST | Other_43_SO (900023) | New Shunt 900012 | 138 | Change Bus Low Volts | - | - | - | - | - | 11.1743 | -
1 | FAR_WEST | Other_44_SO (900005) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.4898 | -
1 | FAR_WEST | Other_45_SO (900009) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.6007 | -
1 | FAR_WEST | Other_46_SO (900012) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 10.2004 | - | -
1 | FAR_WEST | Other_46_SO (900012) | L_001086BARSTOWNW_8-011105PECONE_P8C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.5607 | - | -
1 | FAR_WEST | Other_46_SO (900012) | L_001097CULBERSON_8-011082MAVRKDRW_8C1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.3804 | -
1 | FAR_WEST | Other_46_SO (900012) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 12.5618 | 9.4803 | -
TONCOR | FAR_WEST | OWLHILLS2_8 (11267) | L_011183TUNSTLL_8-011199RDRUNNER_T8C1 | 138 | Change Bus Low Volts | - | - | - | 8.6529 | - | - | -
TONCOR | FAR_WEST | OWLHILLS2_T8 (11269) | L_011183TUNSTLL_8-011199RDRUNNER_T8C1 | 138 | Change Bus Low Volts | - | - | - | 8.6529 | - | - | -
TPDEC0 | SOUTH_CE | P_FLATRO8_1_ (70111) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.5134 | - | -
TONCOR | NORTH_CE | PADERA_8 (2286) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Change Bus Low Volts | - | - | - | 8.9328 | - | - | -
TBPUB | SOUTHERN | PALOALTO (5965) | E_NEDIN_CC1_TRAIN | 138 | Change Bus Low Volts | - | - | - | 8.0882 | - | - | -
TONCOR | FAR_WEST | PECONE_P8 (11105) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 9.6971 | - | -
TTNMP | FAR_WEST | PECOSBND1 (38098) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 9.719 | - | -
TONCOR | SOUTH_CE | PFLGRVIL1_8 (3665) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Change Bus Low Volts | - | - | - | 9.272 | - | - | -
TONCOR | SOUTH_CE | PFLGRVILS_8 (13665) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Change Bus Low Volts | - | - | - | 8.873 | - | - | -
TONCOR | SOUTH_CE | PINTAIL_8 (3692) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Change Bus Low Volts | - | - | - | 9.9425 | - | - | -
TONCOR | NORTH_CE | PLUTO1_8 (12303) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Change Bus Low Volts | - | 8.8441 | 10.8642 | - | - | - | -
TONCOR | NORTH_CE | PLUTO2_8 (12304) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Change Bus Low Volts | - | 8.8441 | 10.8642 | - | - | - | -
TSTEC | COAST | PRARIEVISB8 (57668) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.1661 | - | -
TBPUB | SOUTHERN | PRICE_RD (59410) | E_NEDIN_CC1_TRAIN | 138 | Change Bus Low Volts | - | - | - | 8.1676 | - | - | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | L_010080REDBERRY_8-900043Other_132C1 | 138 | Change Bus High Volts | 8.3505 | - | - | - | - | - | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | L_023834ELBOW_8-900043Other_132C1 | 138 | Change Bus High Volts | 8.2169 | - | - | - | - | - | -
TONCOR | FAR_WEST | RETONE_8 (11094) | L_011094RETONE_8-011189QUARRYFLD_8C1 | 138 | Change Bus Low Volts | - | - | 9.3357 | 10.6889 | 12.0762 | 11.3136 | -
TONCOR | FAR_WEST | REXALL_8 (1052) | L_001027ODESEHV_8-001052REXALL_8C1 | 138 | Change Bus Low Volts | - | 8.3222 | 9.0854 | 9.855 | 8.1922 | 8.4817 | -
TONCOR | SOUTH_CE | RNDRCKNE1_8 (3670) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Change Bus Low Volts | - | - | - | 8.6865 | - | - | -
TBREC | NORTH_CE | ROCKHILL (675) | L_000675ROCKHILL-002380WESTRIDGE1_8C1 | 138 | Change Bus Low Volts | 8.0027 | - | - | - | - | - | -
TSTEC | SOUTHERN | ROSSVILLESB8 (5718) | L_005390SOMERSET-005718ROSSVILLESB8C1 | 138 | Change Bus Low Volts | - | - | 8.7542 | - | - | - | -
TONCOR | WEST | SACROC_8 (1311) | L_001064SUN_8-001311SACROC_8C1 | 138 | Change Bus Low Volts | 10.9955 | 8.4832 | 10.3532 | 9.6685 | 9.7705 | 10.0225 | -
TONCOR | NORTH_CE | SGVL1_8 (3076) | L_002434SGVLSW1_8-003076SGVL1_8C1 | 138 | Change Bus Low Volts | - | - | - | 8.4466 | - | - | -
TBPUB | SOUTHERN | SIXTH_ST (59480) | E_NEDIN_CC1_TRAIN | 138 | Change Bus Low Volts | - | - | - | 8 | - | - | -
TONCOR | SOUTH_CE | SKYBOX_8 (3371) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Change Bus Low Volts | - | - | - | 10.4381 | - | - | -
TBPUB | SOUTHERN | SOUTH_PL (59500) | E_NEDIN_CC1_TRAIN | 138 | Change Bus Low Volts | - | - | - | 8.1338 | - | - | -
TSTEC | SOUTHERN | SOUTHMOSTSB8 (5789) | E_NEDIN_CC1_TRAIN | 138 | Change Bus Low Volts | - | - | - | 8.4304 | - | - | -
TONCOR | SOUTH_CE | STARRANCH_8 (3653) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Change Bus Low Volts | - | - | - | 10.2006 | - | - | -
TRAYBN | NORTH_CE | STNPT_RC (6877) | L_002340MELSSA_P8-002374ANNASW_8C1 | 138 | Change Bus Low Volts | 8.96 | - | 8.183 | 9.5777 | - | 8.2417 | -
TRAYBN | NORTH_CE | STNPT_RC (6877) | L_002340MELSSA_P8-002704ANNASE_8C1 | 138 | Change Bus Low Volts | - | - | - | 8.4927 | - | - | -
TRAYBN | EAST | SUNOCORC (6805) | L_003233NEWATHENS_8-003238ATHENS_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.8161 | - | -
TONCOR | SOUTH_CE | TAYLOR_W1_8 (3673) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Change Bus Low Volts | - | - | - | 10.1708 | - | - | -
TONCOR | SOUTH_CE | TAYLOR_W2_8 (3376) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Change Bus Low Volts | - | - | - | 10.1798 | - | - | -
TONCOR | SOUTH_CE | TAYLOR1_8 (3658) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Change Bus Low Volts | - | - | - | 8.0205 | - | - | -
TONCOR | SOUTH_CE | TEAL_8 (3362) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Change Bus Low Volts | - | - | - | 10.434 | - | - | -
TONCOR | NORTH_CE | THMSAVE1_8 (13696) | L_012446MDLTM2_8-012904ENETOH2_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.6542 | - | -
TBPUB | SOUTHERN | TITAN (5963) | E_NEDIN_CC1_TRAIN | 138 | Change Bus Low Volts | - | - | - | 8.2176 | - | - | -
TTNMP | FAR_WEST | TNCOTTNWD_1 (38099) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.9916 | -
TTNMP | FAR_WEST | TNETOYAHC_1 (38119) | New Shunt 900021 | 138 | Change Bus Low Volts | - | - | - | 8.558 | - | 8.9202 | -
TTNMP | FAR_WEST | TNETOYAHM_1 (38118) | New Shunt 900021 | 138 | Change Bus Low Volts | - | - | - | 8.5453 | 9.0191 | 8.906 | -
TTNMP | FAR_WEST | TNETOYAHT_1 (38117) | New Shunt 900021 | 138 | Change Bus Low Volts | - | - | - | 8.5448 | 9.0186 | 8.9055 | -
TTNMP | FAR_WEST | TNFAULKNER1 (38124) | L_038124TNFAULKNER1-900038Other_47_SOC1 | 138 | Change Bus High Volts | - | - | 8.154 | - | - | - | -
TTNMP | FAR_WEST | TNGRISHAM_1 (38100) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.9869 | -
TTNMP | FAR_WEST | TNGRISHAMC1 (38101) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.9871 | -
TTNMP | FAR_WEST | TNSCIMITRM1 (38102) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 9.6975 | - | -
TTNMP | FAR_WEST | TNSCMTRCCP1 (38104) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 9.6976 | - | -
TTNMP | FAR_WEST | TNSCMTRCOP1 (38103) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 9.7046 | - | -
TTNMP | FAR_WEST | TNSNDLKCEC1 (38106) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Change Bus Low Volts | - | - | 8.0268 | - | - | - | -
TONCOR | FAR_WEST | TOWA_P8 (11069) | L_001097CULBERSON_8-011082MAVRKDRW_8C1 | 138 | Change Bus Low Volts | - | - | - | - | - | 8.867 | -
TONCOR | FAR_WEST | TOWA_P8 (11069) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Change Bus Low Volts | - | - | - | - | 8.7292 | - | -
TONCOR | FAR_WEST | TUNSTLL_8 (11183) | L_011183TUNSTLL_8-011199RDRUNNER_T8C1 | 138 | Change Bus Low Volts | - | - | 9.5708 | - | - | - | -
TONCOR | NORTH_CE | VENUS (1908) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Change Bus Low Volts | - | 8.815 | 10.8341 | - | - | - | -
TBREC | NORTH_CE | VENUS3_8 (441) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Change Bus Low Volts | - | 8.8384 | - | - | - | - | -
TAEPTN | FAR_WEST | VERH4A (60207) | L_060385SOLSTICE4A-060808HOEFSROA4AC1 | 138 | Change Bus Low Volts | - | - | 10.3879 | - | - | - | -
TBPUB | SOUTHERN | WATERPRT (59450) | E_NEDIN_CC1_TRAIN | 138 | Change Bus Low Volts | - | - | - | 8.7854 | - | - | -
TONCOR | FAR_WEST | WRGRN_P8 (11350) | L_001328QUARTZSAND_8-010029LILDEWEY_8C1 | 138 | Change Bus Low Volts | 9.1566 | - | - | - | - | - | -
TONCOR | FAR_WEST | WRGRN_P8 (11350) | L_010029LILDEWEY_8-011350WRGRN_P8C1 | 138 | Change Bus Low Volts | 9.1477 | - | - | - | - | - | -

## Buses
Owner | Zone | Bus | Contingency | kV | Category | Limit | 2026sum pu | 2027min pu | 2027sum pu | 2029sum pu | 2030sum pu | 2030sum_EHV pu | Notes
TAEPTC | SOUTHERN | ACME7A (81005) | Haber - Coleto Creek | 345 | Bus Low Volts | 0.9 | - | - | - | - | - | 0.75213 | -
TAEPTC | SOUTHERN | ACME7A (81005) | L_008676STATIC7A-081003HABER7AC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | - | 0.89473 | -
TAEPTC | SOUTHERN | ACME7A (81005) | Pre-contingency | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.87947 | - | -
RCASTL | NORTH_CE | AGUAYO_5 (153033) | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus High Volts | 1.05 | 1.072 | - | 1.0729 | 1.0659 | 1.0707 | 1.0726 | -
TONCOR | NORTH_CE | AIRLIQD_P8 (2283) | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89243 | - | - | - | -
TONCOR | NORTH_CE | AIRLIQD_P8 (2283) | L_000442RAILPORT-001908VENUSC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.88994 | - | - | - | -
1 | SOUTHERN | AIRLIQSW4A (8979) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87153 | - | -
1 | SOUTHERN | AIRLIQSW4A (8979) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8944 | - | -
1 | SOUTHERN | AIRLIQSW4A (8979) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90782 | - | -
TONCOR | FAR_WEST | AIRPARK_8 (1325) | L_001322BIGSPRIG_8-010044STEER_8C1 | 138 | Bus Low Volts | 0.9 | 0.85301 | 0.88803 | - | - | 0.88301 | - | -
TONCOR | FAR_WEST | AIRPARK_8 (1325) | L_010044STEER_8-011316BSPGWSW_8C1 | 138 | Bus Low Volts | 0.9 | 0.85302 | 0.88804 | - | - | 0.88302 | - | -
TONCOR | NORTH_CE | AIRPRD_T8 (2305) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87181 | 0.83696 | 0.89898 | -
TONCOR | NORTH_CE | AIRPRD_T8 (2305) | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89515 | - | -
TONCOR | NORTH_CE | AIRPRD1_8 (2306) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87168 | 0.83682 | 0.89885 | -
TONCOR | NORTH_CE | AIRPRD1_8 (2306) | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89503 | - | -
TONCOR | WEST | AIRPTRD_8 (23845) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.84663 | - | - | - | - | -
TETRTX | SOUTHERN | ALAZAN4A (8515) | L_008458B_DAVIS4A-085010CARVL4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90972 | - | -
TRAYBN | NORTH_CE | ALHUB_RC (6826) | L_002370COLLINSS1_8-002380WESTRIDGE1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89999 | 0.89996 | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | 3WT_001302WILLOWVAL_5_001301WILLOWVAL_8_018537WILLOWVAL_3 C 3 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0508 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | ANDREWS COUNTY SOUTH - NORTH ANDREWS/HOLT 138 KV SUM 2023 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | BUFFALO - STANTON EAST 138 KV LINE BEG - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | C5-WETT-2_A-2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | CONSAVVY - GREY WELL DRAW/MIDLAND EAST 138 KV LINE 2028 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | CULBERSON - COALSON DRAW CKT 2 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | CULBERSON - COALSON DRAW DCKT 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | EILAND - BULLDOG 138 KV LINE 2027 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | G_132881LMESASLR_G1US1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | G_132882LMESASLR_S2US2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | G_134441LAPETUS_S1US1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | HOLLY_CON | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | HOLT - N ANDREWS B SUM 2017 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001018MOSS_5-001185MIDCONW_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001023MIDLNDE_8-001116WINDWOOD_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001023MIDLNDE_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0504 | - | - | - | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001023MIDLNDE_8-011295MIDLDWNT_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001023MIDLNDE_8-011296MIDLDWNT2_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001116WINDWOOD_8-001117MIDLANDW_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001132MIDLDWNT_8-011295MIDLDWNT_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001134LITTMAN_8-001278PHILANDS_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001134LITTMAN_8-011273NELSON_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001141HOLTSS_8-001262EMMATAP_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001153ARENATAP_8-001159NOANDREW_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001153ARENATAP_8-001173ANDHWY181_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001154BAKKETAP_8-001159NOANDREW_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001154BAKKETAP_8-001161UNPKRBK_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001154BAKKETAP_8-001280BAKKE_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001157ANDRCOSO_8-900039Other_141C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001159NOANDREW_8-001167MUSTANG_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.052 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001159NOANDREW_8-001262EMMATAP_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001161UNPKRBK_8-900099Other_36C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001163LAMESA_8-001307KEYLYNTE_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001163LAMESA_8-010008LAMESA2_8C1 | 138 | Bus High Volts | 1.05 | 1.0552 | - | 1.0518 | 1.0572 | 1.0522 | 1.054 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001163LAMESA_8-132883LMESASLR_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0508 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001167MUSTANG_8-001168PAULDTAP_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.052 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001168PAULDTAP_8-900060OTHER_140C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.052 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001169ALKALILK_8-001170PAULDTAP2_8C1 | 138 | Bus High Volts | 1.05 | 1.0554 | - | 1.0523 | 1.0579 | 1.0531 | 1.0549 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001170PAULDTAP2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | 1.0559 | - | 1.0529 | 1.0584 | 1.0537 | 1.0554 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | 1.0572 | - | 1.0524 | 1.0554 | 1.0511 | 1.0534 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.056 | - | 1.0512 | 1.0541 | - | 1.0521 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0574 | - | 1.0527 | 1.0557 | 1.0515 | 1.0538 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001173ANDHWY181_8-900039Other_141C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0615 | - | 1.0574 | 1.0608 | 1.0569 | 1.0592 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.062 | - | 1.0579 | 1.0612 | 1.0573 | 1.0597 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001177TEXMABEE_8-001181ANDHWY87_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.051 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001177TEXMABEE_8-011175BAIRDLAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0591 | - | 1.0576 | 1.0606 | 1.0547 | 1.0579 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0583 | - | 1.0568 | 1.0598 | 1.0538 | 1.057 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0589 | - | 1.0574 | 1.0604 | 1.0543 | 1.0576 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001181ANDHWY87_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0634 | - | 1.0622 | 1.0653 | 1.0594 | 1.0627 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0536 | - | 1.0519 | 1.0548 | - | 1.0519 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001183MIDCONW_8-023862TELPHRD_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001184GODDARD_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | 1.0593 | - | 1.0549 | 1.0581 | 1.054 | 1.0564 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0581 | - | 1.0566 | 1.0596 | 1.0536 | 1.0568 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001264SANADTAP_8-001269MIDFARMS_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001264SANADTAP_8-001283XTOBLOCK9_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001272FULLERTON_8-001275NIXPOD_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001275NIXPOD_8-001278PHILANDS_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001283XTOBLOCK9_8-900099Other_36C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0509 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001307KEYLYNTE_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001308GAILLYNT_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001326STANTON_E_8-011229STANTON_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001328QUARTZSAND_8-010029LILDEWEY_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001355BUZZDRAW_8-023829KOCHTAP_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001393DAWSON115_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | 1.0505 | - | - | 1.0527 | - | 1.0505 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_001393DAWSON115_8-900060OTHER_140C1 | 138 | Bus High Volts | 1.05 | 1.0507 | - | - | 1.0529 | - | 1.0507 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_009418PATRICIA_8-009419JPAYNE_CB_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_009424FTBLOCKS_8-131453KEO_2_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_010008LAMESA2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | 1.054 | - | 1.0505 | 1.056 | 1.051 | 1.0528 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_010029LILDEWEY_8-011350WRGRN_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_010036MUSTGSPG_8-023840GLSRNCH_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_010036MUSTGSPG_8-023855TALLCTY_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_011078LEANCLAY_8-038099TNCOTTNWD_1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0584 | - | 1.0539 | 1.057 | 1.0528 | 1.0552 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_011167ALKALILK2_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0561 | - | 1.0529 | 1.0588 | 1.0533 | 1.0569 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_011167ALKALILK2_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | 1.0548 | - | 1.0513 | 1.0571 | 1.0515 | 1.0551 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.059 | - | 1.0576 | 1.0605 | 1.0546 | 1.0578 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_011189QUARRYFLD_8-900004Other_10C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_011229STANTON_8-023837BUFFLO_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_011278GODDARD2_8-011280GODDARD2_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_011280GODDARD2_T8-011301MOCKNGBRD_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_011296MIDLDWNT2_T8-900033OTHER_133C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_011337POLECAT1_8-011350WRGRN_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_023829KOCHTAP_8-023835VLMOOR_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_023855TALLCTY_8-023862TELPHRD_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_038097TNBCCASTLE1-038099TNCOTTNWD_1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_038145TNCEDRVALE1-038146TNBCTRESTL1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_038190TNLONESTAR1-038191TNBCGWRWNK1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_038294TNFOXTAIL_1-038296TNBCATOKA_1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_038340TNAIRPORT41-038341TNBCLNCIUM1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_038380TNCOYANOSA1-038382TNBCCANYON1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_888856HOLLY_POI-059900LONG_DRAWC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | L_901397ONC900020_TAP-900020Other_135C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | 1.0978 | - | 1.0957 | 1.0952 | 1.0912 | 1.0936 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | MIDESSA SOUTH - MIDLAND EAST & ODESSA CKT 2 138 KV SUM 2027 - FUT (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0513 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | MIDESSA SOUTH - MIDLAND EAST 138 KV SUM 2022 - FUT (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.051 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | MIDLAND COUNTY NW - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0638 | - | 1.0625 | 1.0655 | 1.0597 | 1.0629 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | MIDLAND COUNTY NW - MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0632 | - | 1.0623 | 1.0653 | 1.0594 | 1.0626 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | MIDLAND EAST - CONSAVVY 138 KV SUM 2028 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | MIDLAND EAST - CONSAVVY/MIDLAND DOWNTOWN 138 KV SUM 2028 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | 1.0625 | - | 1.0584 | 1.0615 | 1.0577 | 1.06 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0621 | - | 1.0576 | 1.0606 | 1.0572 | 1.0592 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | MIDLAND EAST - MIDLAND DOWNTOWN 138 KV WIN 2023 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | MIDLAND EAST - SU_BUFFALO 138 KV SUM 2018 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | MOSS - HOLT 138 KV/MIDLAND COUNTY NW SW 345 KV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | MOSS - HOLT/YUCCA 138 KV/MIDLAND COUNTY NW SW 345 KV (DOUBLE B TO B) SUM 2025- FUTURE | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | MOSS - MIDLAND COUNTY NW 138 KV 2019 SUM - FUTURE (DOUBLE B TO B) B | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | MOSS - MIDLAND COUNTY NW 138 KV CKT 2 2019 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | MOSS - MIDLAND COUNTY NW CKT 2 2019 SPG - FUTURE | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | NATURAL DAM - CALF CREEK - BIG SPRING 138 KV SUM 2026 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | NELSON - FULLERTON 138 KV WIN 2020 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | NORTH ANDREWS - ANDREWS COUNTY SOUTH 138 KV 2023 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | NORTH ANDREWS - MCKENZIE 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0562 | - | 1.053 | 1.0588 | 1.0534 | 1.0569 | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | ODESSA - MIDESSA SOUTH CKT 2 138 KV SUM 2027 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.0555 | - | - | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | QUARRY FIELD - BLUE MOUNTAIN CKT 2 138 KV SUM 2025 - FUTURE (SINGLE B TO B)_MODIFIED_BY_MZ | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | QUARTZ SAND - POLECAT CREEK 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | RIVERTON - DELAWARE RIVER SWITCH 138 KV DCKT LINE (DOUBLE B TO B) WIN 2025 - SUM 2030 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | RIVERTON - DELAWARE RIVER SWITCH 138 KV LINE SOUTH CKT 1 SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | S_011386CONSAVVY1_31 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | S_011389CONSAVVY2_31 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | SAND LAKE - YUCCA DR DCKT 138 KV SUM 2019 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | SPRABERRY - DEWEY LAKE TAP 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | STANTON EAST - SPRABERRY 69 KV/ BUFFALO 138 KV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | TALL CITY - PECAN GROVE/GLASS RANCH 138 KV DCKT LINE (DOUBLE B TO B) 2028 SUM - FUTURE | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | VEALMOOR - BUZZARD DRAW 138 KV LINE SUM 2022 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | WILLOW VALLEY - LAMESA 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | WILLOW VALLEY TRANSFORMER 1 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0508 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | WOLF - ODESSA EHV 138 KV SUM 2027 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK_8 (1169) | XFMR-RANGER_5 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | 3WT_001302WILLOWVAL_5_001301WILLOWVAL_8_018537WILLOWVAL_3 C 3 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0508 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | ANDREWS COUNTY SOUTH - NORTH ANDREWS/HOLT 138 KV SUM 2023 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | BUFFALO - STANTON EAST 138 KV LINE BEG - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | C5-WETT-2_A-2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | CONSAVVY - GREY WELL DRAW/MIDLAND EAST 138 KV LINE 2028 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | CULBERSON - COALSON DRAW CKT 2 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | CULBERSON - COALSON DRAW DCKT 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | EILAND - BULLDOG 138 KV LINE 2027 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | G_132881LMESASLR_G1US1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | G_132882LMESASLR_S2US2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | G_134441LAPETUS_S1US1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | HOLLY_CON | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | HOLT - N ANDREWS B SUM 2017 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001018MOSS_5-001185MIDCONW_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001023MIDLNDE_8-001116WINDWOOD_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001023MIDLNDE_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0504 | - | - | - | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001023MIDLNDE_8-011295MIDLDWNT_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001023MIDLNDE_8-011296MIDLDWNT2_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001116WINDWOOD_8-001117MIDLANDW_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001132MIDLDWNT_8-011295MIDLDWNT_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001134LITTMAN_8-001278PHILANDS_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001134LITTMAN_8-011273NELSON_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001141HOLTSS_8-001262EMMATAP_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001153ARENATAP_8-001159NOANDREW_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001153ARENATAP_8-001173ANDHWY181_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001154BAKKETAP_8-001159NOANDREW_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001154BAKKETAP_8-001161UNPKRBK_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001154BAKKETAP_8-001280BAKKE_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001157ANDRCOSO_8-900039Other_141C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001159NOANDREW_8-001167MUSTANG_8C1 | 138 | Bus High Volts | 1.05 | 1.05 | - | - | 1.052 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001159NOANDREW_8-001262EMMATAP_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001161UNPKRBK_8-900099Other_36C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001163LAMESA_8-001307KEYLYNTE_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001163LAMESA_8-010008LAMESA2_8C1 | 138 | Bus High Volts | 1.05 | 1.0551 | - | 1.0517 | 1.0571 | 1.0522 | 1.0539 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001163LAMESA_8-132883LMESASLR_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0508 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001167MUSTANG_8-001168PAULDTAP_8C1 | 138 | Bus High Volts | 1.05 | 1.05 | - | - | 1.052 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001168PAULDTAP_8-900060OTHER_140C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.052 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001169ALKALILK_8-001170PAULDTAP2_8C1 | 138 | Bus High Volts | 1.05 | 1.0554 | - | 1.0523 | 1.0578 | 1.0531 | 1.0548 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001169ALKALILK_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0554 | - | 1.0523 | 1.0579 | 1.0531 | 1.0548 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001170PAULDTAP2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | 1.0559 | - | 1.0528 | 1.0583 | 1.0536 | 1.0553 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | 1.0572 | - | 1.0524 | 1.0554 | 1.0511 | 1.0534 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.056 | - | 1.0512 | 1.0541 | - | 1.0521 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0574 | - | 1.0527 | 1.0557 | 1.0515 | 1.0538 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001173ANDHWY181_8-900039Other_141C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0615 | - | 1.0574 | 1.0608 | 1.0569 | 1.0592 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.062 | - | 1.0579 | 1.0612 | 1.0573 | 1.0596 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001177TEXMABEE_8-001181ANDHWY87_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.051 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001177TEXMABEE_8-011175BAIRDLAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0591 | - | 1.0577 | 1.0606 | 1.0547 | 1.0579 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0583 | - | 1.0568 | 1.0598 | 1.0538 | 1.057 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0589 | - | 1.0574 | 1.0604 | 1.0544 | 1.0576 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001181ANDHWY87_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0635 | - | 1.0622 | 1.0653 | 1.0594 | 1.0627 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0536 | - | 1.052 | 1.0548 | - | 1.0519 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001183MIDCONW_8-023862TELPHRD_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001184GODDARD_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | 1.0593 | - | 1.0549 | 1.0581 | 1.0541 | 1.0564 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0581 | - | 1.0566 | 1.0596 | 1.0536 | 1.0568 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001264SANADTAP_8-001269MIDFARMS_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001264SANADTAP_8-001283XTOBLOCK9_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001272FULLERTON_8-001275NIXPOD_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001275NIXPOD_8-001278PHILANDS_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001283XTOBLOCK9_8-900099Other_36C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0509 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001307KEYLYNTE_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001308GAILLYNT_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001326STANTON_E_8-011229STANTON_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001328QUARTZSAND_8-010029LILDEWEY_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001355BUZZDRAW_8-023829KOCHTAP_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001393DAWSON115_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | 1.0505 | - | - | 1.0527 | - | 1.0505 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_001393DAWSON115_8-900060OTHER_140C1 | 138 | Bus High Volts | 1.05 | 1.0507 | - | - | 1.0529 | - | 1.0507 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_009418PATRICIA_8-009419JPAYNE_CB_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_009424FTBLOCKS_8-131453KEO_2_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_010008LAMESA2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | 1.0539 | - | 1.0505 | 1.0559 | 1.051 | 1.0527 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_010029LILDEWEY_8-011350WRGRN_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_010036MUSTGSPG_8-023840GLSRNCH_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_010036MUSTGSPG_8-023855TALLCTY_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_011078LEANCLAY_8-038099TNCOTTNWD_1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0584 | - | 1.0539 | 1.057 | 1.0528 | 1.0551 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_011167ALKALILK2_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | 1.0548 | - | 1.0514 | 1.0572 | 1.0516 | 1.0551 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.059 | - | 1.0576 | 1.0605 | 1.0546 | 1.0578 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_011189QUARRYFLD_8-900004Other_10C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_011229STANTON_8-023837BUFFLO_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_011278GODDARD2_8-011280GODDARD2_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_011280GODDARD2_T8-011301MOCKNGBRD_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_011296MIDLDWNT2_T8-900033OTHER_133C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_011337POLECAT1_8-011350WRGRN_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_023829KOCHTAP_8-023835VLMOOR_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_023855TALLCTY_8-023862TELPHRD_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_038097TNBCCASTLE1-038099TNCOTTNWD_1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_038145TNCEDRVALE1-038146TNBCTRESTL1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_038190TNLONESTAR1-038191TNBCGWRWNK1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_038294TNFOXTAIL_1-038296TNBCATOKA_1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_038340TNAIRPORT41-038341TNBCLNCIUM1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_038380TNCOYANOSA1-038382TNBCCANYON1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_888856HOLLY_POI-059900LONG_DRAWC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | L_901397ONC900020_TAP-900020Other_135C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | LAMESA - MCKENZIE DRAW 138 KV SUM 2023 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0554 | - | 1.0523 | 1.0579 | 1.0531 | 1.0548 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | 1.0978 | - | 1.0957 | 1.0952 | 1.0911 | 1.0936 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | MIDESSA SOUTH - MIDLAND EAST & ODESSA CKT 2 138 KV SUM 2027 - FUT (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0513 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | MIDESSA SOUTH - MIDLAND EAST 138 KV SUM 2022 - FUT (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.051 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | MIDLAND COUNTY NW - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0638 | - | 1.0625 | 1.0655 | 1.0597 | 1.0629 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | MIDLAND COUNTY NW - MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0632 | - | 1.0623 | 1.0653 | 1.0594 | 1.0626 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | MIDLAND EAST - CONSAVVY 138 KV SUM 2028 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | MIDLAND EAST - CONSAVVY/MIDLAND DOWNTOWN 138 KV SUM 2028 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | 1.0625 | - | 1.0584 | 1.0615 | 1.0577 | 1.06 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0621 | - | 1.0576 | 1.0606 | 1.0572 | 1.0592 | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | MIDLAND EAST - MIDLAND DOWNTOWN 138 KV WIN 2023 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | MIDLAND EAST - SU_BUFFALO 138 KV SUM 2018 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | MOSS - HOLT 138 KV/MIDLAND COUNTY NW SW 345 KV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | MOSS - HOLT/YUCCA 138 KV/MIDLAND COUNTY NW SW 345 KV (DOUBLE B TO B) SUM 2025- FUTURE | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | MOSS - MIDLAND COUNTY NW 138 KV 2019 SUM - FUTURE (DOUBLE B TO B) B | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | MOSS - MIDLAND COUNTY NW 138 KV CKT 2 2019 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | MOSS - MIDLAND COUNTY NW CKT 2 2019 SPG - FUTURE | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | NATURAL DAM - CALF CREEK - BIG SPRING 138 KV SUM 2026 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | NELSON - FULLERTON 138 KV WIN 2020 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | NORTH ANDREWS - ANDREWS COUNTY SOUTH 138 KV 2023 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | ODESSA - MIDESSA SOUTH CKT 2 138 KV SUM 2027 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.0555 | - | - | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | QUARRY FIELD - BLUE MOUNTAIN CKT 2 138 KV SUM 2025 - FUTURE (SINGLE B TO B)_MODIFIED_BY_MZ | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | QUARTZ SAND - POLECAT CREEK 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | RIVERTON - DELAWARE RIVER SWITCH 138 KV DCKT LINE (DOUBLE B TO B) WIN 2025 - SUM 2030 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | RIVERTON - DELAWARE RIVER SWITCH 138 KV LINE SOUTH CKT 1 SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | S_011386CONSAVVY1_31 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | S_011389CONSAVVY2_31 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | SAND LAKE - YUCCA DR DCKT 138 KV SUM 2019 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | SPRABERRY - DEWEY LAKE TAP 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | STANTON EAST - SPRABERRY 69 KV/ BUFFALO 138 KV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | TALL CITY - PECAN GROVE/GLASS RANCH 138 KV DCKT LINE (DOUBLE B TO B) 2028 SUM - FUTURE | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | VEALMOOR - BUZZARD DRAW 138 KV LINE SUM 2022 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | WILLOW VALLEY - LAMESA 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | WILLOW VALLEY TRANSFORMER 1 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0508 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | WOLF - ODESSA EHV 138 KV SUM 2027 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | ALKALILK2_8 (11167) | XFMR-RANGER_5 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | NORTH_CE | ALLA_HUB_P8 (1757) | L_002370COLLINSS1_8-002380WESTRIDGE1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.9 | 0.89996 | - | -
TONCOR | NORTH_CE | ALLENSW1_5 (2513) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | 0.94338 | 0.93597 | - | -
TONCOR | NORTH_CE | ALLENSW2_5 (2514) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94221 | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | G_132831HOLMAN_UNIT1US1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91957 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | G_170200ACA_UNIT1US1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91349 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_001009YUCCADR_8-011245RIVERVIEW_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91775 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_006630FTST4A-038355TNLEONCRK_1C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91952 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_006653BARL2A-909999NSC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.9186 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_006655BARL4A-060385SOLSTICE4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91614 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_006663COCS2A-038490TNBELDING_0C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91963 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_006666ALPINE2A-006674BRONCO2AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.90361 | 0.91747 | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_006674BRONCO2A-038490TNBELDING_0C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91959 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_006674BRONCO2A-132832HOLMAN1_9C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91956 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_006675GONZALES2A-060339ACACIA2AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91339 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_006680ALMC4A-060444HAYTER4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.87835 | 0.88006 | 0.90048 | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_011245RIVERVIEW_8-900064Other_134C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91823 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91704 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_060383LINTERNA4A-060385SOLSTICE4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91858 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_060383LINTERNA4A-132331REROCK_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91785 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_060385SOLSTICE4A-060393PIGCREEK4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91567 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_060385SOLSTICE4A-060444HAYTER4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.86832 | 0.88499 | 0.87251 | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_060385SOLSTICE4A-060808HOEFSROA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91969 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_060392LOTEBUSH4A-060415BASIN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.9198 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_060393PIGCREEK4A-134245TAYGETE_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91685 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_060393PIGCREEK4A-134705TYGTEII_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91889 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_060397GASPADTA4A-060415BASIN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91962 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L_060397GASPADTA4A-900064Other_134C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91853 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L2020745 | 138 | Bus Low Volts | 0.92 | - | - | 0.91991 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L2020965 | 138 | Bus Low Volts | 0.92 | - | - | 0.87839 | 0.88011 | 0.90053 | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | L2020971-B2 | 138 | Bus Low Volts | 0.92 | - | - | 0.91979 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.0866 | - | - | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | LCRA TSC_T494 | 138 | Bus Low Volts | 0.92 | - | - | 0.90399 | 0.91764 | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.92364 | 0.93303 | 0.94502 | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | S_038340TNAIRPORT411 | 138 | Bus Low Volts | 0.92 | - | - | 0.91931 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | SAND LAKE - SOLSTICE 345 KV DCKT LINE (DOUBLE B TO B) WIN 2027 - FUTURE | 138 | Bus Low Volts | 0.92 | - | - | 0.91306 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | T_006653BARL2A-006655BARL4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91905 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | T200015 | 138 | Bus Low Volts | 0.92 | - | - | 0.91909 | - | - | - | -
TAEPTN | FAR_WEST | ALMC4A (6680) | YUCCA DRIVE - LOTEBUSH (AEP) 138 KV 2021 SUM - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | 0.91979 | - | - | - | -
TONCOR | NORTH_CE | ALVARADO1_8 (2297) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89778 | 0.86311 | 0.83532 | 0.88211 | -
TONCOR | NORTH_CE | ALVARADO1_8 (2297) | BEPC_306 | 138 | Bus Low Volts | 0.9 | 0.8433 | 0.80589 | - | - | - | - | -
TONCOR | NORTH_CE | ALVARADO1_8 (2297) | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | Bus Low Volts | 0.9 | 0.87211 | 0.8155 | 0.77096 | - | - | - | -
TONCOR | NORTH_CE | ALVARADO1_8 (2297) | L_000442RAILPORT-001908VENUSC1 | 138 | Bus Low Volts | 0.9 | 0.87037 | 0.81518 | 0.7657 | - | - | - | -
TONCOR | NORTH_CE | ALVARADO1_8 (2297) | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | Bus Low Volts | 0.9 | 0.84328 | 0.80521 | - | - | - | - | -
TAEN | SOUTH_CE | AMD (9151) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94709 | - | - | -
TAEN | SOUTH_CE | AMD (9151) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85839 | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | 3WT_001302WILLOWVAL_5_001301WILLOWVAL_8_018537WILLOWVAL_3 C 3 | 138 | Bus High Volts | 1.05 | - | 1.0508 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | ANDREWS COUNTY SOUTH - NORTH ANDREWS/HOLT 138 KV SUM 2023 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | EILAND - BULLDOG 138 KV LINE 2026 SUM - 2027 SUM (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001023MIDLNDE_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0539 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001134LITTMAN_8-011273NELSON_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001159NOANDREW_8-001167MUSTANG_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0532 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001163LAMESA_8-001307KEYLYNTE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0529 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001163LAMESA_8-010008LAMESA2_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0541 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001163LAMESA_8-011363HARDYMGN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001167MUSTANG_8-001168PAULDTAP_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0529 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001168PAULDTAP_8-900060OTHER_140C1 | 138 | Bus High Volts | 1.05 | - | 1.0529 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001169ALKALILK_8-001170PAULDTAP2_8C1 | 138 | Bus High Volts | 1.05 | - | 1.053 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001169ALKALILK_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.053 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001170PAULDTAP2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0535 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0569 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0564 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0568 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.052 | 1.059 | - | 1.0517 | - | 1.0502 | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0523 | 1.0587 | - | 1.052 | - | 1.0505 | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001177TEXMABEE_8-001181ANDHWY87_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001177TEXMABEE_8-011175BAIRDLAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0575 | 1.0728 | 1.056 | 1.059 | 1.053 | 1.0562 | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0564 | 1.0723 | 1.0549 | 1.0578 | 1.0518 | 1.055 | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0572 | 1.0733 | 1.0557 | 1.0587 | 1.0526 | 1.0558 | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0501 | 1.069 | - | 1.0511 | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | 1.0503 | 1.0578 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0561 | 1.072 | 1.0546 | 1.0575 | 1.0515 | 1.0547 | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0537 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001307KEYLYNTE_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0531 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001308GAILLYNT_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0531 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001355BUZZDRAW_8-011363HARDYMGN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001393DAWSON115_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.053 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_001393DAWSON115_8-900060OTHER_140C1 | 138 | Bus High Volts | 1.05 | - | 1.0532 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_010008LAMESA2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0531 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0573 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_011167ALKALILK2_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0557 | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_011167ALKALILK2_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.055 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0574 | 1.0728 | 1.0559 | 1.0589 | 1.0529 | 1.0561 | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | LAMESA - BUZZARD DRAW 138 KV LINE 2018 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | LAMESA - BUZZARD DRAW 69/138 KV DCKT LINE 2019 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | LAMESA - MCKENZIE DRAW 138 KV SUM 2023 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.053 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | 1.0529 | 1.0593 | - | 1.0524 | - | 1.0509 | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0523 | 1.057 | - | 1.0512 | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | NATURAL DAM - CALF CREEK - BIG SPRING 138 KV SUM 2026 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | NORTH ANDREWS - LAMESA - MCKENZIE 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0594 | 1.0658 | 1.0552 | 1.063 | 1.0581 | 1.0603 | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | NORTH ANDREWS - MCKENZIE 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.056 | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | RANGER CAMP - BARBER LAKE SW CKT 2 138 KV SUM 2026 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | 1.0509 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | WILLOW VALLEY - LAMESA 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0529 | - | - | - | - | -
TONCOR | FAR_WEST | ANDHWY87_8 (1181) | WILLOW VALLEY TRANSFORMER 1 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0508 | - | - | - | - | -
TONCOR | SOUTH_CE | ANDICE_8 (3512) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85405 | - | -
TAEPTC | SOUTHERN | ANGSTRM7A (8249) | E_INGLCOSW_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91141 | - | -
TAEPTC | SOUTHERN | ANGSTRM7A (8249) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89287 | - | -
TAEPTC | SOUTHERN | ANGSTRM7A (8249) | SAN_PAT_CON | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91835 | - | -
TAEN | SOUTH_CE | ANGUSVAL (9155) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93667 | - | - | -
TAEN | SOUTH_CE | ANGUSVAL (9155) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85439 | - | -
TAEN | SOUTH_CE | ANGUSVAL (9155) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94784 | - | -
TRAYBN | NORTH_CE | ANNA_RC (6819) | L_002340MELSSA_P8-002374ANNASW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89749 | - | - | -
TONCOR | NORTH_CE | ANNAGCEC_T8 (2520) | L_002340MELSSA_P8-002374ANNASW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.8975 | - | - | -
TONCOR | NORTH_CE | ANNASE_8 (2704) | L_002340MELSSA_P8-002374ANNASW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89735 | - | - | -
ERCOT | NORTH_CE | ANOLEBES_B1 (154411) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88769 | - | -
RIPARA | FAR_WEST | ARAGORN_8 (135113) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.0515 | - | - | - | - | -
TAEPTC | SOUTHERN | ARANSASP4A (8430) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86971 | - | -
TAEPTC | SOUTHERN | ARANSASP4A (8430) | E_NUECES_B_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91123 | - | -
TAEPTC | SOUTHERN | ARANSASP4A (8430) | L_008422I_DUPSW4A-008425INGLESID4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.87374 | 0.85682 | 0.76713 | 0.86609 | -
TAEPTC | SOUTHERN | ARANSASP4A (8430) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88126 | - | -
TAEPTC | SOUTHERN | ARANSASP4A (8430) | L_008579KATOEN7A-008606GODDARD7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91325 | - | -
TAEPTC | SOUTHERN | ARANSASP4A (8430) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89575 | - | -
TAEPTC | SOUTHERN | ARROYOPOI7A (8705) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | 0.88496 | - | - | -
TAEPTC | SOUTHERN | ARROYOPOI7A (8705) | E5DVA1C1_1_B | 345 | Bus Low Volts | 0.92 | - | - | - | 0.89082 | - | - | -
TAEPTC | SOUTHERN | ARROYOPOI7A (8705) | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91754 | 0.90739 | - | -
TONCOR | FAR_WEST | ARUBA1_8 (1226) | L_001222PECKTAP_8-001226ARUBA1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0568 | - | - | - | - | -
TONCOR | NORTH_CE | ASHGRVE_8 (12313) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87596 | - | -
TONCOR | SOUTH_CE | ASHTONW_MB1 (9226) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93194 | - | - | -
TONCOR | SOUTH_CE | ASHTONW_MB1 (9226) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.8571 | - | -
TONCOR | SOUTH_CE | ASHTONW_MB2 (9224) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.932 | - | - | -
TONCOR | SOUTH_CE | ASHTONW_MB2 (9224) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85713 | - | -
TONCOR | SOUTH_CE | ASHWDS1_8 (3679) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85713 | - | -
TONCOR | SOUTH_CE | ASHWDS2_8 (3680) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8571 | - | -
TONCOR | FAR_WEST | ATLRESRC_8 (11114) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8912 | - | -
RLCRA | SOUTH_CE | AUSTDAM8 (170022) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85704 | - | -
TAEN | SOUTH_CE | AUSTNDAM (9139) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94618 | - | - | -
TAEN | SOUTH_CE | AUSTNDAM (9139) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85703 | - | -
TAEN | SOUTH_CE | AUSTROP8 (9328) | AEN_AU-DG¦DL_2013 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.92387 | - | -
TAEN | SOUTH_CE | AUSTROP8 (9328) | AEN_DL-AU¦LP_2013 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94905 | - | -
TAEN | SOUTH_CE | AUSTROP8 (9328) | AEN_LP-AU¦DL_2013 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94361 | - | -
TAEN | SOUTH_CE | AUSTROP8 (9328) | AEN_LY-FPP:CIS-HO | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94684 | - | -
TAEN | SOUTH_CE | AUSTROP8 (9328) | AEN_LY-FPP¦CIS | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.93993 | - | -
TAEN | SOUTH_CE | AUSTROP8 (9328) | G_RIO_TRAIN | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94934 | - | -
TAEN | SOUTH_CE | AUSTROP8 (9328) | J5LCA1C1_B | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94925 | - | -
TAEN | SOUTH_CE | AUSTROP8 (9328) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.87163 | - | -
TAEN | SOUTH_CE | AUSTROP8 (9328) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.91281 | - | -
TAEN | SOUTH_CE | AUSTROP8 (9328) | L_005133ELMCREEK-005380SHAULAC1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94854 | - | -
TAEN | SOUTH_CE | AUSTROP8 (9328) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94913 | - | -
TAEN | SOUTH_CE | AUSTROP8 (9328) | L_009045DUNLAP8-009328AUSTROP8C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.93877 | - | -
TAEN | SOUTH_CE | AUSTROP8 (9328) | LCRA TSC_T185_T246 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.9495 | - | -
TAEN | SOUTH_CE | AUSTROP8 (9328) | LCRA TSC_T255_TAE3121_1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.93355 | - | -
TAEN | SOUTH_CE | AUSTROP8 (9328) | LCRATSC_6_EUCLID_JOHNDU | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94074 | - | -
TAEN | SOUTH_CE | AUSTROP8 (9328) | Pre-contingency | 138 | Bus Low Volts | 0.98 | - | - | - | - | 0.96773 | - | -
TONCOR | SOUTH_CE | AVERY_8 (3517) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87967 | - | -
TAEN | SOUTH_CE | BA138_CAP (9001) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86171 | - | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0522 | - | - | - | - | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0518 | - | - | - | - | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0522 | - | - | - | - | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0541 | - | - | - | - | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0539 | - | - | - | - | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0563 | 1.0723 | 1.0547 | 1.0577 | 1.0516 | 1.0549 | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0572 | 1.0734 | 1.0557 | 1.0587 | 1.0526 | 1.0558 | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0686 | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | - | 1.053 | - | - | - | - | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0559 | 1.072 | 1.0544 | 1.0574 | 1.0513 | 1.0545 | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0526 | - | - | - | - | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | L_011167ALKALILK2_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | L_011167ALKALILK2_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0574 | 1.0729 | 1.0559 | 1.0588 | 1.0528 | 1.0561 | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | - | 1.0544 | - | - | - | - | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0519 | - | - | - | - | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | NORTH ANDREWS - LAMESA - MCKENZIE 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0546 | 1.0601 | 1.0502 | 1.0579 | 1.0532 | 1.0554 | -
TONCOR | FAR_WEST | BAIRDLAK_8 (11175) | NORTH ANDREWS - MCKENZIE 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TAEN | SOUTH_CE | BAL138_CAP (9017) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93819 | - | - | -
TAEN | SOUTH_CE | BAL138_CAP (9017) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85514 | - | -
TAEN | SOUTH_CE | BAL138_CAP (9017) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.949 | - | -
TONCOR | WEST | BARBER_LK1_8 (1189) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | 0.82576 | 0.84322 | 0.8382 | 0.83965 | 0.82309 | 0.83676 | -
TONCOR | WEST | BARBER_LK1_8 (1189) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.74318 | - | - | - | - | -
TONCOR | WEST | BARBER_LK2_8 (1190) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | 0.82579 | 0.84325 | 0.83823 | 0.83968 | 0.82312 | 0.83679 | -
TONCOR | WEST | BARBER_LK2_8 (1190) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.74306 | - | - | - | - | -
TAEPTN | FAR_WEST | BARL4A (6655) | L_006655BARL4A-060385SOLSTICE4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.90521 | 0.88783 | 0.88721 | 0.88719 | -
TAEPTN | FAR_WEST | BARL4A (6655) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.073 | - | - | - | - | - | -
TAEPTN | FAR_WEST | BARL4A (6655) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.94432 | - | - | - | -
TONCOR | FAR_WEST | BARRNCH_8 (11235) | BARR RANCH - PLEASANT FARMS (LCRA) 138 KV LINE 2024 WIN - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0545 | - | - | - | - | -
TONCOR | FAR_WEST | BARRNCH_8 (11235) | L_011234QUICKRVER_T8-018660BULLHEADT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0552 | - | - | - | - | -
TONCOR | FAR_WEST | BARRNCH_8 (11235) | L_011235BARRNCH_8-018660BULLHEADT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0543 | - | - | - | - | -
TONCOR | FAR_WEST | BARRNCH_8 (11235) | PLEASANT FARMS (LCRA) - PEGASUS 138 KV (SINGLE B TO B) B WIN 2024 - FUTURE | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TBREC | NORTH_CE | BARTLETT (118) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89655 | - | 0.91981 | -
TBREC | NORTH_CE | BARTLETT (118) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.84337 | - | -
TBREC | NORTH_CE | BARTLETTSW (114) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89676 | - | 0.92 | -
TBREC | NORTH_CE | BARTLETTSW (114) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.84358 | - | -
TAEN | SOUTH_CE | BARTON (9158) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86168 | - | -
TONCOR | FAR_WEST | BASIN4A (60415) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0687 | - | - | - | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | 0.88132 | - | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89985 | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.897 | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88701 | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89146 | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89864 | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.897 | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89652 | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89017 | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89205 | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89791 | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8803 | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | TRIN-RICH (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8998 | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89084 | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | TR-TC1 (DOUBLE B TO B)_B | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89808 | - | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89734 | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89203 | - | -
TONCOR | NORTH_CE | BATCHLRD_8 (2217) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | Bus Low Volts | 0.9 | - | - | - | 0.86452 | - | - | -
TONCOR | SOUTH_CE | BATTLEGRND_8 (3690) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88373 | - | -
RBRUEN | SOUTHERN | BBREEZE_5 (161753) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.9 | - | - | - | 0.84761 | - | - | -
RBRUEN | SOUTHERN | BBREEZE_5 (161753) | E5DVA1C1_1_B | 345 | Bus Low Volts | 0.9 | - | - | - | 0.85143 | - | - | -
RBRUEN | SOUTHERN | BBREEZE_5 (161753) | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | Bus Low Volts | 0.9 | - | - | - | 0.87457 | 0.8689 | - | -
TONCOR | EAST | BBRN_OPN_8 (3509) | L_003509BBRN_OPN_8-003510PINOAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0577 | - | - | - | - | - | -
TAEN | SOUTH_CE | BC138_CAP (9002) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94636 | - | - | -
TAEN | SOUTH_CE | BC138_CAP (9002) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85733 | - | -
TONCOR | FAR_WEST | BEALSCRK_8 (11331) | BIG SPRING WEST SWITCH - BIG SPRING 138 KV WIN 2025 - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | 0.8764 | - | - | - | - | - | -
TONCOR | FAR_WEST | BEALSCRK_8 (11331) | L_001322BIGSPRIG_8-010044STEER_8C1 | 138 | Bus Low Volts | 0.9 | 0.85854 | 0.89109 | - | - | 0.8884 | - | -
TONCOR | FAR_WEST | BEALSCRK_8 (11331) | L_010044STEER_8-011316BSPGWSW_8C1 | 138 | Bus Low Volts | 0.9 | 0.85856 | 0.8911 | - | - | 0.88841 | - | -
TONCOR | FAR_WEST | BEALSCRK_8 (11331) | L_011316BSPGWSW_8-011331BEALSCRK_8C1 | 138 | Bus Low Volts | 0.9 | 0.89519 | - | - | - | - | - | -
TAEN | SOUTH_CE | BEECREEK_MB1 (9160) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94633 | - | - | -
TAEN | SOUTH_CE | BEECREEK_MB1 (9160) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.8573 | - | -
TAEN | SOUTH_CE | BEECREEK_MB2 (9159) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85729 | - | -
TBREC | NORTH_CE | BELLCNTY8 (132) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89276 | - | -
TONCOR | NORTH_CE | BENBRK_SRA_8 (18741) | L_001874BENBRK_A_8-018741BENBRK_SRA_8C2 | 138 | Bus High Volts | 1.05 | - | 1.075 | - | 1.0698 | 1.051 | 1.0508 | -
TTMPA | NORTH_CE | BENDAVIS_5 (970) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | 0.94709 | 0.93032 | - | -
TONCOR | EAST | BETO_8 (3284) | JEW-LONG_LAKE-PAL_S_8 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0582 | - | - | - | - | - | -
TONCOR | EAST | BETO_8 (3284) | L_003279LONGLKTA_8-003280LONGLAKE_8C1 | 138 | Bus High Volts | 1.05 | 1.0565 | - | - | - | - | - | -
TONCOR | EAST | BETO_8 (3284) | L_003280LONGLAKE_8-003284BETO_8C1 | 138 | Bus High Volts | 1.05 | 1.0621 | - | - | - | - | - | -
TONCOR | EAST | BETO_8 (3284) | L_003281TENNCLNY_8-003499BLAKFTAP_8C1 | 138 | Bus High Volts | 1.05 | 1.0529 | - | - | - | - | - | -
TONCOR | EAST | BETO_8 (3284) | L_003509BBRN_OPN_8-003510PINOAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0513 | - | - | - | - | - | -
TONCOR | EAST | BEULAH_5 (3307) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.87403 | - | -
RBIGST | SOUTH_CE | BIG_STAR_5 (170604) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.83672 | - | -
RBIGST | SOUTH_CE | BIG_STAR_5 (170604) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89862 | - | -
TONCOR | FAR_WEST | BIGBEND_8 (10015) | Rockhound-Blue Acres & Grey Well Draw 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | 1.072 | 1.0922 | - | - | - | - | -
TONCOR | FAR_WEST | BIGBEND_8 (10015) | Rockhound-Blue Acres 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | 1.0736 | 1.0919 | - | - | - | - | -
RBIGBR | EAST | BIGBRNM2_8 (3507) | L_003509BBRN_OPN_8-003510PINOAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0577 | - | - | - | - | - | -
TAEPTN | FAR_WEST | BIGLAKE4A (6535) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91292 | 0.89106 | 0.89655 | -
TAEPTN | FAR_WEST | BIGLAKE4A (6535) | L_006536BIGLAKE4B-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90812 | - | -
TAEPTN | FAR_WEST | BIGLAKE4A (6535) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.87945 | 0.86192 | 0.8778 | -
TAEPTN | FAR_WEST | BIGLAKE4A (6535) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.87636 | 0.85808 | 0.87421 | -
TAEPTN | FAR_WEST | BIGLAKE4A (6535) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91971 | 0.87126 | 0.85175 | 0.86826 | -
TAEPTN | FAR_WEST | BIGLAKE4A (6535) | L2020944-A | 138 | Bus Low Volts | 0.92 | - | - | - | 0.87644 | 0.8582 | 0.87427 | -
TAEPTN | FAR_WEST | BIGLAKE4A (6535) | T_006535BIGLAKE4A-006536BIGLAKE4BC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91292 | - | -
TETRTX | FAR_WEST | BIGLAKE4B (6536) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90889 | 0.91403 | -
TETRTX | FAR_WEST | BIGLAKE4B (6536) | L_006536BIGLAKE4B-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9081 | - | -
TETRTX | FAR_WEST | BIGLAKE4B (6536) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.86306 | 0.84634 | 0.86166 | -
TETRTX | FAR_WEST | BIGLAKE4B (6536) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91836 | 0.86034 | 0.84285 | 0.85852 | -
TETRTX | FAR_WEST | BIGLAKE4B (6536) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91454 | 0.85571 | 0.83613 | 0.85229 | -
TETRTX | FAR_WEST | BIGLAKE4B (6536) | L2020944-A | 138 | Bus Low Volts | 0.92 | - | - | 0.91845 | 0.86041 | 0.84298 | 0.85858 | -
TONCOR | NORTH_CE | BIGONION_5 (2466) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89782 | - | -
TONCOR | NORTH_CE | BIGONION_5 (2466) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89754 | - | -
TONCOR | NORTH_CE | BIGONION_5 (2466) | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89974 | - | -
TONCOR | NORTH_CE | BIGONION_5 (2466) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93425 | - | -
TONCOR | NORTH_CE | BIGONION_5 (2466) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89331 | - | -
TONCOR | NORTH_CE | BIGONION_5 (2466) | TRIN-RICH (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8921 | - | -
TONCOR | NORTH_CE | BIGONION_5 (2466) | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89847 | - | -
TONCOR | NORTH_CE | BIGONION_5 (2466) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89903 | - | -
TONCOR | NORTH_CE | BIGONION_5 (2466) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | Bus Low Volts | 0.9 | - | - | - | 0.88764 | - | - | -
TONCOR | SOUTH_CE | BIRDNEST_8 (3661) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.86981 | - | -
TONCOR | EAST | BLACKFOT_8 (3282) | JEW-LONG_LAKE-PAL_S_8 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0535 | - | - | - | - | - | -
TONCOR | EAST | BLACKFOT_8 (3282) | L_003279LONGLKTA_8-003280LONGLAKE_8C1 | 138 | Bus High Volts | 1.05 | 1.052 | - | - | - | - | - | -
TONCOR | EAST | BLACKFOT_8 (3282) | L_003280LONGLAKE_8-003284BETO_8C1 | 138 | Bus High Volts | 1.05 | 1.0568 | - | - | - | - | - | -
TONCOR | EAST | BLACKFOT_8 (3282) | L_003281TENNCLNY_8-003284BETO_8C1 | 138 | Bus High Volts | 1.05 | 1.0561 | - | - | - | - | - | -
TONCOR | EAST | BLACKFOT_8 (3282) | L_003499BLAKFTAP_8-003509BBRN_OPN_8C1 | 138 | Bus High Volts | 1.05 | 1.0545 | - | - | - | - | - | -
TONCOR | EAST | BLACKFOT_8 (3282) | L_003509BBRN_OPN_8-003510PINOAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0565 | - | - | - | - | - | -
TAEPTC | SOUTHERN | BLACKPOI7A (88670) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89972 | - | -
TONCOR | FAR_WEST | BLAIRLAKE_8 (11238) | L_011242CRTNYCRK_8-060792ATHEY4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89113 | - | -
TONCOR | FAR_WEST | BLAKEDRW_8 (11244) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0711 | - | - | - | - | -
TONCOR | EAST | BLAKFTAP_8 (3499) | JEW-LONG_LAKE-PAL_S_8 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0544 | - | - | - | - | - | -
TONCOR | EAST | BLAKFTAP_8 (3499) | L_003279LONGLKTA_8-003280LONGLAKE_8C1 | 138 | Bus High Volts | 1.05 | 1.053 | - | - | - | - | - | -
TONCOR | EAST | BLAKFTAP_8 (3499) | L_003280LONGLAKE_8-003284BETO_8C1 | 138 | Bus High Volts | 1.05 | 1.0578 | - | - | - | - | - | -
TONCOR | EAST | BLAKFTAP_8 (3499) | L_003281TENNCLNY_8-003284BETO_8C1 | 138 | Bus High Volts | 1.05 | 1.057 | - | - | - | - | - | -
TONCOR | EAST | BLAKFTAP_8 (3499) | L_003499BLAKFTAP_8-003509BBRN_OPN_8C1 | 138 | Bus High Volts | 1.05 | 1.0554 | - | - | - | - | - | -
TONCOR | EAST | BLAKFTAP_8 (3499) | L_003509BBRN_OPN_8-003510PINOAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0574 | - | - | - | - | - | -
TONCOR | FAR_WEST | BLUEACR_8 (23857) | ADD_CONSAVVY-GREY WELL DRAW | 138 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0511 | -
TONCOR | FAR_WEST | BLUEACR_8 (23857) | ADD_GREY WELL DRAW - Blue Acres | 138 | Bus High Volts | 1.05 | - | 1.0676 | - | 1.0722 | - | - | -
TONCOR | FAR_WEST | BLUEACR_8 (23857) | CONSAVVY - GREY WELL DRAW/MIDLAND EAST 138 KV LINE 2028 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | 1.0521 | -
TONCOR | FAR_WEST | BLUEACR_8 (23857) | Grey Well Draw - Blue Acres & Rockhound 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | 1.0686 | 1.0706 | 1.0728 | - | 1.0727 | -
TONCOR | FAR_WEST | BLUEACR_8 (23857) | L_011335BUCHRNCH_8-023858YOSEMT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0517 | 1.0508 | 1.0606 | - | 1.0517 | -
TONCOR | FAR_WEST | BLUEACR_8 (23857) | L_011388CONSAVVY_8-011396GREYWELL_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0511 | -
TONCOR | FAR_WEST | BLUEACR_8 (23857) | L_011396GREYWELL_8-023857BLUEACR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0676 | 1.0692 | 1.0722 | - | 1.0713 | -
TAEN | SOUTH_CE | BLUFFSPG (9262) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86362 | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | ALLEN SW - ANNA SW 138 KV (DOUBLE B TO B) A 23 RIDGEVIEW | 230 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | ALLEN SW - ANNA SW/BLOOMDALE SW 138 KV (DOUBLE B TO B) | 230 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 230 | Bus High Volts | 1.05 | - | - | - | 1.0669 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 230 | Bus High Volts | 1.05 | - | - | - | 1.0666 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 230 | Bus High Volts | 1.05 | - | - | - | 1.052 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | CEDAR HILL - WATERMILL (SINGLE B TO B) REINDEER | 230 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | CEDAR HILL SW 322 - NORWOOD (SINGLE B TO B) NORWOOD 345 KV TRANSFORMER NEW_LOAD | 230 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 230 | Bus High Volts | 1.05 | - | - | - | 1.0514 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | L_002217BATCHLRD_8-002466BIGONION_5C1 | 230 | Bus High Volts | 1.05 | - | - | - | 1.052 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | L_002217BATCHLRD_8-003159ELROD_5C1 | 230 | Bus High Volts | 1.05 | - | - | - | 1.0514 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | L_002466BIGONION_5-888877GLASGOW_POIC1 | 230 | Bus High Volts | 1.05 | - | - | - | 1.0511 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | L_003159ELROD_5-068091NAVARROC1 | 230 | Bus High Volts | 1.05 | - | - | - | 1.0511 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | NORWOOD - CEDAR HILL SW 345 KV (SINGLE B TO B) NEW_LOAD | 230 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | NORWOOD-CEDAR HILL SW/MOUNTAIN CREEK DCKT (DOUBLE B TO B) A BLUBONT NEW_LOAD | 230 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | Pre-contingency | 230 | Bus High Volts | 1.05 | 1.0518 | 1.0653 | 1.0651 | - | - | 1.0643 | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | SEAGOVILLE SW-WATERMILL 138 KV (SINGLE B TO B) WILMER 138/69 TRANSFORMER A GELLER | 230 | Bus High Volts | 1.05 | - | - | - | 1.0549 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | SEAGOVILLE SW-WATERMILL/WILMER-FERRIS DCKT (DOUBLE B TO B) A | 230 | Bus High Volts | 1.05 | - | - | - | 1.0549 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | Watermill Switch-Hidden Creek SW 138 kV Line(Double B TO B) new load | 230 | Bus High Volts | 1.05 | - | - | - | 1.0512 | - | - | -
RLIMES | NORTH_CE | BOARDCRK_SUB (120544) | WATERMILL-CEDAR CREST/CEDAR HILL SWITCH DCKT 138 KV (DOUBLE B TO B) D H SCHOOL 138 | 230 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | NORTH | BONHAM_8 (1808) | L_001760BONHMSS1_8-001762BONHMNW1_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0502 | -
TONCOR | NORTH | BONHMNW1_8 (1762) | L_001755ECTOR_P8-001762BONHMNW1_8C1 | 138 | Bus High Volts | 1.05 | 1.0506 | - | 1.0504 | - | - | 1.0529 | -
TONCOR | NORTH | BONHMSS1_8 (1760) | L_001755ECTOR_P8-001762BONHMNW1_8C1 | 138 | Bus High Volts | 1.05 | 1.0507 | - | 1.0505 | - | - | 1.0531 | -
TONCOR | NORTH | BONHMSS1_8 (1760) | L_001760BONHMSS1_8-001762BONHMNW1_8C1 | 138 | Bus High Volts | 1.05 | 1.0517 | - | 1.0515 | 1.0504 | 1.0502 | 1.0543 | -
TONCOR | FAR_WEST | BRECK_8 (11141) | L_011180ARYOBLUFF_T8-011199RDRUNNER_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.83236 | - | -
TONCOR | FAR_WEST | BRECK_8 (11141) | L_011183TUNSTLL_8-011199RDRUNNER_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86945 | 0.78338 | - | -
TONCOR | FAR_WEST | BRELYN_8 (11332) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.83669 | - | - | - | - | -
TBREC | NORTH_CE | BRISKET (179) | L_000181CAYOTE-000241WHITNEY8C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | NORTH_CE | BRITNRD1_5 (11901) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8997 | - | -
TONCOR | NORTH_CE | BRITNRD1_5 (11901) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93896 | - | -
TONCOR | NORTH_CE | BRITNRD1_5 (11901) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89971 | - | -
TONCOR | NORTH_CE | BRITTNRD2_5 (11902) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94183 | - | -
TAEN | SOUTH_CE | BRODIE (9169) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85954 | - | -
TAEN | SOUTH_CE | BRSTRM_MB1 (9165) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86721 | - | -
TAEN | SOUTH_CE | BRSTRM_MB2 (9163) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86723 | - | -
TSTEC | SOUTHERN | BRUNISW8 (5887) | L_005887BRUNISW8-008297BRUNI44AC1 | 138 | Bus High Volts | 1.05 | 1.0659 | 1.0689 | - | - | 1.0501 | - | -
TONCOR | SOUTH_CE | BRUSHYCRK_8 (3541) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88559 | - | -
TBTU | EAST | BRYN_BRUSCK (32867) | L_032780BRYN_RELLIS-032853BRYN_SMETANAC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85602 | 0.84891 | -
TBTU | EAST | BRYN_BRUSCK (32867) | L_032851BRYN_LENRDRD-032853BRYN_SMETANAC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.84228 | 0.85314 | -
TBTU | EAST | BRYN_KOPPE (32860) | L_032851BRYN_LENRDRD-032853BRYN_SMETANAC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89804 | - | -
TBTU | EAST | BRYN_KOPPE (32860) | L_032878BRYN_GRNPRAI-032895BRYN_WBRN138C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89906 | - | -
TBTU | EAST | BRYN_LENRDRD (32851) | BRYN_9995DC | 138 | Bus Low Volts | 0.9 | - | - | 0.84021 | 0.83636 | - | - | -
TBTU | EAST | BRYN_LENRDRD (32851) | L_032780BRYN_RELLIS-032852BRYN_STEELE_C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85936 | 0.86491 | -
TBTU | EAST | BRYN_LENRDRD (32851) | L_032851BRYN_LENRDRD-032862BRYN_ATK138C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.84587 | 0.84246 | - | - | -
TBTU | EAST | BRYN_LENRDRD (32851) | L_032852BRYN_STEELE_-032857BRYN_SNOO138C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.84774 | 0.85417 | -
TBTU | EAST | BRYN_RELLIS (32780) | BRYN_9995DC | 138 | Bus Low Volts | 0.9 | - | - | 0.84265 | 0.83876 | - | - | -
TBTU | EAST | BRYN_RELLIS (32780) | L_032780BRYN_RELLIS-032852BRYN_STEELE_C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.79473 | 0.80094 | -
TBTU | EAST | BRYN_RELLIS (32780) | L_032780BRYN_RELLIS-032853BRYN_SMETANAC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.87497 | 0.87175 | 0.72173 | 0.71246 | -
TBTU | EAST | BRYN_RELLIS (32780) | L_032851BRYN_LENRDRD-032853BRYN_SMETANAC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.8702 | 0.8669 | 0.69944 | 0.71485 | -
TBTU | EAST | BRYN_RELLIS (32780) | L_032851BRYN_LENRDRD-032862BRYN_ATK138C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.84829 | 0.84484 | - | - | -
TBTU | EAST | BRYN_RELLIS (32780) | L_032852BRYN_STEELE_-032857BRYN_SNOO138C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89887 | 0.89624 | 0.78016 | 0.78742 | -
TBTU | EAST | BRYN_RELLIS (32780) | L_032857BRYN_SNOO138-032860BRYN_KOPPEC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89557 | 0.89807 | -
TBTU | EAST | BRYN_RELLIS (32780) | L_032860BRYN_KOPPE-032895BRYN_WBRN138C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89066 | 0.8946 | -
TBTU | EAST | BRYN_RELLIS (32780) | L_032863BRYN_THMP_CK-032897BRYN_DSBY138C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89971 | - | -
TBTU | EAST | BRYN_RELLIS (32780) | L_032878BRYN_GRNPRAI-032895BRYN_WBRN138C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88405 | 0.88811 | -
TBTU | EAST | BRYN_RELLIS (32780) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.92855 | 0.93219 | -
TBTU | EAST | BRYN_SMETANA (32853) | BRYN_9995DC | 138 | Bus Low Volts | 0.9 | - | - | 0.84103 | 0.83716 | - | - | -
TBTU | EAST | BRYN_SMETANA (32853) | L_032780BRYN_RELLIS-032852BRYN_STEELE_C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.83256 | 0.83841 | -
TBTU | EAST | BRYN_SMETANA (32853) | L_032851BRYN_LENRDRD-032853BRYN_SMETANAC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.86982 | 0.86652 | 0.69896 | 0.71438 | -
TBTU | EAST | BRYN_SMETANA (32853) | L_032851BRYN_LENRDRD-032862BRYN_ATK138C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.84668 | 0.84326 | - | - | -
TBTU | EAST | BRYN_SMETANA (32853) | L_032852BRYN_STEELE_-032857BRYN_SNOO138C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.81959 | 0.82639 | -
TBTU | EAST | BRYN_SMETANA (32853) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94582 | 0.94938 | -
TBTU | EAST | BRYN_SNOO138 (32857) | L_032780BRYN_RELLIS-032853BRYN_SMETANAC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.82046 | 0.813 | -
TBTU | EAST | BRYN_SNOO138 (32857) | L_032851BRYN_LENRDRD-032853BRYN_SMETANAC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8043 | 0.81653 | -
TBTU | EAST | BRYN_STEELE_ (32852) | BRYN_9995DC | 138 | Bus Low Volts | 0.9 | - | - | 0.86995 | 0.86619 | - | - | -
TBTU | EAST | BRYN_STEELE_ (32852) | L_032780BRYN_RELLIS-032853BRYN_SMETANAC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89903 | 0.89595 | 0.76436 | 0.7558 | -
TBTU | EAST | BRYN_STEELE_ (32852) | L_032851BRYN_LENRDRD-032853BRYN_SMETANAC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89484 | 0.89167 | 0.74444 | 0.75862 | -
TBTU | EAST | BRYN_STEELE_ (32852) | L_032851BRYN_LENRDRD-032862BRYN_ATK138C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.87537 | 0.87203 | - | - | -
TBTU | EAST | BRYN_STEELE_ (32852) | L_032852BRYN_STEELE_-032857BRYN_SNOO138C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89841 | 0.89576 | 0.7796 | 0.78686 | -
TBTU | EAST | BRYN_STEELE_ (32852) | L_032860BRYN_KOPPE-032895BRYN_WBRN138C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89999 | - | -
TBTU | EAST | BRYN_STEELE_ (32852) | L_032878BRYN_GRNPRAI-032895BRYN_WBRN138C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89306 | 0.89703 | -
TBTU | EAST | BRYN_STEELE_ (32852) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94123 | 0.94481 | -
TBTU | EAST | BRYN_THMP_CK (32863) | L_032780BRYN_RELLIS-032853BRYN_SMETANAC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88119 | 0.87436 | -
TBTU | EAST | BRYN_THMP_CK (32863) | L_032851BRYN_LENRDRD-032853BRYN_SMETANAC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.86916 | 0.87907 | -
TBTU | EAST | BRYN_WBRN138 (32895) | L_032878BRYN_GRNPRAI-032895BRYN_WBRN138C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.898 | - | -
TONCOR | NORTH_CE | BRYNST1_8 (2907) | L_002903ENET1_8-002909DEEPELM_8C1 | 138 | Bus High Volts | 1.05 | - | 1.08 | 1.1018 | 1.0947 | 1.0962 | 1.0692 | -
TONCOR | NORTH_CE | BRYNST1_8 (2907) | L_002906NNET1T_8-002909DEEPELM_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0736 | 1.1084 | 1.1009 | 1.102 | 1.0756 | -
TONCOR | NORTH_CE | BRYNST1_8 (2907) | L_012441PARKD_1EN8-012445MDLTM1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0535 | - | - | - | - | -
TONCOR | NORTH_CE | BRYNST2_8 (2908) | L_012442PARKD_2EN8-012446MDLTM2_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.8897 | - | - | 0.89193 | -
TONCOR | NORTH_CE | BRYNST2_8 (2908) | L_012446MDLTM2_8-012904ENETOH2_8C1 | 138 | Bus Low Volts | 0.9 | 0.88988 | - | 0.86856 | 0.89356 | - | 0.87117 | -
TONCOR | FAR_WEST | BSPGWSW_8 (11316) | BIG SPRING WEST SWITCH - BIG SPRING 138 KV WIN 2025 - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | 0.87402 | 0.89876 | - | - | - | - | -
TONCOR | FAR_WEST | BSPGWSW_8 (11316) | L_001322BIGSPRIG_8-010044STEER_8C1 | 138 | Bus Low Volts | 0.9 | 0.85453 | 0.88888 | - | - | 0.8845 | - | -
TONCOR | FAR_WEST | BSPGWSW_8 (11316) | L_010044STEER_8-011316BSPGWSW_8C1 | 138 | Bus Low Volts | 0.9 | 0.85454 | 0.88889 | - | - | 0.88451 | - | -
TONCOR | FAR_WEST | BUCHRNCH_8 (11335) | ADD_CONSAVVY-GREY WELL DRAW | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | 1.0513 | -
TONCOR | FAR_WEST | BUCHRNCH_8 (11335) | ADD_GREY WELL DRAW - Blue Acres | 138 | Bus High Volts | 1.05 | - | 1.0676 | - | 1.0722 | - | - | -
TONCOR | FAR_WEST | BUCHRNCH_8 (11335) | CONSAVVY - GREY WELL DRAW/MIDLAND EAST 138 KV LINE 2028 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | 1.0523 | -
TONCOR | FAR_WEST | BUCHRNCH_8 (11335) | Grey Well Draw - Blue Acres & Rockhound 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | 1.0686 | 1.0706 | 1.0728 | - | 1.0727 | -
TONCOR | FAR_WEST | BUCHRNCH_8 (11335) | L_010019CRESPINRCH_8-011335BUCHRNCH_8C1 | 138 | Bus High Volts | 1.05 | - | - | 1.0698 | 1.0729 | - | 1.072 | -
TONCOR | FAR_WEST | BUCHRNCH_8 (11335) | L_011335BUCHRNCH_8-023857BLUEACR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.068 | - | - | - | - | -
TONCOR | FAR_WEST | BUCHRNCH_8 (11335) | L_011335BUCHRNCH_8-023858YOSEMT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0521 | 1.0513 | 1.061 | - | 1.0522 | -
TONCOR | FAR_WEST | BUCHRNCH_8 (11335) | L_011388CONSAVVY_8-011396GREYWELL_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | 1.0513 | -
TONCOR | FAR_WEST | BUCHRNCH_8 (11335) | L_011396GREYWELL_8-023857BLUEACR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0676 | 1.0692 | 1.0722 | - | 1.0713 | -
TONCOR | FAR_WEST | BUCHRNCH_8 (11335) | Rockhound-Blue Acres & Grey Well Draw 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | 1.1026 | 1.1236 | - | - | - | - | -
TONCOR | FAR_WEST | BUCHRNCH_8 (11335) | Rockhound-Blue Acres 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | 1.1043 | 1.1233 | - | - | - | - | -
TONCOR | NORTH_CE | BUCK_H_5 (3424) | BROWN SS - RUSSELL GAP / BUCKHORN_5 (DOUBLE B TO B ) | 345 | Bus High Volts | 1.05 | - | 1.0591 | - | - | - | - | -
TONCOR | NORTH_CE | BUCK_H_5 (3424) | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus High Volts | 1.05 | 1.0593 | - | 1.0595 | 1.0532 | 1.0576 | 1.0597 | -
TAEN | SOUTH_CE | BULICK_LD1 (9161) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94049 | - | - | -
TAEN | SOUTH_CE | BULICK_LD1 (9161) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85953 | - | -
TAEN | SOUTH_CE | BULICK_LD2 (9162) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94049 | - | - | -
TAEN | SOUTH_CE | BULICK_LD2 (9162) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85953 | - | -
RBULL | FAR_WEST | BULLCRK_1_8 (131953) | Pre-contingency | 138 | Bus High Volts | 1.05 | 1.133 | 1.1088 | 1.1353 | 1.1351 | 1.1401 | 1.0854 | -
RBULL | FAR_WEST | BULLCRK_2_8 (131954) | Pre-contingency | 138 | Bus High Volts | 1.05 | 1.133 | 1.1088 | 1.1353 | 1.1351 | 1.1401 | 1.0853 | -
RBULL | FAR_WEST | BULLCRK_3_8 (131955) | Pre-contingency | 138 | Bus High Volts | 1.05 | 1.1329 | 1.1088 | 1.1352 | 1.135 | 1.14 | 1.0853 | -
TONCOR | FAR_WEST | BULLDOG_8 (23833) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | 0.89304 | - | - | - | 0.89638 | - | -
TONCOR | FAR_WEST | BULLDOG_8 (23833) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.86634 | - | - | - | - | -
TONCOR | FAR_WEST | BULLHEAD_P8 (18661) | L_011234QUICKRVER_T8-018660BULLHEADT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0555 | - | - | - | - | -
TAEN | SOUTH_CE | BURLSN_MB1 (9120) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85889 | - | -
TAEN | SOUTH_CE | BURLSN_MB2 (9121) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.8589 | - | -
TGSEC | WEST | BUSBYCV_1 (60356) | L_006648HARGROVE4A-076011L_TWINBU8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91317 | 0.90207 | 0.91388 | -
TGSEC | WEST | BUSBYCV_1 (60356) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91542 | - | -
TGSEC | WEST | BUSBYCV_1 (60356) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91271 | - | -
TGSEC | WEST | BUSBYCV_1 (60356) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90868 | - | -
TGSEC | WEST | BUSBYCV_1 (60356) | L2020944-A | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91282 | - | -
TGSEC | WEST | BUSBYCV_1 (60356) | LCRA TSC_T429_T9426 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91365 | 0.90249 | 0.91411 | -
TCPSE | SOUTH_CE | CACHENA (5068) | E5DVA1C1_1_B | 345 | Bus High Volts | 1.05 | - | 1.0768 | - | - | - | - | -
TCPSE | SOUTH_CE | CACHENA (5068) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89937 | - | -
TCPSE | SOUTH_CE | CACHENA (5068) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus High Volts | 1.05 | - | 1.0764 | - | - | - | - | -
ERCOT | SOUTH_CE | CACHENA_S1 (170671) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89959 | - | -
TAEPTN | FAR_WEST | CALLON4A (60211) | L_060209ORIGIN4A-060716SGSA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89744 | 0.89837 | - | -
TAEPTN | FAR_WEST | CALLON4A (60211) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.0546 | - | - | - | - | - | -
TAEPTN | FAR_WEST | CALLON4A (60211) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.9193 | - | - | - | -
TAEN | SOUTH_CE | CAMERON (9171) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93712 | - | - | -
TAEN | SOUTH_CE | CAMERON (9171) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85444 | - | -
TAEN | SOUTH_CE | CAMERON (9171) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94764 | - | -
TAEPTC | SOUTHERN | CANDELA7A (8709) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.9 | - | - | - | 0.86793 | - | - | -
TAEPTC | SOUTHERN | CANDELA7A (8709) | E5DVA1C1_1_B | 345 | Bus Low Volts | 0.9 | - | - | - | 0.87439 | - | - | -
TAEPTC | SOUTHERN | CANDELA7A (8709) | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89654 | - | -
TAEN | SOUTH_CE | CARDINAL (9179) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94992 | - | - | -
TAEN | SOUTH_CE | CARDINAL (9179) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85692 | - | -
TAEPTC | SOUTHERN | CARRIZO4A (8005) | L_008005CARRIZO4A-008283ASHERTON4AC1 | 138 | Bus High Volts | 1.05 | 1.0598 | 1.0582 | 1.0597 | 1.0624 | 1.0609 | 1.0618 | -
TAEN | SOUTH_CE | CARSON (9175) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86247 | - | -
TAEPTN | WEST | CASSAVA4A (60360) | L_006036YUCCA4A-006525ESMERALD4AC1 | 138 | Bus Low Volts | 0.92 | 0.8154 | - | 0.73159 | - | - | - | -
TAEPTN | WEST | CASSAVA4A (60360) | L_006036YUCCA4A-060360CASSAVA4AC1 | 138 | Bus Low Volts | 0.92 | 0.8645 | - | 0.8148 | 0.77182 | 0.72272 | 0.7179 | -
TAEPTN | WEST | CASSAVA4A (60360) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.90774 | 0.8778 | 0.8505 | 0.85493 | -
TAEPTN | WEST | CASSAVA4A (60360) | L_006536BIGLAKE4B-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91264 | - | -
TAEPTN | WEST | CASSAVA4A (60360) | L_006648HARGROVE4A-076011L_TWINBU8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91622 | - | -
TAEPTN | WEST | CASSAVA4A (60360) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88938 | 0.87272 | 0.88942 | -
TAEPTN | WEST | CASSAVA4A (60360) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88649 | 0.86909 | 0.88577 | -
TAEPTN | WEST | CASSAVA4A (60360) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.87973 | 0.86335 | 0.88015 | -
TAEPTN | WEST | CASSAVA4A (60360) | L2020944-A | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88657 | 0.86922 | 0.88584 | -
TAEPTN | WEST | CASSAVA4A (60360) | LCRA TSC_T429_T9426 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91701 | - | -
TAEPTN | WEST | CASSAVA4A (60360) | T_006535BIGLAKE4A-006536BIGLAKE4BC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91673 | - | -
TTNMP | FAR_WEST | CAYMUSJ_1 (38413) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0608 | - | - | - | - | -
TBREC | NORTH_CE | CAYOTE (181) | L_000181CAYOTE-000241WHITNEY8C1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
TAEPTC | SOUTHERN | CEBOLLA7A (8601) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | 0.8469 | - | - | -
TAEPTC | SOUTHERN | CEBOLLA7A (8601) | E5DVA1C1_1_B | 345 | Bus Low Volts | 0.92 | - | - | - | 0.85072 | - | - | -
TAEPTC | SOUTHERN | CEBOLLA7A (8601) | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | Bus Low Volts | 0.92 | - | - | - | 0.87387 | 0.86803 | - | -
TBREC | NORTH_CE | CEDARHILL (220) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91835 | 0.88816 | 0.8531 | 0.91602 | -
TBREC | NORTH_CE | CEDARHILL (220) | KEMP RANCH - SARDIS 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90541 | - | -
TBREC | NORTH_CE | CEDARHILL (220) | KEMP RANCH - SARDIS 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90541 | - | -
TBREC | NORTH_CE | CEDARHILL (220) | KEMP RANCH - SOAP CREEK / SARDIS 138 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89949 | - | -
TBREC | NORTH_CE | CEDARHILL (220) | L_000203SARDIS8-002309WAX_NW_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90432 | - | -
TBREC | NORTH_CE | CEDARHILL (220) | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89422 | - | -
TBREC | NORTH_CE | CEDARHILL (220) | L_002305AIRPRD_T8-002307MDLTHTXI1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89753 | - | -
TBREC | NORTH_CE | CEDARHILL (220) | L_002307MDLTHTXI1_8-012307NEWBRCH_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90879 | - | -
TBREC | NORTH_CE | CEDARHILL (220) | L_002308MDLTH_S_8-002309WAX_NW_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89836 | - | -
TBREC | NORTH_CE | CEDARHILL (220) | L_002308MDLTH_S_8-012307NEWBRCH_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91207 | - | -
TBREC | NORTH_CE | CEDARHILL (220) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.919 | - | -
TBREC | NORTH_CE | CEDARHILL (220) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94638 | - | -
TBREC | NORTH_CE | CEDARHILL (220) | SOAP CREEK - CEDAR HILL / SARDIS 138 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90294 | - | -
TRAYBN | NORTH_CE | CELINARC (6943) | L_000675ROCKHILL-002380WESTRIDGE1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
TRAYBN | NORTH_CE | CELINARC (6943) | L_002370COLLINSS1_8-002380WESTRIDGE1_8C1 | 138 | Bus Low Volts | 0.9 | 0.88957 | - | 0.88267 | 0.87737 | 0.87743 | 0.87816 | -
TONCOR | NORTH_CE | CELINASE1_8 (2350) | L_000675ROCKHILL-002380WESTRIDGE1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
TONCOR | NORTH_CE | CELINASE1_8 (2350) | L_002350CELINASE1_8-002366WILSNCRK_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0515 | - | - | - | - | -
TONCOR | NORTH_CE | CELINASE1_8 (2350) | L_002370COLLINSS1_8-002380WESTRIDGE1_8C1 | 138 | Bus Low Volts | 0.9 | 0.89005 | - | 0.88316 | 0.87786 | 0.87792 | 0.87865 | -
1 | NORTH_CE | CELINAW_RC (6793) | L_002370COLLINSS1_8-002380WESTRIDGE1_8C1 | 138 | Bus Low Volts | 0.9 | 0.89079 | - | 0.88392 | 0.87862 | 0.87867 | 0.8794 | -
TETRTX | SOUTHERN | CENIZO7A (80220) | E_DUKE_CC1_TRAIN | 345 | Bus High Volts | 1.05 | - | - | - | - | 1.0503 | - | -
TETRTX | SOUTHERN | CENIZO7A (80220) | E_NEDIN_CC1_TRAIN | 345 | Bus High Volts | 1.05 | - | - | - | - | 1.0508 | - | -
TETRTX | SOUTHERN | CENIZO7A (80220) | L_008601CEBOLLA7A-008902RIOHONDO7CC1 | 345 | Bus High Volts | 1.05 | - | - | - | - | 1.05 | - | -
TETRTX | SOUTHERN | CENIZO7A (80220) | L_008601CEBOLLA7A-080076AJO7AC1 | 345 | Bus High Volts | 1.05 | - | - | - | - | 1.0501 | - | -
TETRTX | SOUTHERN | CENIZO7A (80220) | L_080220CENIZO7A-161105BORDAS_5C1 | 345 | Bus High Volts | 1.05 | - | - | - | - | 1.0508 | - | -
TETRTX | SOUTHERN | CENIZO7A (80220) | L1000097 | 345 | Bus High Volts | 1.05 | - | - | - | - | 1.05 | - | -
TETRTX | SOUTHERN | CENIZO7A (80220) | S_080220CENIZO7A1 | 345 | Bus High Volts | 1.05 | - | - | - | - | 1.051 | - | -
TETRTX | SOUTHERN | CENIZO7C (80225) | Pre-contingency | 345 | Bus High Volts | 1.05 | - | 1.0579 | - | - | 0.9473 | - | -
TETRTX | SOUTHERN | CENIZO7C (80225) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | 1.0579 | - | - | 0.9473 | - | -
TONCOR | NORTH_CE | CENTURY1_5 (1929) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89881 | - | -
TONCOR | NORTH_CE | CENTURY1_5 (1929) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94204 | - | -
TONCOR | NORTH_CE | CENTURY3_5 (1930) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94589 | - | -
TONCOR | EAST | CENTVILL_8 (3358) | L_003358CENTVILL_8-003394JEWETTA_8C1 | 138 | Bus High Volts | 1.05 | 1.0727 | - | - | - | - | - | -
TAEN | SOUTH_CE | CF138_CAP (9005) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86282 | - | -
TAEPTC | SOUTHERN | CHALUPA_138 (162253) | L_008601CEBOLLA7A-008902RIOHONDO7CC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.057 | 1.0504 | - | -
TAEPTC | SOUTHERN | CHALUPA_138 (162253) | L1000097 | 138 | Bus High Volts | 1.05 | - | - | - | 1.057 | 1.0504 | - | -
TAEPTC | SOUTHERN | CHALUPA_138 (162253) | M10000841000093-1A | 138 | Bus High Volts | 1.05 | - | - | - | 1.0522 | - | - | -
TAEPTC | SOUTHERN | CHALUPA_138 (162253) | P7/C5-SHRY-1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TAEPTC | SOUTHERN | CHALYBE4A (8735) | E_NEDIN_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | 0.8885 | - | - | -
TAEPTC | SOUTHERN | CHALYBE4A (8735) | E5DVA1C1_1_B | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89883 | - | - | -
TAEPTC | SOUTHERN | CHALYBE4A (8735) | P7/C5-SHRY-1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91549 | 0.90529 | 0.9106 | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88861 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | ARGENTA_CON | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88172 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89496 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89764 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | DVCPA1C21B_1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8915 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | DVCPA1C21B_2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89369 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | E_B_DAVIS_CC1_TRAIN | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8784 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | E_CCEC_CC1_TRAIN | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89217 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | E_INGLCOSW_CC1_TRAIN | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.86194 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | E_LGE_CC1_TRAIN | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89055 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89031 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | E_NUECES_B_CC1_TRAIN | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.86587 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | G_080039LUCERO7AUS1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89791 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | G_163521PEREGRN_S1US1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89899 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | G_163641CHARGER_S1US1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.87357 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | G_170126CALAVER_JKS2UL2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89308 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | Haber - Coleto Creek | 345 | Bus Low Volts | 0.9 | - | - | - | - | - | 0.82981 | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.85928 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.84702 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88488 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_005133ELMCREEK-005380SHAULAC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88047 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89322 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_005380SHAULA-005915SO_TEX__345AC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89244 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_005725PAWNEESW5-008164COLETO7AC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.86832 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88017 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_008249ANGSTRM7A-008676STATIC7AC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.86453 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89854 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.84501 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_008579KATOEN7A-008606GODDARD7AC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.87041 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_008606GODDARD7A-888858ARGENTA_POIC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89152 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88172 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_080071ZORILLO7A-080076AJO7AC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89434 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_081003HABER7A-008164COLETO7AC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89361 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_081003HABER7A-008164COLETO7AC2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89361 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_084555AMBER7A-085000N_SHARPE7AC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89644 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89585 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | LCRA TSC_T255_TAE3121_1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89924 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | M10000271115801 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88873 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | M105311105321 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89051 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | M115851115803 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89434 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | MB100002711580 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88873 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | MB1158011585 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89434 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | N5GSU2_B | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89308 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | P7-1_E1>>T1839X1_ERC | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89416 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | P7-1_E1>>T1839X2_ERC | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89195 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | P7-1_E1>>T2764Y_ERCa | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88984 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | SAN_PAT_CON | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.87003 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | STP - HOUDINI & STP - SHAULA | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89025 | - | -
ERCOT | SOUTHERN | CHARGER_S1 (163641) | WAP - HOUDINI & STP - SHAULA | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89489 | - | -
TAEPTC | SOUTHERN | CHENIRE4A (8568) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88875 | - | -
TAEPTC | SOUTHERN | CHENIRE4A (8568) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89569 | - | -
TAEPTC | SOUTHERN | CHENIRE4A (8568) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91125 | - | -
TAEPTC | SOUTHERN | CHENIRE4B (8575) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88875 | - | -
TAEPTC | SOUTHERN | CHENIRE4B (8575) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89569 | - | -
TAEPTC | SOUTHERN | CHENIRE4B (8575) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91125 | - | -
TAEPTN | FAR_WEST | CHERRYCR4A (60206) | L_060209ORIGIN4A-060716SGSA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89606 | 0.89684 | - | -
TAEPTN | FAR_WEST | CHERRYCR4A (60206) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.0538 | - | - | - | - | - | -
TAEPTN | FAR_WEST | CHERRYCR4A (60206) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.91822 | - | - | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89508 | - | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89987 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89635 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88221 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88617 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89893 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | GLASGOW_CON | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89867 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89946 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89635 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89893 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89887 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89978 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89307 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88763 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89817 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | 0.9417 | 0.92497 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8874 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | TRIN-RICH (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89996 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89328 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89399 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89182 | - | -
TONCOR | NORTH_CE | CHILSW1_5 (2420) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | Bus Low Volts | 0.9 | - | - | - | 0.88818 | - | - | -
TONCOR | WEST | CHINAGRV_8 (1318) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | 0.88457 | 0.89735 | 0.89075 | 0.89148 | 0.87979 | 0.89431 | -
TONCOR | WEST | CHINAGRV_8 (1318) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.83169 | - | - | - | - | -
TONCOR | WEST | CHINAGRVX1_8 (19521) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | 0.84883 | 0.86449 | 0.85867 | 0.85982 | 0.84528 | 0.85934 | -
TONCOR | WEST | CHINAGRVX1_8 (19521) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.77812 | - | - | - | - | -
TONCOR | WEST | CHINAGRVX2_8 (19520) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | 0.8547 | 0.87025 | 0.86446 | 0.86561 | 0.85117 | 0.86513 | -
TONCOR | WEST | CHINAGRVX2_8 (19520) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.78464 | - | - | - | - | -
TAEPTN | NORTH | CHLD4A (6030) | L_006030CHLD4A-006135PADU4AC1 | 138 | Bus Low Volts | 0.92 | 0.81153 | - | 0.81378 | 0.81386 | 0.82934 | 0.89273 | -
TAEPTN | NORTH | CHLD4A (6030) | L_006032CHIL2A-006053KIRKLAND2AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | - | 0.91969 | -
TAEPTN | NORTH | CHLD4A (6030) | L_006048PAUL2A-006051QUAN2AC1 | 138 | Bus Low Volts | 0.92 | 0.81705 | - | 0.82072 | 0.8176 | 0.81371 | 0.8171 | -
TAEPTN | NORTH | CHLD4A (6030) | L_006050LKPAULS4A-006060VERN4AC1 | 138 | Bus Low Volts | 0.92 | 0.91479 | - | 0.91998 | 0.91586 | - | - | -
TAEPTN | NORTH | CHLD4A (6030) | L_006051QUAN2A-060446GOODLETT2AC1 | 138 | Bus Low Volts | 0.92 | 0.89636 | - | 0.90205 | - | 0.89757 | 0.90095 | -
TAEPTN | NORTH | CHLD4A (6030) | L_006053KIRKLAND2A-060446GOODLETT2AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | - | 0.91975 | -
TAEPTN | NORTH | CHLD4A (6030) | L_006117EASTMUND4B-006320TARDIS4AC1 | 138 | Bus Low Volts | 0.92 | 0.89232 | - | 0.89846 | 0.89537 | 0.89845 | 0.90222 | -
TAEPTN | NORTH | CHLD4A (6030) | L_006135PADU4A-006320TARDIS4AC1 | 138 | Bus Low Volts | 0.92 | 0.86635 | 0.90137 | 0.86894 | 0.87245 | 0.86833 | 0.86824 | -
TAEPTN | NORTH | CHLD4A (6030) | L_006140MATA2A-140082WEC_1_8C1 | 138 | Bus Low Volts | 0.92 | 0.91896 | - | - | - | - | - | -
TAEPTN | NORTH | CHLD4A (6030) | L2020025-2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | - | 0.91986 | -
TAEPTN | NORTH | CHLD4A (6030) | MB2002820034 | 138 | Bus Low Volts | 0.92 | 0.81709 | - | 0.81897 | 0.81764 | 0.81365 | 0.81712 | -
TAEPTN | NORTH | CHLD4A (6030) | Pre-contingency | 138 | Bus Low Volts | 0.95 | 0.94047 | - | 0.94505 | 0.94475 | 0.94571 | - | -
TAEPTN | NORTH | CHLD4A (6030) | T_006048PAUL2A-006050LKPAULS4AC1 | 138 | Bus Low Volts | 0.92 | 0.85488 | - | 0.85559 | 0.85453 | 0.85154 | 0.85175 | -
TAEPTN | NORTH | CHLD4A (6030) | T200004 | 138 | Bus Low Volts | 0.92 | 0.91732 | - | - | 0.91829 | - | - | -
TAEPTN | NORTH | CHLD4A (6030) | T200012 | 138 | Bus Low Volts | 0.92 | 0.84606 | - | 0.84734 | 0.84778 | 0.84619 | 0.84917 | -
TAEPTN | NORTH | CHLD4A (6030) | T200013 | 138 | Bus Low Volts | 0.92 | 0.91479 | - | 0.91998 | 0.91586 | - | - | -
TAEPTN | NORTH | CHLD4A (6030) | T200014 | 138 | Bus Low Volts | 0.92 | 0.81054 | - | 0.81264 | 0.81259 | 0.83389 | 0.89276 | -
TAEPTC | WEST | CHPRROSA4A (8007) | L_008005CARRIZO4A-008283ASHERTON4AC1 | 138 | Bus High Volts | 1.05 | 1.051 | - | 1.0509 | 1.0536 | 1.0521 | 1.053 | -
TAEPTC | SOUTHERN | CHRGRPOI7A (8678) | Haber - Coleto Creek | 345 | Bus Low Volts | 0.95 | - | - | - | - | - | 0.82965 | -
TAEPTC | SOUTHERN | CHRGRPOI7A (8678) | L_008249ANGSTRM7A-008676STATIC7AC1 | 345 | Bus High Volts | 1.05 | - | 1.0592 | - | - | - | 0.94839 | -
TAEPTC | SOUTHERN | CHRGRPOI7A (8678) | L_008249ANGSTRM7A-008676STATIC7AC1 | 345 | Bus Low Volts | 0.95 | - | 1.0592 | - | - | - | 0.94839 | -
TAEPTC | SOUTHERN | CHRGRPOI7A (8678) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.91876 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | AEN_FPP-HO¦LY | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9385 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | AEN_LP-AU¦DL_2013 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94345 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | BAS_RANCH_CON | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94902 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93999 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94555 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94978 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | DVCPA1C21B_1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94544 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | G_170126CALAVER_JKS2UL2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94767 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | G_888839BAS_RANCH_POIUC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94906 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | G_RIO_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94587 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | J5LCA1C1_B | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94577 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.8366 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.8985 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94543 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | L_005133ELMCREEK-005380SHAULAC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93679 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | L_005915SO_TEX__345A-008715RADIANT7AC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94616 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93627 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | L_007055L_FPPYD25_1Y-009073HOLMANC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94983 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | N5GSU2_B | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94767 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | P7-1_E1>>T1839X2_ERC | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94577 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | P7-1_E1>>T3944Z_ERC | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94378 | - | -
TAEN | SOUTH_CE | CISTERN (9043) | Pre-contingency | 345 | Bus Low Volts | 0.98 | - | - | - | - | 0.97216 | - | -
TAEN | SOUTH_CE | CL138_CAP (9003) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94995 | - | - | -
TAEN | SOUTH_CE | CL138_CAP (9003) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85695 | - | -
TONCOR | NORTH_CE | CLEBRN_8 (2290) | BEPC_306 | 138 | Bus Low Volts | 0.9 | - | 0.8984 | - | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_8 (2290) | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.87886 | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_8 (2290) | L_000442RAILPORT-001908VENUSC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.87603 | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_8 (2290) | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89784 | - | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_N_8 (2280) | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89085 | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_N_8 (2280) | L_000442RAILPORT-001908VENUSC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.88833 | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_W_8 (2291) | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89898 | - | - | - | -
TONCOR | NORTH_CE | CLEBRN_W_8 (2291) | L_000442RAILPORT-001908VENUSC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89639 | - | - | - | -
TONCOR | NORTH_CE | CLEBRNSW_8 (2279) | BEPC_306 | 138 | Bus Low Volts | 0.9 | - | 0.89761 | - | - | - | - | -
TONCOR | NORTH_CE | CLEBRNSW_8 (2279) | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.87752 | - | - | - | -
TONCOR | NORTH_CE | CLEBRNSW_8 (2279) | L_000442RAILPORT-001908VENUSC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.87467 | - | - | - | -
TONCOR | NORTH_CE | CLEBRNSW_8 (2279) | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89704 | - | - | - | - | -
TAEPTC | SOUTHERN | CLLCOTTE4A (8027) | L_008027CLLCOTTE4A-008452LON_HILL4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89063 | 0.84755 | 0.89933 | -
TONCOR | NORTH_CE | CNVLSW1_5 (2453) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93097 | - | -
TAEPTC | COAST | COBRA7A (8728) | E5DVA1C1_1_B | 345 | Bus Low Volts | 0.92 | - | - | - | 0.90411 | - | - | -
TAEPTC | COAST | COBRA7A (8728) | Haber - Coleto Creek | 345 | Bus Low Volts | 0.92 | - | - | - | - | - | 0.79488 | -
TAEPTC | COAST | COBRA7A (8728) | L_005915SO_TEX__345A-008715RADIANT7AC1 | 345 | Bus High Volts | 1.05 | - | 1.0526 | - | - | - | - | -
TAEPTC | COAST | COBRA7A (8728) | L_008249ANGSTRM7A-008676STATIC7AC1 | 345 | Bus High Volts | 1.05 | - | 1.0599 | - | - | - | - | -
TAEPTC | COAST | COBRA7A (8728) | L_008676STATIC7A-081003HABER7AC1 | 345 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TAEPTC | COAST | COBRA7A (8728) | L_008728COBRA7A-081003HABER7AC1 | 345 | Bus High Volts | 1.05 | - | 1.0593 | - | - | - | - | -
TAEPTC | COAST | COBRA7A (8728) | L_081003HABER7A-081004CRUNCH7AC1 | 345 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TAEPTC | COAST | COBRA7A (8728) | M11227210000105-2 | 345 | Bus High Volts | 1.05 | - | 1.0526 | - | - | - | - | -
TAEPTC | COAST | COBRA7A (8728) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.87419 | - | -
TAEPTC | SOUTHERN | COFFPORT4A (8914) | E_NEDIN_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | 0.90376 | - | - | -
TAEPTC | SOUTHERN | COFFPORT4A (8914) | E5DVA1C1_1_B | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91356 | - | - | -
ERCOT | SOUTHERN | COLETO_1_8 (160122) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88894 | - | -
ERCOT | SOUTHERN | COLETO_1_8 (160122) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8827 | - | -
ERCOT | SOUTHERN | COLETO_1_8 (160122) | L_005725PAWNEESW5-008164COLETO7AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89326 | - | -
ERCOT | SOUTHERN | COLETO_1_8 (160122) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89095 | - | -
ERCOT | SOUTHERN | COLETO_1_8 (160122) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94436 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | ARGENTA_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91493 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | E_B_DAVIS_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91048 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90231 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | E_NEDIN_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91984 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | E_NUECES_B_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90148 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | G_163641CHARGER_S1US1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91695 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88894 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8827 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91622 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | L_005133ELMCREEK-005380SHAULAC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.912 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | L_005725PAWNEESW5-008164COLETO7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89326 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91313 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89095 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | L_008579KATOEN7A-008606GODDARD7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90887 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | L_008676STATIC7A-081003HABER7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90479 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91602 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | M10000271115801 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91847 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | MB100002711580 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91847 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94436 | - | -
TAEPTC | SOUTHERN | COLETO4A (8162) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90915 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | 3WT_008164COLETO7A_008162COLETO4A_008160CC1TERT C 1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.919 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | 3WT_008164COLETO7A_008162COLETO4A_008181CC2TERT C 2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9193 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | AEN_FPP-HO¦LY | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9189 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | AEN_LP-AU¦DL_2013 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9143 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | AEN_LY-FPP:CIS-HO | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91103 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | AEN_LY-FPP¦CIS | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90811 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89754 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | AEN_P7 FPP-LP.DC_1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91763 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | AEN_P7 FPP-LP.DC_2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91765 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | ARGENTA_CON | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89187 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | BAS_RANCH_CON | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90836 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90272 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90514 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91897 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | BLUBIRD_CON | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91889 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9078 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | CACTUS_CON | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91701 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | DVCPA1C21B_1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89972 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | DVCPA1C21B_2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90175 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_B_DAVIS_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.88807 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_BASTEN_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91701 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_BRAUNIG_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91223 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_CCEC_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9012 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_DUKE_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90806 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_FERGCC_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91731 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_FRNYPP_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91826 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_FRNYPP_CC2_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91824 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_GUADG_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91609 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_GUADG_CC2_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91615 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_INGLCOSW_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.87714 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_JCKCNTY2_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91995 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_LGE_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90049 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_LOSTPI_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91886 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89853 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_NUECES_B_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.87758 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_OECCS_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91895 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_OECCS_CC2_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91893 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_PANDA_S_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91981 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_PANDA_T1_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91854 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_PANDA_T2_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91856 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_VICTORIA_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91257 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_WCPP_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91866 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_WHCCS_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91922 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E_WHCCS2_CC2_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91727 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E5P4A1C1_B | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91652 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E5SCA1C1_B | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91658 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | E5T5A1C1_B | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91473 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_000575JCKCNTY5UN1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91964 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_006100OKLA7AUC0 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91917 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_007044L_MARION5_1YUN1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91662 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_007048L_GARFIE5_1YUN1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9182 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_008249ANGSTRM7AUS1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91528 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_008573BONILLA7AUW1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91751 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_010012METEOR_5US1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91962 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_080039LUCERO7AUS1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90713 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_080039LUCERO7AUS2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91043 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_080219LOBO7AUS1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91745 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_080219LOBO7AUS2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91999 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_080355DELSOL7AUS1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91949 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_085000N_SHARPE7AUS1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91901 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_113051GARCITAS_S1US1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91337 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_150111CPSES_UNIT1UU1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91644 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_150112CPSES_UNIT2UU2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9164 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_150741SCES_UNIT1UL1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9188 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_160101B_D_B_DAVIG1UN1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91026 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_160131SAN_SANMIGG1UL1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91502 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_160151INGLCOS_CTG1UPE | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.914 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_160152INGLCOS_CTG2UPE | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.914 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_160153INGLCOSW_STGUPE | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91284 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_160201LGE_LGE_GT1UPE | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91486 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_160202LGE_LGE_GT2UPE | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91537 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_160203LGE_LGE_STGUPE | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91973 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_160261CCEC_GT1UPE | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91811 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_160262CCEC_GT2UPE | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91811 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_160263CCEC_ST1UPE | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91772 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_160391PAP1_PAP1UW1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91941 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_160392COTTON_PAP2UW1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91601 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_161501MIDWIND_UNIUW1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91771 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_161651PATWND_UNIT1UW1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91721 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_161951STELLA_W1UW1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91986 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_162201CRANEL_W1UW1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91894 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_162911BLACKJAK_W1UW1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91928 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_162912BLACKJAK_W2UW2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9193 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_163071ALGODON_W1UW1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91937 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_163521PEREGRN_S1US1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90487 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_163641CHARGER_S1US1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89345 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_163691REDONDA_S1US1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91837 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_163881TULSITA_S1US1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91674 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_163931OUTPOST_S1US1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91365 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_170101FPPYD_FPP_G1UL1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91954 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_170102FPPYD_FPP_G2UL2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91972 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_170126CALAVER_JKS2UL2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89967 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_170671CACHENA_S1US1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91683 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_888839BAS_RANCH_POIUC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90838 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_888851TRIFECTA_POIUN1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91988 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_888858ARGENTA_POIUS1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91368 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_888879BLUBIRD_POIUS1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.919 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | G_RIO_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90996 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | HOLLY_CON | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91855 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | J5GSU4_B | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91903 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | J5LCA1C1_B | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90993 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | J5ST1_B | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91903 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91967 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91709 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_001839STONCRK_8-140002SHER1_TLC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91983 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91758 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91824 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91825 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91954 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.865 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_003687BELL_E_5-003705BRANGUS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91975 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.85739 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.8938 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_005133ELMCREEK-005380SHAULAC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.88942 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90137 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_005380SHAULA-005915SO_TEX__345AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90067 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_005607WRBRTN8-008172VICTORIA4AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91975 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_005607WRBRTN8-008912MEDIOCR4AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91864 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_005725PAWNEESW5-008164COLETO7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.85928 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_005779REDSWTAP8-005784REDGATESW8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91664 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_005779REDSWTAP8-161031REDGATE_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91664 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_005895PEARSALLSUB8-058959PEARSALLSCB8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91993 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.88923 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91701 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008144SEADRFTC4A-008189TUNGSTEN4AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91366 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008144SEADRFTC4A-080065MELNCRK4AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91355 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008162COLETO4A-008172VICTORIA4AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91559 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008162COLETO4A-008172VICTORIA4AC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91501 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008164COLETO7A-008673RAPTOR7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89962 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008172VICTORIA4A-110883VIC_SU5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91851 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008172VICTORIA4A-110884VIC_SU6C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91993 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008249ANGSTRM7A-008676STATIC7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90317 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008249ANGSTRM7A-008956WHITEPT7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91577 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008249ANGSTRM7A-080039LUCERO7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91982 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008318RIOHONDO7A-162745LMJDSW_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91805 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008319RIOHONDO4A-160750LV1_AB_8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91501 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008380NEDIN4A-160234NEDIN_1_8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91692 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008380NEDIN4A-160235NEDIN_2_8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91692 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008422I_DUPSW4A-008425INGLESID4AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91686 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008437RINCON4B-080065MELNCRK4AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91914 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9067 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.86267 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008458B_DAVIS4A-160105B_DAVIS_1_8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91026 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008458B_DAVIS4A-160106B_DAVIS_2_8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90874 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008458B_DAVIS4A-160107B_DAVIS_3_9C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91685 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008458B_DAVIS4A-160108B_DAVIS_4_9C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91685 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008579KATOEN7A-008606GODDARD7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.88361 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008606GODDARD7A-888858ARGENTA_POIC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90102 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008624GRISSOM7A-008673RAPTOR7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91264 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008659NAISMITH7A-080039LUCERO7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91975 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008663ELSUZPOI7A-163415ELSAUZ_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91777 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008676STATIC7A-081003HABER7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.87461 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008912MEDIOCR4A-008920HAISLEY4AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91894 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008963HEC4A-008981HECGT14AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91947 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008963HEC4A-008983HECST14AC3 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91879 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008980FRONTERA4A-160180FRONT_EC_C1TC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91839 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008980FRONTERA4A-160181FRONT_EC_C2TC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91839 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_008980FRONTERA4A-160182FRONT_EC_STTC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91813 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_009043CISTERN-009073HOLMANC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91863 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_009043CISTERN-009074LYTTON5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91704 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89144 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_080071ZORILLO7A-080076AJO7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90236 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_080071ZORILLO7A-080171SARITA7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9107 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_080072STELPOI7A-080076AJO7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91978 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_080072STELPOI7A-161953STELLA_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91982 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_080076AJO7A-085000N_SHARPE7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9126 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_080078REFORZAR7A-084555AMBER7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91216 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_080171SARITA7A-160299BAFFIN_2_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91073 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_080219LOBO7A-163223CORAZON_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91865 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_080259PELICAN4A-160394COTTON_1_8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91601 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_080259PELICAN4A-160395PAP1_1_8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91941 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_080260GILA4A-160095NUECES_B_2_8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91629 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_080260GILA4A-160096NUECES_B_3_8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91632 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_080309LASPULGA4A-160694REDFISH_8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91983 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_080503SANTASW4A-085001N_SHARPE4AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91709 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_080503SANTASW4A-161455CHAWIND_8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91711 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_080509LADKPOI7A-161753BBREEZE_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9196 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_084555AMBER7A-085000N_SHARPE7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90574 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_085008PATPOI7A-161653PATWIND_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91666 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_088173JCKSLPOI4A-163575JACKALOPE_8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91648 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_088574WRAYPOI7A-162695ELTRUENO_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91924 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_088606JRVKPOI7A-162005KNKWA1_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91782 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_088624CRNLLPOI7A-162204CRANEL_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9161 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_088670BLACKPOI7A-162915BLACKJAK_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91116 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_888858ARGENTA_POI-008689TANGO7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91201 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90414 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L1000027 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91978 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L10010434_MODIFIED_BY_MZ | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91943 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L10010717 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91947 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L10011226 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.916 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L10011585 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9107 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L10011690 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91805 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L10011910-1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91762 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L10012087 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91666 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L10012091 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91782 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L10012100 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91851 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L10012105 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91993 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L10012915 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91709 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L11000026 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9161 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L11000047 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91924 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L11000090 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91773 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L11000095 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9196 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | L11000105 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91709 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | LAKE CREEK - RATTLE SNAKE 345 KV WITH SANDY UNIT (SINGLE B TO B) | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9188 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | LCRA TSC_T185_T246 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91406 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | LCRA TSC_T255_TAE3121_1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90615 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91162 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | M10000242128101-1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89863 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | M10000244128102-1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89874 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | M10000254106503-1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9191 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | M10000271115801 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.897 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | M102253112251-1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91606 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | M105311105321 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90047 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | M105902106102-1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91713 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | M115851115803 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90236 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | M128103100534 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91354 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | M128104100523 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91418 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | M128152129153 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91566 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | MB100002412810-1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89882 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | MB100002711580 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.897 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | MB1005312810 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91373 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | MB106501000025-2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91963 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | MB1101411110-1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91566 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | MB1158011585 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90236 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | MB1281010052 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91436 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | MB1291012930 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9135 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | MB1291512815a | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91576 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | MB210140210145-AAAAB | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91974 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | MBAM-REFORnew | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90878 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91864 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91889 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | N5GSU2_B | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89967 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91506 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | NEW_CTG_P7.1_5725_8689_1_2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91296 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | P7-1_E1>>T1839X1_ERC | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90218 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | P7-1_E1>>T1839X2_ERC | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90013 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | P7-1_E1>>T1850A1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91968 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | P7-1_E1>>T2764Y_ERCa | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89837 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | P7-1_E1>>T4848K | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91707 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | P7-1_E1>>T7475A | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91789 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | P7-1_E1>>T7498C_ERC | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91939 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | P7-1_E1>>T9899A | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91728 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | P7-1_E1>LEG-OUTLAW_ERC | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91617 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.92435 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | R4U2A5C1_1_B | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91216 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | RAT_SNAKE-SNDY_CREEK_5 (SINGLE B TO B) | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9188 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | SAN_PAT_CON | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.88418 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | STECL_10262 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91502 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | STP - HOUDINI & STP - SHAULA | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89874 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91714 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91437 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | TRIFECTA_CON | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91987 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | TRIN-RICH (DOUBLE B TO B) | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91935 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91699 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91738 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91708 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | U3GSU1_B | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91622 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91436 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | WAP - HOUDINI & STP - SHAULA | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90284 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91866 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | XFMR-SANDYCRK_5-01 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9188 | - | -
TAEPTC | SOUTHERN | COLETO7A (8164) | XFMR-WHCCS2_5-1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91893 | - | -
TONCOR | NORTH_CE | COLLINSS1_5 (2372) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94949 | - | -
TAEN | SOUTH_CE | COMMONFD (9183) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86279 | - | -
TONCOR | NORTH_CE | COTTONWD_8 (2304) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87766 | 0.84434 | - | -
TONCOR | NORTH_CE | COTTONWD1_8 (2301) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94172 | - | -
TONCOR | NORTH_CE | COTTONWD1_8 (2301) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89786 | - | -
TONCOR | NORTH_CE | COTTONWD2_8 (2302) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89111 | - | -
TONCOR | NORTH_CE | COTTONWD2_8 (2302) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.93188 | - | -
TONCOR | NORTH_CE | COTTONWD2_8 (2302) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89414 | - | -
TONCOR | NORTH_CE | COURTLND1_5 (1931) | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89538 | - | -
TONCOR | NORTH_CE | COURTLND1_5 (1931) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89735 | - | -
TONCOR | NORTH_CE | COURTLND1_5 (1931) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94035 | - | -
TONCOR | FAR_WEST | COYANOSA_8 (1239) | L_011242CRTNYCRK_8-060792ATHEY4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89473 | - | -
TONCOR | FAR_WEST | COYANOSAS_8 (11246) | L_011242CRTNYCRK_8-060792ATHEY4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89652 | 0.86806 | 0.88406 | -
TONCOR | FAR_WEST | COYANOSNW_8 (1243) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0711 | - | - | - | - | -
TONCOR | FAR_WEST | COYANOSNW2_8 (1247) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0711 | - | - | - | - | -
TONCOR | WEST | CP SOUTH (900126) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | 0.84845 | 0.86413 | 0.85831 | 0.85947 | 0.8449 | 0.85897 | -
TONCOR | WEST | CP SOUTH (900126) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.77759 | - | - | - | - | -
1 | NORTH_CE | CPR_RC (6790) | L_002370COLLINSS1_8-002380WESTRIDGE1_8C1 | 138 | Bus Low Volts | 0.9 | 0.88957 | - | 0.88255 | 0.87707 | 0.87702 | 0.87775 | -
TONCOR | FAR_WEST | CRATERCK_8 (11224) | L_001084ORLA_SW1_8-011132LONGPAST_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0527 | - | - | - | - | -
TONCOR | FAR_WEST | CRATERCK_8 (11224) | L_001095SCRWBEAN_T8-011132LONGPAST_8C1 | 138 | Bus High Volts | 1.05 | 1.0518 | 1.0539 | - | - | - | - | -
TONCOR | FAR_WEST | CRESPINRCH_8 (10019) | ADD_CONSAVVY-GREY WELL DRAW | 138 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0511 | -
TONCOR | FAR_WEST | CRESPINRCH_8 (10019) | ADD_GREY WELL DRAW - Blue Acres | 138 | Bus High Volts | 1.05 | - | - | - | 1.0722 | - | - | -
TONCOR | FAR_WEST | CRESPINRCH_8 (10019) | CONSAVVY - GREY WELL DRAW/MIDLAND EAST 138 KV LINE 2028 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | 1.0521 | -
TONCOR | FAR_WEST | CRESPINRCH_8 (10019) | Grey Well Draw - Blue Acres & Rockhound 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | - | 1.0706 | 1.0728 | - | 1.0727 | -
TONCOR | FAR_WEST | CRESPINRCH_8 (10019) | L_011335BUCHRNCH_8-023858YOSEMT_8C1 | 138 | Bus High Volts | 1.05 | - | - | 1.0509 | 1.0606 | - | 1.0518 | -
TONCOR | FAR_WEST | CRESPINRCH_8 (10019) | L_011388CONSAVVY_8-011396GREYWELL_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0511 | -
TONCOR | FAR_WEST | CRESPINRCH_8 (10019) | L_011396GREYWELL_8-023857BLUEACR_8C1 | 138 | Bus High Volts | 1.05 | - | - | 1.0692 | 1.0722 | - | 1.0713 | -
TONCOR | NORTH_CE | CRLTN_NW1_5 (2361) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94732 | - | -
TAEPTC | SOUTHERN | CRNLLPOI7A (88624) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89971 | - | -
TBREC | NORTH_CE | CROWLEY (399) | L_000394CONCORD8-000398JOSHUAC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91425 | - | -
TONCOR | FAR_WEST | CRTNYCRK_8 (11242) | L_011242CRTNYCRK_8-060792ATHEY4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.8839 | 0.85363 | 0.87004 | -
TAEPTC | SOUTHERN | CRUCE7A (80079) | Pre-contingency | 345 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | 1.051 | -
TAEPTC | SOUTHERN | CRUNCH7A (81004) | Haber - Coleto Creek | 345 | Bus Low Volts | 0.9 | - | - | - | - | - | 0.7558 | -
TAEPTC | SOUTHERN | CRUNCH7A (81004) | L_008676STATIC7A-081003HABER7AC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | - | 0.8978 | -
TAEPTC | SOUTHERN | CRUNCH7A (81004) | Pre-contingency | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88259 | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | L_001009YUCCADR_8-011245RIVERVIEW_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91819 | - | - | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | L_011245RIVERVIEW_8-900064Other_134C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91886 | - | - | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | L_060207VERH4A-060808HOEFSROA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.89973 | - | - | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91661 | - | - | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | L_060383LINTERNA4A-060385SOLSTICE4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91877 | - | - | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | L_060383LINTERNA4A-132331REROCK_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91767 | - | - | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | L_060385SOLSTICE4A-060393PIGCREEK4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91501 | - | - | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | L_060385SOLSTICE4A-060716SGSA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.87014 | - | - | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | L_060385SOLSTICE4A-060808HOEFSROA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.85134 | - | - | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | L_060393PIGCREEK4A-134245TAYGETE_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91644 | - | - | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | L_060393PIGCREEK4A-134705TYGTEII_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91943 | - | - | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | L_060397GASPADTA4A-900064Other_134C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91928 | - | - | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.0543 | - | - | - | - | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.92638 | - | - | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | S_038340TNAIRPORT411 | 138 | Bus Low Volts | 0.92 | - | - | 0.91996 | - | - | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | S_060721CRYO4A1 | 138 | Bus Low Volts | 0.92 | - | - | 0.90795 | - | - | - | -
TAEPTN | FAR_WEST | CRYO4A (60721) | SAND LAKE - SOLSTICE 345 KV DCKT LINE (DOUBLE B TO B) WIN 2027 - FUTURE | 138 | Bus Low Volts | 0.92 | - | - | 0.91164 | - | - | - | -
TAEPTC | SOUTHERN | CRYSTAL4A (8006) | L_008005CARRIZO4A-008283ASHERTON4AC1 | 138 | Bus High Volts | 1.05 | 1.0556 | 1.054 | 1.0555 | 1.0582 | 1.0567 | 1.0576 | -
TAEN | SOUTH_CE | DAFFIN (9184) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94217 | - | - | -
TAEN | SOUTH_CE | DAFFIN (9184) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85411 | - | -
TAEN | SOUTH_CE | DAFFIN (9184) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.92791 | - | -
TAEN | SOUTH_CE | DAFFIN (9184) | LCRATSC_6_EUCLID_JOHNDU | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94523 | - | -
TAEN | SOUTH_CE | DAFFIN (9184) | Pre-contingency | 138 | Bus Low Volts | 0.98 | - | - | - | - | 0.97985 | - | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001159NOANDREW_8-001167MUSTANG_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001163LAMESA_8-010008LAMESA2_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001167MUSTANG_8-001168PAULDTAP_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001169ALKALILK_8-001170PAULDTAP2_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.051 | - | - | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001169ALKALILK_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.051 | - | - | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001170PAULDTAP2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0513 | - | - | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | 1.051 | - | - | - | - | - | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0501 | - | - | - | - | - | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0512 | - | - | - | - | - | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0543 | - | 1.051 | 1.0537 | 1.0503 | 1.0519 | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0548 | - | 1.0515 | 1.0541 | 1.0506 | 1.0523 | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001177TEXMABEE_8-011175BAIRDLAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0524 | - | 1.0511 | 1.0534 | - | 1.0507 | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0517 | - | 1.0505 | 1.0527 | - | - | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0522 | - | 1.0509 | 1.0532 | - | 1.0504 | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001181ANDHWY87_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0558 | - | 1.0547 | 1.0571 | 1.0522 | 1.0545 | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | 1.0527 | - | - | 1.0516 | - | - | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0516 | - | 1.0503 | 1.0526 | - | - | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_001393DAWSON115_8-900060OTHER_140C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0515 | - | - | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0519 | - | - | 1.0507 | - | - | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0523 | - | 1.0511 | 1.0533 | - | 1.0506 | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | LAMESA - MCKENZIE DRAW 138 KV SUM 2023 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.051 | - | - | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | 1.0818 | - | 1.0799 | 1.0797 | 1.0761 | 1.0779 | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | MIDLAND COUNTY NW - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0561 | - | 1.0549 | 1.0572 | 1.0524 | 1.0546 | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | MIDLAND COUNTY NW - MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0556 | - | 1.0548 | 1.0571 | 1.0522 | 1.0544 | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | 1.0552 | - | 1.0519 | 1.0543 | 1.051 | 1.0526 | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0549 | - | 1.0513 | 1.0537 | 1.0506 | 1.052 | -
TONCOR | FAR_WEST | DAWSON115_8 (1393) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | SOUTH_CE | DBLCREEK_8 (3494) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89394 | - | - | -
TONCOR | SOUTH_CE | DBLCREEK_8 (3494) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85117 | - | -
TAEN | SOUTH_CE | DECKER_MB1 (9187) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94747 | - | - | -
TAEN | SOUTH_CE | DECKER_MB1 (9187) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86399 | - | -
TAEN | SOUTH_CE | DECKER_MB3 (9188) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94726 | - | - | -
TAEN | SOUTH_CE | DECKER_MB3 (9188) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86389 | - | -
TONCOR | WEST | DEEPCRK_8 (1304) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.88892 | - | - | - | - | -
TONCOR | NORTH_CE | DEEPELM_8 (2909) | L_002903ENET1_8-002909DEEPELM_8C1 | 138 | Bus High Volts | 1.05 | - | 1.08 | 1.1017 | 1.0946 | 1.0961 | 1.0692 | -
TONCOR | NORTH_CE | DEEPELM_8 (2909) | L_012441PARKD_1EN8-012445MDLTM1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0534 | - | - | - | - | -
TETRTX | SOUTHERN | DELSOL7C (80307) | Pre-contingency | 345 | Bus High Volts | 1.05 | - | - | 1.052 | 1.107 | 1.1339 | - | -
TONCOR | FAR_WEST | DESERTWD2_8 (11285) | EILAND - BULLDOG 138 KV LINE 2026 SUM - 2027 SUM (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.052 | - | - | - | - | -
TONCOR | FAR_WEST | DESERTWD2_8 (11285) | L_001221TEXHARVY_8-001226ARUBA1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0761 | 1.0543 | 1.0521 | - | - | -
TONCOR | FAR_WEST | DESERTWD2_8 (11285) | L_001221TEXHARVY_8-011226PEMBERTN_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0769 | 1.0559 | 1.054 | 1.0503 | - | -
TONCOR | FAR_WEST | DESERTWD2_8 (11285) | L_001222PECKTAP_8-001226ARUBA1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0661 | - | - | - | - | -
TONCOR | FAR_WEST | DESERTWD2_8 (11285) | L_001333MCDONALD_8-011282DESERTWD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0533 | 1.0621 | 1.0531 | 1.0563 | - | 1.0523 | -
TONCOR | FAR_WEST | DESERTWD2_8 (11285) | L_011226PEMBERTN_8-011227THRYSIX_P8C1 | 138 | Bus High Volts | 1.05 | 1.0542 | 1.0878 | 1.0773 | 1.0746 | 1.0717 | 1.0705 | -
TONCOR | FAR_WEST | DESERTWD2_8 (11285) | L_011227THRYSIX_P8-011282DESERTWD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.065 | 1.0932 | 1.0881 | 1.0895 | 1.0875 | 1.0864 | -
TONCOR | FAR_WEST | DESERTWD2_8 (11285) | PECK – SPRABERRY 138 KV DCKT LINE (DOUBLE B TO B) WIN 2025 - FUTURE | 138 | Bus High Volts | 1.05 | - | 1.0515 | - | - | - | - | -
TONCOR | FAR_WEST | DESERTWD2_T8 (11282) | EILAND - BULLDOG 138 KV LINE 2026 SUM - 2027 SUM (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0519 | - | - | - | - | -
TONCOR | FAR_WEST | DESERTWD2_T8 (11282) | L_001221TEXHARVY_8-001226ARUBA1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0761 | 1.0543 | 1.052 | - | - | -
TONCOR | FAR_WEST | DESERTWD2_T8 (11282) | L_001221TEXHARVY_8-011226PEMBERTN_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0768 | 1.0559 | 1.0539 | 1.0503 | - | -
TONCOR | FAR_WEST | DESERTWD2_T8 (11282) | L_001222PECKTAP_8-001226ARUBA1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.066 | - | - | - | - | -
TONCOR | FAR_WEST | DESERTWD2_T8 (11282) | L_001333MCDONALD_8-011282DESERTWD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0533 | 1.062 | 1.053 | 1.0563 | - | 1.0523 | -
TONCOR | FAR_WEST | DESERTWD2_T8 (11282) | L_011226PEMBERTN_8-011227THRYSIX_P8C1 | 138 | Bus High Volts | 1.05 | 1.0541 | 1.0878 | 1.0772 | 1.0746 | 1.0716 | 1.0704 | -
TONCOR | FAR_WEST | DESERTWD2_T8 (11282) | L_011227THRYSIX_P8-011282DESERTWD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0649 | 1.0932 | 1.088 | 1.0894 | 1.0874 | 1.0863 | -
TONCOR | FAR_WEST | DESERTWD2_T8 (11282) | PECK – SPRABERRY 138 KV DCKT LINE (DOUBLE B TO B) WIN 2025 - FUTURE | 138 | Bus High Volts | 1.05 | - | 1.0514 | - | - | - | - | -
TAEN | SOUTH_CE | DESSAU (9193) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93362 | - | 0.94818 | -
TAEN | SOUTH_CE | DESSAU (9193) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.8512 | - | -
TAEN | SOUTH_CE | DESSAU (9193) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94032 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8941 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89716 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89736 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89651 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89483 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89672 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89499 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89692 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89714 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89514 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89533 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | 0.88326 | - | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89844 | - | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89363 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89562 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89215 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | BEPC_015_2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89977 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88688 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89937 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | BLUBIRD_CON | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89507 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89923 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | CEDAR HILL - DESOTO/LOOP NINE 345 KV DCKT (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89269 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.87628 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88039 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89835 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | DRY_CREEK_CON | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89676 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | E_FRNYPP_CC1_TRAIN | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89448 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | E_FRNYPP_CC2_TRAIN | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89446 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88991 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88966 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | G_150023MCSES_UNIT8UN8 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89529 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | G_150092LH2SES_UNIT2UN2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89973 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | G_150112CPSES_UNIT2UU2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89729 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | GLASGOW_CON | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88969 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89594 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89911 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89511 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_001906VENUS_S5-011901BRITNRD1_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89813 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_001931COURTLND1_5-002420CHILSW1_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89774 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89449 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88688 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88966 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_002427WATMLL_W5-002432TRICRN1_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89379 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_002427WATMLL_W5-002432TRICRN1_5C2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89379 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_002431DESSW1_5-002847LOOP9_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88608 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89608 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88861 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89458 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89477 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8912 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_003159ELROD_5-068091NAVARROC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89271 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89928 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_015200FORBESR1_5-068090SAMSWC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89602 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89479 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89639 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89743 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89846 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89985 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | LOOP NINE-DESOTO/CEDAR HILL 345 KV DCKT (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88122 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88216 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88061 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89506 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89332 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88819 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | 0.93244 | 0.92948 | 0.91452 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89834 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | TIMBERVIEW-COMANCHE PEAK*DECORDOVA 345 KV (SINGLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89773 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89863 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.87313 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89928 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | TRIN-RICH (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89376 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | TRIN-SK*ME (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89418 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8978 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88253 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89702 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88647 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89769 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8994 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88263 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89518 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | Bus Low Volts | 0.9 | - | - | - | 0.87156 | - | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89885 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89808 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | XFMR-LKHB_2T8-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89973 | - | -
TONCOR | NORTH_CE | DESSW1_5 (2431) | XFMR-MTCK_8T8-8 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89529 | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | L_001009YUCCADR_8-011245RIVERVIEW_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91796 | - | - | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | L_011245RIVERVIEW_8-900064Other_134C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91863 | - | - | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | L_060207VERH4A-060808HOEFSROA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.8995 | - | - | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91638 | - | - | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | L_060383LINTERNA4A-060385SOLSTICE4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91854 | - | - | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | L_060383LINTERNA4A-132331REROCK_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91744 | - | - | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | L_060385SOLSTICE4A-060393PIGCREEK4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91478 | - | - | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | L_060385SOLSTICE4A-060716SGSA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.8699 | - | - | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | L_060385SOLSTICE4A-060808HOEFSROA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.85109 | - | - | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | L_060393PIGCREEK4A-134245TAYGETE_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91621 | - | - | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | L_060393PIGCREEK4A-134705TYGTEII_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.9192 | - | - | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | L_060397GASPADTA4A-900064Other_134C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91905 | - | - | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.0541 | - | - | - | - | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.92616 | - | - | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | S_038340TNAIRPORT411 | 138 | Bus Low Volts | 0.92 | - | - | 0.91973 | - | - | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | S_060721CRYO4A1 | 138 | Bus Low Volts | 0.92 | - | - | 0.90772 | - | - | - | -
TAEPTN | FAR_WEST | DIAMOND4A (60727) | SAND LAKE - SOLSTICE 345 KV DCKT LINE (DOUBLE B TO B) WIN 2027 - FUTURE | 138 | Bus Low Volts | 0.92 | - | - | 0.91141 | - | - | - | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001159NOANDREW_8-001167MUSTANG_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001163LAMESA_8-010008LAMESA2_8C1 | 138 | Bus High Volts | 1.05 | 1.0513 | - | - | 1.053 | - | - | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001167MUSTANG_8-001168PAULDTAP_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001168PAULDTAP_8-900060OTHER_140C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001169ALKALILK_8-001170PAULDTAP2_8C1 | 138 | Bus High Volts | 1.05 | 1.0516 | - | - | 1.0537 | - | 1.0507 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001169ALKALILK_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0516 | - | - | 1.0537 | - | 1.0508 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001170PAULDTAP2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | 1.0521 | - | - | 1.0541 | - | 1.0511 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | 1.0535 | - | - | 1.0517 | - | - | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0524 | - | - | 1.0506 | - | - | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0536 | - | - | 1.0521 | - | 1.0501 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0573 | - | 1.0536 | 1.0566 | 1.0529 | 1.0549 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0577 | - | 1.054 | 1.057 | 1.0533 | 1.0553 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001177TEXMABEE_8-011175BAIRDLAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0551 | - | 1.0537 | 1.0563 | 1.0509 | 1.0536 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0544 | - | 1.053 | 1.0556 | 1.0501 | 1.0528 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0549 | - | 1.0535 | 1.0561 | 1.0506 | 1.0533 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001181ANDHWY87_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.059 | - | 1.0578 | 1.0605 | 1.0552 | 1.0579 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0502 | - | - | 1.0511 | - | - | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | 1.0554 | - | 1.0514 | 1.0542 | 1.0504 | 1.0524 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0542 | - | 1.0528 | 1.0554 | - | 1.0526 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001393DAWSON115_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0512 | - | - | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_001393DAWSON115_8-900060OTHER_140C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0515 | - | - | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_010008LAMESA2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | 1.0503 | - | - | 1.0519 | - | - | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0545 | - | 1.0504 | 1.0532 | - | 1.0512 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.055 | - | 1.0537 | 1.0563 | 1.0508 | 1.0535 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | LAMESA - MCKENZIE DRAW 138 KV SUM 2023 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0516 | - | - | 1.0537 | - | 1.0507 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | 1.0893 | - | 1.0873 | 1.0869 | 1.083 | 1.0852 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | MIDLAND COUNTY NW - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0593 | - | 1.0581 | 1.0607 | 1.0554 | 1.0581 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | MIDLAND COUNTY NW - MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0588 | - | 1.0579 | 1.0605 | 1.0551 | 1.0578 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | 1.0582 | - | 1.0544 | 1.0573 | 1.0537 | 1.0556 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0579 | - | 1.0538 | 1.0565 | 1.0532 | 1.0549 | -
TONCOR | FAR_WEST | DILLON_P8 (11206) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.0525 | - | - | - | - | -
TAEPTC | WEST | DLNCRK4A (8991) | L_008261WHITING4A-008991DLNCRK4AC1 | 138 | Bus High Volts | 1.05 | 1.06 | - | 1.0545 | 1.0564 | 1.0538 | 1.0561 | -
ERCOT | COAST | DOW_AS (110162) | P1-2_(110133-110162-1) | 138 | Bus High Volts | 1.05 | 1.1382 | 1.1356 | 1.1381 | 1.1372 | 1.1346 | 1.1326 | -
RDOW | COAST | DOWGEN_2_8 (110127) | L_110127DOWGEN_2_8-110128DOWGEN_3_8CSG | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87166 | - | -
RDOW | COAST | DOWGEN_4_8 (110129) | L_110128DOWGEN_3_8-110129DOWGEN_4_8CSG | 138 | Bus Low Volts | 0.9 | 0.83595 | - | 0.8405 | 0.86647 | - | - | -
TONCOR | FAR_WEST | DRLHOLES_8 (11272) | L_011112DELRIVER_8-011272DRLHOLES_8C1 | 138 | Bus High Volts | 1.05 | 1.0571 | - | - | - | - | - | -
TONCOR | FAR_WEST | DRLHOLES_8 (11272) | L_011141BRECK_8-011269OWLHILLS2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0578 | - | - | - | - | - | -
TONCOR | FAR_WEST | DRLHOLES_8 (11272) | L_011180ARYOBLUFF_T8-011199RDRUNNER_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88389 | - | -
TONCOR | FAR_WEST | DRLHOLES_8 (11272) | L_011183TUNSTLL_8-011199RDRUNNER_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8621 | - | -
TONCOR | FAR_WEST | DRLHOLES_8 (11272) | L_011269OWLHILLS2_T8-011272DRLHOLES_8C1 | 138 | Bus High Volts | 1.05 | 1.0682 | - | 1.0612 | - | - | - | -
TONCOR | NORTH | DRYFRK_8 (1505) | L_001426FISHRDSS1_8-001543HENRITAW_9C1 | 138 | Bus High Volts | 1.05 | - | 1.1047 | - | 1.0722 | 1.1093 | 1.1032 | -
TONCOR | NORTH | DRYFRK_8 (1505) | L_001452LANHAM_T9-001544HENRIETA_9C1 | 138 | Bus High Volts | 1.05 | - | 1.0975 | - | 1.0687 | 1.1034 | 1.0999 | -
TONCOR | NORTH_CE | DUBLIN1_8 (1636) | NEW-COMCHE-STEPHENVILLE (SINGLE B TO B ) B-1 | 138 | Bus Low Volts | 0.9 | 0.88658 | - | 0.87417 | 0.89242 | - | 0.89201 | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | AEN_DL-AU¦LP_2013 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.87981 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | AEN_LP-AU¦DL_2013 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93849 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | AEN_LY-FPP:CIS-HO | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93894 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | AEN_LY-FPP¦CIS | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.92954 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | AEN_P1-1_GEN_SH5A+5C | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94957 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | AUSTROP - BEULAH/TORTOISE_5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94582 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | BAS_RANCH_CON | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94542 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94362 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94807 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | DVCPA1C21B_1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94549 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | DVCPA1C21B_2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94854 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | E_B_DAVIS_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94928 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | E_BASTEN_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94458 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | E_FERGCC_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9467 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | E_LOSTPI_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94956 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94955 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | E_NUECES_B_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94812 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | G_007048L_GARFIE5_1YUN1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94624 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | G_170073GID_GIDEONG3UN3 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94923 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | G_170126CALAVER_JKS2UL2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94204 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | G_888839BAS_RANCH_POIUC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94545 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | G_RIO_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94038 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | 0.93117 | - | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | J5LCA1C1_B | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94028 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.81738 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | L_003696HUTTOSS__5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94773 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | L_003696HUTTOSS__5-003699SALADOSS_5C2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94773 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.90239 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94469 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | L_005133ELMCREEK-005380SHAULAC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9373 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94957 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | L_005380SHAULA-005915SO_TEX__345AC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9495 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | L_005915SO_TEX__345A-008715RADIANT7AC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94372 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93769 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | L_007040L_AUSTRO5_1Y-009044DUNLAP5C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.92446 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94457 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | L_009043CISTERN-009074LYTTON5C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94987 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | LCRA TSC_T185_T246 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94124 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | LCRA TSC_T255_TAE3121_1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.92292 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | LCRATSC_6_EUCLID_JOHNDU | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94092 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | M10000271115801 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94966 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | MB100002711580 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94966 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | N5GSU2_B | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94204 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | P7-1_E1>>T1839X1_ERC | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94883 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | P7-1_E1>>T1839X2_ERC | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94573 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | P7-1_E1>>T2764Y_ERCa | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94898 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | P7-1_E1>>T3944Z_ERC | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94176 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | Pre-contingency | 345 | Bus Low Volts | 0.98 | - | - | - | - | 0.96164 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | STP - HOUDINI & STP - SHAULA | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94924 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9433 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94838 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | TORTOISE - BEULAH/AUSTROP_5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94797 | - | -
TAEN | SOUTH_CE | DUNLAP5 (9044) | WAP - HOUDINI & STP - SHAULA | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9499 | - | -
TAEN | SOUTH_CE | DUNLAP8 (9045) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.9447 | - | - | -
TAEN | SOUTH_CE | DUNLAP8 (9045) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.87094 | - | -
TAEN | SOUTH_CE | DUNLAP8 (9045) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94957 | - | -
TONCOR | WEST | DUNN_8 (11330) | L_001318CHINAGRV_8-011330DUNN_8C1 | 138 | Bus Low Volts | 0.9 | 0.87778 | - | 0.87741 | 0.87923 | 0.88018 | 0.89765 | -
TONCOR | WEST | DUNN_8 (11330) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | 0.88516 | 0.89799 | 0.89117 | 0.89217 | 0.8804 | 0.89518 | -
TONCOR | WEST | DUNN_8 (11330) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.83325 | - | - | - | - | -
REAST1 | SOUTH_CE | E_BLACK_8 (170523) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8842 | - | -
TAEN | SOUTH_CE | EAST_VILLAGE (9195) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.9297 | - | 0.94952 | -
TAEN | SOUTH_CE | EAST_VILLAGE (9195) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.8559 | - | -
TAEN | SOUTH_CE | EAST_VILLAGE (9195) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94948 | - | -
TAEN | SOUTH_CE | EASTON PARK (9143) | AEN_GF-SR: EP-HC | 138 | Bus High Volts | 1.05 | - | - | - | - | 1.0681 | - | -
TAEN | SOUTH_CE | EASTON PARK (9143) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86485 | - | -
TAEN | SOUTH_CE | EDBLUESTN (9196) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94577 | - | - | -
TAEN | SOUTH_CE | EDBLUESTN (9196) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86041 | - | -
TONCOR | FAR_WEST | EDWARD_T8 (1110) | L_001013WOLFSS_8-001103SANDHLTA_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0524 | - | - | - | - | -
TONCOR | FAR_WEST | EDWARDS_8 (1101) | L_001013WOLFSS_8-001103SANDHLTA_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0522 | - | - | - | - | -
TBREC | NORTH_CE | EGAN2 (33405) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91735 | - | -
TONCOR | FAR_WEST | EILAND_8 (23853) | L_001335FORSANTA_8-011337POLECAT1_8C1 | 138 | Bus Low Volts | 0.9 | 0.89875 | 0.89894 | - | - | - | - | -
TONCOR | FAR_WEST | EILAND_8 (23853) | MCDONALD RD - POLECAT 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | 0.89883 | 0.89894 | - | - | - | - | -
TONCOR | FAR_WEST | EILAND_8 (23853) | Pre-contingency | 138 | Bus Low Volts | 0.95 | 0.94877 | - | - | - | - | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | 3WT_023875EINSTN_5_023852EINSTN_8_023874EINSTN_3 C 1 | 138 | Bus Low Volts | 0.9 | - | 0.89022 | - | - | 0.89896 | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | CARTERVILLE - EILAND 138 KV LINE SUM 2030 - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89377 | 0.8975 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | EINSTEIN - CARTERVILLE 138 KV LINE 2025 SUM - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.8807 | - | 0.89975 | 0.8905 | 0.89429 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_001189BARBER_LK1_8-010050RANGER_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.8995 | - | - | - | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_001328QUARTZSAND_8-010029LILDEWEY_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.87344 | - | - | 0.89049 | 0.89452 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_001333MCDONALD_8-001334GLASSCNTYN_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.8503 | 0.88374 | 0.88101 | 0.87378 | 0.8797 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_001333MCDONALD_8-131143MCDLD_1_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89031 | - | - | - | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_001334GLASSCNTYN_8-001335FORSANTA_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.8533 | 0.88877 | 0.88577 | 0.87598 | 0.8843 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_001335FORSANTA_8-011337POLECAT1_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.84328 | 0.88311 | 0.88065 | 0.87403 | 0.87956 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_010018CARTVLRNCH_8-023851CARTRVL_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.8807 | - | 0.89975 | 0.89051 | 0.89429 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_010018CARTVLRNCH_8-023852EINSTN_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88072 | - | 0.89977 | 0.89052 | 0.89431 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_010022EILANDRNCH_8-023851CARTRVL_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89379 | 0.89751 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_010022EILANDRNCH_8-023853EILAND_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89378 | 0.8975 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_010029LILDEWEY_8-011350WRGRN_P8C1 | 138 | Bus Low Volts | 0.9 | - | 0.87347 | - | - | 0.89056 | 0.89458 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_010032LILLUTHER_8-023831LUTHER_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.8873 | - | - | - | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_010032LILLUTHER_8-023835VLMOOR_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.8873 | - | - | - | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_010041SALEM_8-023832COYOTE_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88813 | - | - | - | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_010041SALEM_8-023833BULLDOG_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88813 | - | - | - | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_010050RANGER_8-011393FRONTIER_P8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89858 | - | - | - | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_010080REDBERRY_8-023833BULLDOG_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.85165 | - | - | 0.89334 | 0.89468 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_010080REDBERRY_8-900043Other_132C1 | 138 | Bus Low Volts | 0.9 | - | 0.85 | - | - | 0.89222 | 0.89357 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_011337POLECAT1_8-011350WRGRN_P8C1 | 138 | Bus Low Volts | 0.9 | - | 0.87493 | - | - | 0.89355 | 0.8975 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_023831LUTHER_8-023832COYOTE_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88756 | - | - | - | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_023834ELBOW_8-900043Other_132C1 | 138 | Bus Low Volts | 0.9 | - | 0.85327 | - | - | 0.89587 | 0.89715 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_023849VLMOOR_5-059900LONG_DRAWC1 | 138 | Bus Low Volts | 0.9 | - | 0.89915 | - | - | - | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_023851CARTRVL_8-023853EILAND_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88209 | - | - | - | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | L_023875EINSTN_5-059903BEARKATC1 | 138 | Bus Low Volts | 0.9 | - | 0.89022 | - | - | 0.89896 | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | LCRA TSC_BAKERS_CEDACA_DC | 138 | Bus Low Volts | 0.9 | - | 0.89856 | - | - | - | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | LUTHER - VEALMOOR 138 KV LINE 2026 SUM - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.88729 | - | - | - | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | MCDONALD RD - POLECAT 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.84328 | 0.8832 | 0.88073 | 0.87418 | 0.87963 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | Prairieland-Quartzsand Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | - | 0.89657 | - | - | - | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | Pre-contingency | 138 | Bus Low Volts | 0.95 | 0.89639 | 0.90674 | 0.93261 | 0.93198 | 0.92143 | 0.92093 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | QUARTZ SAND - POLECAT CREEK 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.87499 | - | - | 0.89365 | 0.89753 | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | - | 0.88529 | - | - | 0.89887 | - | -
TONCOR | FAR_WEST | ELBOW_8 (23834) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.85456 | - | - | - | - | -
TONCOR | FAR_WEST | ELCOR_8 (11198) | CULBERSON - COALSON DRAW DCKT 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0514 | - | - | - | - | -
TONCOR | SOUTH_CE | ELGIN_SUB_8 (3674) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.84205 | - | -
ERCOT | NORTH_CE | ELIZA_5 (153535) | L_002478ROYSE_S5-002485POETRY_5C1 | 345 | Bus High Volts | 1.05 | - | 1.1367 | - | - | - | - | -
TONCOR | EAST | ELKTON_5 (3105) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89472 | - | -
TONCOR | EAST | ELKTON_5 (3105) | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88028 | - | -
TONCOR | EAST | ELKTON_5 (3105) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89449 | - | -
TONCOR | EAST | ELKTON_5 (3105) | TRIN-SK*ME (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.86676 | - | -
TONCOR | EAST | ELKTON_5 (3105) | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89303 | - | -
TONCOR | EAST | ELKTON_5 (3105) | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89756 | 0.86884 | - | -
RELLIS | NORTH_CE | ELLISSLR_8 (152283) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87767 | 0.84436 | - | -
TAEN | SOUTH_CE | ELROY_LD1 (9198) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.84644 | - | -
TAEN | SOUTH_CE | ELROY_LD1 (9198) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.9302 | - | -
TAEN | SOUTH_CE | ELROY_LD1 (9198) | L_007208L_COLTON8_1Y-007209L_ELROY_8_1YC1 | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94368 | 0.91382 | 0.93121 | -
TAEN | SOUTH_CE | ELROY_LD1 (9198) | L_007208L_COLTON8_1Y-007325L_MENDOZ8_1YC1 | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93412 | 0.90309 | 0.92093 | -
TAEN | SOUTH_CE | ELROY_LD1 (9198) | L_007210L_WYLDWO8_1Y-007556L_BLUEBO8_1YC1 | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94966 | - | 0.94805 | -
TAEN | SOUTH_CE | ELROY_LD1 (9198) | L_007310L_SIMGID8_1Y-007555L_BASTWE8_1YC1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | - | 0.92975 | -
TAEN | SOUTH_CE | ELROY_LD1 (9198) | L_007325L_MENDOZ8_1Y-009075LYTTON8C1 | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94677 | 0.92883 | 0.94035 | -
TAEN | SOUTH_CE | ELROY_LD1 (9198) | L_007555L_BASTWE8_1Y-007556L_BLUEBO8_1YC1 | 138 | Bus Low Volts | 0.95 | - | - | 0.94707 | - | - | 0.93017 | -
TAEN | SOUTH_CE | ELROY_LD1 (9198) | LCRA TSC_T410_T648 | 138 | Bus Low Volts | 0.95 | - | - | 0.94969 | - | - | - | -
TAEN | SOUTH_CE | ELROY_LD1 (9198) | Pre-contingency | 138 | Bus Low Volts | 0.98 | - | - | - | 0.9772 | - | 0.97385 | -
RELSAU | SOUTHERN | ELSAUZ_5 (163415) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.9 | - | - | - | 0.87958 | - | - | -
RELSAU | SOUTHERN | ELSAUZ_5 (163415) | E5DVA1C1_1_B | 345 | Bus Low Volts | 0.9 | - | - | - | 0.88344 | - | - | -
RELSAU | SOUTHERN | ELSAUZ_5 (163415) | L_008317LA_PALMA7A-008709CANDELA7AC1 | 345 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0563 | -
RELSAU | SOUTHERN | ELSAUZ_5 (163415) | L_008318RIOHONDO7A-008573BONILLA7AC1 | 345 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0516 | -
RELSAU | SOUTHERN | ELSAUZ_5 (163415) | L_080509LADKPOI7A-161753BBREEZE_5C1 | 345 | Bus High Volts | 1.05 | - | - | - | - | - | 1.05 | -
RELSAU | SOUTHERN | ELSAUZ_5 (163415) | L11000095 | 345 | Bus High Volts | 1.05 | - | - | - | - | - | 1.05 | -
RELSAU | SOUTHERN | ELSAUZ_5 (163415) | M1000031210000064 | 345 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0512 | -
RELSAU | SOUTHERN | ELSAUZ_5 (163415) | M10000841000093-1A | 345 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0541 | -
RELSAU | SOUTHERN | ELSAUZ_5 (163415) | P7/C5-SHRY-3 | 345 | Bus High Volts | 1.05 | - | - | - | - | - | 1.052 | -
RELSAU | SOUTHERN | ELSAUZ_5 (163415) | Pre-contingency | 345 | Bus High Volts | 1.05 | 1.0554 | - | - | - | - | - | -
RELSAU | SOUTHERN | ELSAUZ_5 (163415) | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88877 | - | -
RELSAU | SOUTHERN | ELSAUZ_5 (163415) | T100001 | 345 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0567 | -
TAEPTC | SOUTHERN | ELSUZPOI7A (8663) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | 0.84705 | - | - | -
TAEPTC | SOUTHERN | ELSUZPOI7A (8663) | E5DVA1C1_1_B | 345 | Bus Low Volts | 0.92 | - | - | - | 0.85087 | - | - | -
TAEPTC | SOUTHERN | ELSUZPOI7A (8663) | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | Bus Low Volts | 0.92 | - | - | - | 0.87402 | 0.86812 | - | -
TONCOR | NORTH_CE | ENET1_8 (2903) | L_012441PARKD_1EN8-012445MDLTM1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0533 | - | - | - | - | -
TONCOR | NORTH_CE | ENET2_8 (2904) | L_012442PARKD_2EN8-012446MDLTM2_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.88981 | - | - | 0.89203 | -
TONCOR | NORTH_CE | ENET2_8 (2904) | L_012446MDLTM2_8-012904ENETOH2_8C1 | 138 | Bus Low Volts | 0.9 | 0.88997 | - | 0.86868 | 0.89367 | - | 0.87128 | -
TONCOR | NORTH_CE | ENETOH1_8 (12903) | L_012441PARKD_1EN8-012445MDLTM1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0533 | - | - | - | - | -
TONCOR | NORTH_CE | ENETOH2_8 (12904) | L_012442PARKD_2EN8-012446MDLTM2_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.88981 | - | - | 0.89203 | -
TONCOR | NORTH_CE | ENETOH2_8 (12904) | L_012446MDLTM2_8-012904ENETOH2_8C1 | 138 | Bus Low Volts | 0.9 | 0.88996 | - | 0.86867 | 0.89366 | - | 0.87127 | -
TBREC | NORTH_CE | ENNIS (216) | E_ETCCS_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91273 | - | -
TONCOR | NORTH_CE | ERIKA_POI (888878) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.86224 | - | -
TONCOR | NORTH_CE | ERIKA_POI (888878) | TRIN-SK*ME (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88061 | - | -
TONCOR | NORTH_CE | ERIKA_POI (888878) | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89503 | - | -
TAEPTN | FAR_WEST | ESMERALD4A (6525) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.8921 | 0.86695 | 0.87185 | -
TAEPTN | FAR_WEST | ESMERALD4A (6525) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.90644 | 0.89399 | 0.90927 | -
TAEPTN | FAR_WEST | ESMERALD4A (6525) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.90376 | 0.89063 | 0.90579 | -
TAEPTN | FAR_WEST | ESMERALD4A (6525) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89664 | 0.88529 | 0.90043 | -
TAEPTN | FAR_WEST | ESMERALD4A (6525) | L2020944-A | 138 | Bus Low Volts | 0.92 | - | - | - | 0.90383 | 0.89075 | 0.90585 | -
TONCOR | NORTH | EXPLR_PL1_8 (1766) | L_001755ECTOR_P8-001762BONHMNW1_8C1 | 138 | Bus High Volts | 1.05 | 1.0506 | - | 1.0504 | - | - | 1.0529 | -
TONCOR | NORTH | EXPLR_PL1_8 (1766) | L_001760BONHMSS1_8-001762BONHMNW1_8C1 | 138 | Bus High Volts | 1.05 | 1.0515 | - | 1.0513 | 1.0502 | 1.0501 | 1.0542 | -
TCPSE | SOUTH_CE | FAIRRA (5470) | L_007169L_FAIROA8_1Y-007170L_BERGHE8_1YC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TWETR | FAR_WEST | FARADAY (59905) | C5-WETT-2_B | 345 | Bus High Volts | 1.05 | 1.0582 | 1.0572 | 1.0575 | - | - | - | -
TWETR | FAR_WEST | FARADAY (59905) | C5-WETT-2_B-1 | 345 | Bus High Volts | 1.05 | - | - | - | 1.0553 | - | - | -
TWETR | FAR_WEST | FARADAY (59905) | C5-WETT-2_B-2 | 345 | Bus High Volts | 1.05 | - | - | - | 1.0554 | - | - | -
TWETR | FAR_WEST | FARADAY (59905) | L_059900LONG_DRAW-059905FARADAYC1 | 345 | Bus High Volts | 1.05 | 1.0582 | 1.0571 | 1.0577 | 1.0555 | - | - | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0519 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0515 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0519 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0538 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0536 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0563 | 1.0723 | 1.0547 | 1.0577 | 1.0516 | 1.0549 | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0572 | 1.0734 | 1.0557 | 1.0587 | 1.0526 | 1.0558 | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0686 | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0527 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0559 | 1.072 | 1.0544 | 1.0573 | 1.0513 | 1.0545 | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0523 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | L_011167ALKALILK2_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | L_011167ALKALILK2_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | - | 1.0541 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | NORTH ANDREWS - LAMESA - MCKENZIE 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0543 | 1.0598 | - | 1.0576 | 1.053 | 1.0551 | -
TONCOR | FAR_WEST | FASKENC_8 (11177) | NORTH ANDREWS - MCKENZIE 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0514 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0519 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0515 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0519 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0538 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0536 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0563 | 1.0723 | 1.0547 | 1.0577 | 1.0516 | 1.0549 | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0572 | 1.0734 | 1.0557 | 1.0587 | 1.0526 | 1.0558 | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0686 | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0527 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0559 | 1.072 | 1.0544 | 1.0573 | 1.0513 | 1.0545 | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0523 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | L_011167ALKALILK2_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | L_011167ALKALILK2_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | - | 1.0541 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | NORTH ANDREWS - LAMESA - MCKENZIE 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0543 | 1.0598 | - | 1.0576 | 1.053 | 1.0551 | -
TONCOR | FAR_WEST | FASKENC2_8 (11176) | NORTH ANDREWS - MCKENZIE 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0514 | - | - | - | - | -
TONCOR | NORTH_CE | FEWELL_S1 (888888) | L_003597GROESBECP_8-888888FEWELL_S1C1 | 138 | Bus Low Volts | 0.9 | - | 0.89705 | - | - | - | - | -
TAEN | SOUTH_CE | FISKVIL (9199) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93607 | - | - | -
TAEN | SOUTH_CE | FISKVIL (9199) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85467 | - | -
TAEN | SOUTH_CE | FISKVIL (9199) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94774 | - | -
RFLUVA | WEST | FLUVANNA_8 (181953) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | - | - | - | 1.0504 | - | -
RFLUVA | WEST | FLUVANNA_8 (181953) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | - | 1.0501 | 1.0507 | - | - | -
TBREC | NORTH_CE | FORBESRD_8 (1303) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | 0.8992 | 0.87309 | 0.82986 | 0.79636 | 0.85472 | -
TBREC | NORTH_CE | FORBESRD_8 (1303) | BEPC_306 | 138 | Bus Low Volts | 0.9 | 0.78727 | 0.7315 | - | - | - | - | -
TBREC | NORTH_CE | FORBESRD_8 (1303) | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | Bus Low Volts | 0.9 | 0.82553 | 0.74442 | 0.69043 | - | - | - | -
TBREC | NORTH_CE | FORBESRD_8 (1303) | L_000442RAILPORT-001908VENUSC1 | 138 | Bus Low Volts | 0.9 | 0.82336 | 0.74402 | 0.68372 | - | - | - | -
TBREC | NORTH_CE | FORBESRD_8 (1303) | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | Bus Low Volts | 0.9 | 0.78724 | 0.73073 | - | - | - | - | -
RFORVN | COAST | FORMOSA_16_9 (111450) | L_110471FORFPC_1_8-111450FORMOSA_16_9C1 | 138 | Bus High Volts | 1.05 | - | - | 1.0505 | - | 1.056 | 1.0513 | -
RFORVN | COAST | FORMOSA_18_9 (111452) | L_110471FORFPC_1_8-111452FORMOSA_18_9C2 | 138 | Bus High Volts | 1.05 | - | - | 1.0505 | - | 1.056 | 1.0513 | -
TSTEC | COAST | FRANKLNCAMP8 (5568) | L_005568FRANKLNCAMP8-043470WTRFWL__B138C02 | 138 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0703 | -
TSTEC | COAST | FRANKLNCAMP8 (5568) | P7-1_E1>>T0202B1 | 138 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0703 | -
TONCOR | NORTH_CE | FRNY1_5 (2437) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94779 | - | -
ERCOT | NORTH_CE | FRNYPP_1_5 (150189) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94912 | - | -
ERCOT | NORTH_CE | FRNYPP_2_5 (150190) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94905 | - | -
TONCOR | WEST | FRONTIER_P8 (11393) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.74141 | - | - | - | - | -
TAEN | SOUTH_CE | FV138_CAP (9006) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.9361 | - | - | -
TAEN | SOUTH_CE | FV138_CAP (9006) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85469 | - | -
TAEN | SOUTH_CE | FV138_CAP (9006) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94777 | - | -
TONCOR | FAR_WEST | GAILLYNT_8 (1308) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0651 | - | - | - | - | -
ERCOT | COAST | GARCITAS_S1 (113051) | Haber - Coleto Creek | 345 | Bus Low Volts | 0.9 | - | - | - | - | - | 0.79496 | -
ERCOT | COAST | GARCITAS_S1 (113051) | Pre-contingency | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.87426 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | AEN_LP-AU¦DL_2013 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94136 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | AEN_LY-FPP:CIS-HO | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94868 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | AEN_LY-FPP¦CIS | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93756 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | BAS_RANCH_CON | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94885 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94719 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | DVCPA1C21B_1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94931 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | E_BASTEN_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94348 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | G_007048L_GARFIE5_1YUN1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9452 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | G_170126CALAVER_JKS2UL2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94543 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | G_888839BAS_RANCH_POIUC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94888 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | G_RIO_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9438 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | 0.92758 | - | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | J5LCA1C1_B | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9437 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.82225 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9064 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94853 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | L_005133ELMCREEK-005380SHAULAC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94167 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | L_005915SO_TEX__345A-008715RADIANT7AC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94697 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9412 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94346 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | LCRA TSC_T185_T246 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94082 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | LCRA TSC_T255_TAE3121_1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93156 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | LCRATSC_6_EUCLID_JOHNDU | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94818 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | N5GSU2_B | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94543 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | P7-1_E1>>T1839X2_ERC | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94956 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | P7-1_E1>>T3944Z_ERC | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94521 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | Pre-contingency | 345 | Bus Low Volts | 0.98 | - | - | - | - | 0.96542 | - | -
TAEN | SOUTH_CE | GARFIELD5 (9048) | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94806 | - | -
TAEN | SOUTH_CE | GARFIELD8 (9071) | AEN_GF-SR: EP-HC | 138 | Bus High Volts | 1.05 | - | - | - | - | 1.0694 | - | -
TAEN | SOUTH_CE | GARFIELD8 (9071) | AEN_GF-SR¦EP | 138 | Bus High Volts | 1.05 | - | - | - | - | 1.0697 | - | -
TAEN | SOUTH_CE | GARFIELD8 (9071) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.8847 | - | -
TTNMP | FAR_WEST | GASPADTA4A (60397) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0631 | - | - | - | - | -
TAEPTC | SOUTHERN | GCGV14A (88001) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8913 | - | -
TAEPTC | SOUTHERN | GCGV14A (88001) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89756 | - | -
TAEPTC | SOUTHERN | GCGV14A (88001) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91357 | - | -
TAEPTC | SOUTHERN | GCGV24A (88002) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89129 | - | -
TAEPTC | SOUTHERN | GCGV24A (88002) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89755 | - | -
TAEPTC | SOUTHERN | GCGV24A (88002) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91357 | - | -
TAEPTC | SOUTHERN | GCGV34A (88003) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89127 | - | -
TAEPTC | SOUTHERN | GCGV34A (88003) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89753 | - | -
TAEPTC | SOUTHERN | GCGV34A (88003) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91354 | - | -
TAEPTC | SOUTHERN | GCGV44A (88004) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89127 | - | -
TAEPTC | SOUTHERN | GCGV44A (88004) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89753 | - | -
TAEPTC | SOUTHERN | GCGV44A (88004) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91354 | - | -
TONCOR | NORTH_CE | GELLER_8 (2263) | L_002429WATMLL_8-003083WILMER1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.80368 | 0.79015 | 0.84566 | -
TONCOR | NORTH_CE | GELLER_8 (2263) | L_002434SGVLSW1_8-003076SGVL1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89697 | - | -
RELLIS | NORTH_CE | GERDAU_8 (152285) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87767 | 0.84436 | - | -
TAEPTC | SOUTHERN | GIBBS4A (8173) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89133 | - | -
TAEPTC | SOUTHERN | GIBBS4A (8173) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89759 | - | -
TAEPTC | SOUTHERN | GIBBS4A (8173) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91361 | - | -
ERCOT | SOUTH_CE | GIGABATT_5 (170872) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | 0.8993 | 0.85448 | - | 0.88884 | -
ERCOT | SOUTH_CE | GIGABATT_5 (170872) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.81802 | - | -
ERCOT | SOUTH_CE | GIGABATT_5 (170872) | L_007041L_JOHNDU5_1Y-007047L_HORNSB5_1YC1 | 345 | Bus Low Volts | 0.9 | - | - | - | 0.88826 | 0.88486 | 0.89949 | -
ERCOT | SOUTH_CE | GIGABATT_5 (170872) | LCRA TSC_T510_T775 | 345 | Bus Low Volts | 0.9 | - | - | - | 0.87219 | 0.87115 | 0.88256 | -
ERCOT | SOUTH_CE | GIGABATT_5 (170872) | LCRATSC_5_HORNSB_EUCLID | 345 | Bus Low Volts | 0.9 | - | - | - | 0.87038 | 0.86961 | 0.8811 | -
ERCOT | SOUTH_CE | GIGABATT_5 (170872) | LCRATSC_6_EUCLID_JOHNDU | 345 | Bus Low Volts | 0.9 | - | 0.88954 | 0.89549 | 0.85141 | 0.84251 | 0.85944 | -
ERCOT | SOUTH_CE | GIGABATT_5 (170872) | LCRATSC_7_JOHNDU_ZORN__ | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89114 | - | - | -
ERCOT | SOUTH_CE | GIGABATT_5 (170872) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | 0.94355 | 0.94427 | - | -
TAEN | SOUTH_CE | GILLE138 (9054) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.92309 | - | - | -
TAEN | SOUTH_CE | GILLE138 (9054) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.87212 | - | -
TAEN | SOUTH_CE | GILLE138 (9054) | LCRATSC_6_EUCLID_JOHNDU | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94328 | - | -
TONCOR | FAR_WEST | GLASSCNTYN_8 (1334) | L_001333MCDONALD_8-001334GLASSCNTYN_8C1 | 138 | Bus Low Volts | 0.9 | 0.89919 | - | - | - | - | - | -
TONCOR | FAR_WEST | GLASSHAM_8 (11336) | L_001335FORSANTA_8-011337POLECAT1_8C1 | 138 | Bus Low Volts | 0.9 | 0.89886 | 0.89905 | - | - | - | - | -
TONCOR | FAR_WEST | GLASSHAM_8 (11336) | MCDONALD RD - POLECAT 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | 0.89894 | 0.89905 | - | - | - | - | -
TONCOR | FAR_WEST | GLASSHAM_8 (11336) | Pre-contingency | 138 | Bus Low Volts | 0.95 | 0.94891 | - | - | - | - | - | -
TBREC | NORTH_CE | GLNHEIGHTS (217) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91102 | - | -
TBREC | NORTH_CE | GLNHEIGHTS (217) | 3WT_002431DESSW1_5_002424DESSW1_8_012431DESSW1_3 C 1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9198 | - | -
TBREC | NORTH_CE | GLNHEIGHTS (217) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91746 | - | -
TBREC | NORTH_CE | GLNHEIGHTS (217) | L_000217GLNHEIGHTS-002424DESSW1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89717 | 0.91514 | -
TBREC | NORTH_CE | GLNHEIGHTS (217) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91595 | - | -
TBREC | NORTH_CE | GLNHEIGHTS (217) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91888 | - | - | -
TONCOR | FAR_WEST | GODDARD_8 (1184) | L_001023MIDLNDE_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0537 | - | - | - | - | -
TONCOR | FAR_WEST | GODDARD1_T8 (11279) | L_001023MIDLNDE_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.054 | - | - | - | - | -
RFLUV2 | WEST | GOPHER_138 (133796) | Pre-contingency | 138 | Bus High Volts | 1.05 | 1.0633 | - | 1.0653 | 1.0665 | 1.0701 | 1.0571 | -
RFLUV2 | WEST | GOPHER_138 (133796) | XFMR-RANGER_5 | 138 | Bus High Volts | 1.05 | - | 1.054 | - | - | - | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89284 | - | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89793 | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88881 | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89273 | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89887 | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89793 | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89939 | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89208 | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89234 | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89884 | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | 0.93597 | 0.93763 | 0.92514 | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88217 | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89276 | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89706 | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89358 | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 345 | Bus Low Volts | 0.9 | - | 0.87574 | 0.86803 | - | - | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | Bus Low Volts | 0.9 | - | - | - | 0.87933 | - | - | -
TONCOR | NORTH_CE | GREENRD_5 (3063) | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 345 | Bus Low Volts | 0.9 | - | - | 0.88443 | - | - | - | -
TBREC | NORTH_CE | GRIFFITH (440) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.92 | - | 0.90564 | 0.87848 | 0.8369 | 0.80466 | 0.86043 | -
TBREC | NORTH_CE | GRIFFITH (440) | BEPC_306 | 138 | Bus Low Volts | 0.92 | 0.80175 | 0.75109 | - | - | - | - | -
TBREC | NORTH_CE | GRIFFITH (440) | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | Bus Low Volts | 0.92 | 0.8377 | 0.76323 | 0.71083 | - | - | - | -
TBREC | NORTH_CE | GRIFFITH (440) | L_000442RAILPORT-001908VENUSC1 | 138 | Bus Low Volts | 0.92 | 0.83562 | 0.76285 | 0.70442 | - | - | - | -
TBREC | NORTH_CE | GRIFFITH (440) | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | Bus Low Volts | 0.92 | 0.80172 | 0.75034 | - | - | - | - | -
TBREC | NORTH_CE | GRIFFITH (440) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94692 | - | -
TONCOR | NORTH_CE | GRIFFTH_P8 (1905) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | 0.87849 | 0.83691 | 0.80466 | 0.86044 | -
TONCOR | NORTH_CE | GRIFFTH_P8 (1905) | BEPC_306 | 138 | Bus Low Volts | 0.9 | 0.80175 | 0.75109 | - | - | - | - | -
TONCOR | NORTH_CE | GRIFFTH_P8 (1905) | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | Bus Low Volts | 0.9 | 0.8377 | 0.76323 | 0.71084 | - | - | - | -
TONCOR | NORTH_CE | GRIFFTH_P8 (1905) | L_000442RAILPORT-001908VENUSC1 | 138 | Bus Low Volts | 0.9 | 0.83562 | 0.76285 | 0.70442 | - | - | - | -
TONCOR | NORTH_CE | GRIFFTH_P8 (1905) | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | Bus Low Volts | 0.9 | 0.80173 | 0.75034 | - | - | - | - | -
TONCOR | NORTH_CE | GRIFFTH_P8 (1905) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94692 | - | -
TAEPTC | SOUTHERN | GRISSOM7A (8624) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.8996 | - | -
TONCOR | NORTH_CE | GROES_SE1_8 (3634) | L_003597GROESBECP_8-888888FEWELL_S1C1 | 138 | Bus Low Volts | 0.9 | - | 0.89701 | - | - | - | - | -
TONCOR | NORTH_CE | GROES_SE1_8 (3634) | L_888888FEWELL_S1-003634GROES_SE1_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88745 | - | - | - | - | -
TAEN | SOUTH_CE | GROVE (9200) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94807 | - | - | -
TAEN | SOUTH_CE | GROVE (9200) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85965 | - | -
RCALP | SOUTH_CE | GUADG_1_5 (170167) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89667 | - | -
TAEPTC | SOUTHERN | GULCH7A (8704) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | 0.88496 | - | - | -
TAEPTC | SOUTHERN | GULCH7A (8704) | E5DVA1C1_1_B | 345 | Bus Low Volts | 0.92 | - | - | - | 0.89082 | - | - | -
TAEPTC | SOUTHERN | GULCH7A (8704) | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91754 | 0.90739 | - | -
TAEPTC | SOUTHERN | HABER7A (81003) | Haber - Coleto Creek | 345 | Bus Low Volts | 0.9 | - | - | - | - | - | 0.75664 | -
TAEPTC | SOUTHERN | HABER7A (81003) | L_008676STATIC7A-081003HABER7AC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | - | 0.8985 | -
TAEPTC | SOUTHERN | HABER7A (81003) | Pre-contingency | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88331 | - | -
TONCOR | NORTH_CE | HACKBRY1_5 (2387) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9443 | - | -
TONCOR | FAR_WEST | HADACRN_8 (23867) | DRIVER - HADACOL CORNER 138 KV LINE BEG - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0517 | 1.0545 | 1.0514 | 1.0514 | 1.0511 | 1.0512 | -
TONCOR | FAR_WEST | HADACRN_8 (23867) | L_023863DRIVER_8-023867HADACRN_8C1 | 138 | Bus High Volts | 1.05 | 1.0517 | 1.0545 | 1.0514 | 1.0514 | 1.0511 | 1.0512 | -
TONCOR | FAR_WEST | HADAROAD_8 (10025) | DRIVER - HADACOL CORNER 138 KV LINE BEG - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0515 | 1.0542 | 1.0512 | 1.0512 | 1.0509 | 1.0509 | -
TONCOR | FAR_WEST | HADAROAD_8 (10025) | L_023863DRIVER_8-023867HADACRN_8C1 | 138 | Bus High Volts | 1.05 | 1.0515 | 1.0542 | 1.0512 | 1.0512 | 1.0509 | 1.0509 | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | ARGENTA_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90681 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | E_B_DAVIS_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90497 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | E_CCEC_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91037 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9013 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | E_NEDIN_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91806 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | E_NUECES_B_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88629 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9056 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90099 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | L_005133ELMCREEK-005380SHAULAC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91769 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9189 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | L_008027CLLCOTTE4A-008452LON_HILL4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89618 | 0.8537 | 0.90469 | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | L_008027CLLCOTTE4A-008924PORTILLA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91352 | 0.8752 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91912 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8671 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | L_008579KATOEN7A-008606GODDARD7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89327 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | L_008606GODDARD7A-888858ARGENTA_POIC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91303 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | M10000253106503-1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91301 | - | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | M10000254106503-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87449 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | M10000271115801 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91626 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | MB100002510650-2 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91307 | - | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | MB100002711580 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91626 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | MB106501000025-2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87499 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.93992 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | S_008924PORTILLA4A1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91815 | - | -
TAEPTC | SOUTHERN | HAISLEY4A (8920) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90655 | - | -
TAEN | SOUTH_CE | HAMLTN_MB1 (9203) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93678 | - | - | -
TAEN | SOUTH_CE | HAMLTN_MB1 (9203) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85471 | - | -
TAEN | SOUTH_CE | HAMLTN_MB1 (9203) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94828 | - | -
TAEN | SOUTH_CE | HAMLTN_MB2 (9202) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93675 | - | - | -
TAEN | SOUTH_CE | HAMLTN_MB2 (9202) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.8547 | - | -
TAEN | SOUTH_CE | HAMLTN_MB2 (9202) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94826 | - | -
TAEPTN | WEST | HARGROVE4A (6648) | L_006648HARGROVE4A-076011L_TWINBU8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91485 | 0.90389 | 0.91566 | -
TAEPTN | WEST | HARGROVE4A (6648) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91719 | - | -
TAEPTN | WEST | HARGROVE4A (6648) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9145 | - | -
TAEPTN | WEST | HARGROVE4A (6648) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91048 | - | -
TAEPTN | WEST | HARGROVE4A (6648) | L2020944-A | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9146 | - | -
TAEPTN | WEST | HARGROVE4A (6648) | LCRA TSC_T429_T9426 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91533 | 0.90431 | 0.91588 | -
RHAYS | SOUTH_CE | HAY_HAYSENG5 (170195) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8743 | - | -
RHAYS | SOUTH_CE | HAY_HAYSENG6 (170196) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8743 | - | -
RHAYS | SOUTH_CE | HAY_HAYSENG7 (170197) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8743 | - | -
RHAYS | SOUTH_CE | HAY_HAYSENG8 (170198) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8743 | - | -
TLCRA | FAR_WEST | HAYTER4A (60444) | L_060385SOLSTICE4A-060444HAYTER4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.84598 | 0.85574 | 0.83804 | 0.91357 | -
TLCRA | FAR_WEST | HAYTER4A (60444) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.0732 | - | - | - | - | - | -
TLCRA | FAR_WEST | HAYTER4A (60444) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.94338 | - | - | - | -
TAEPTC | SOUTHERN | HECKER4A (8565) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89055 | - | -
TAEPTC | SOUTHERN | HECKER4A (8565) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89749 | - | -
TAEPTC | SOUTHERN | HECKER4A (8565) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91301 | - | -
TBREC | NORTH | HENRIETA (767) | L_001426FISHRDSS1_8-001543HENRITAW_9C1 | 138 | Bus High Volts | 1.1 | - | 1.1047 | - | - | 1.1093 | 1.1032 | -
TBREC | NORTH | HENRIETA (767) | L_001452LANHAM_T9-001544HENRIETA_9C1 | 138 | Bus High Volts | 1.1 | - | - | - | - | 1.1034 | - | -
TONCOR | NORTH | HENRIETA_9 (1544) | L_001426FISHRDSS1_8-001543HENRITAW_9C1 | 138 | Bus High Volts | 1.05 | - | 1.1047 | - | 1.0722 | 1.1093 | 1.1032 | -
TONCOR | NORTH | HENRIETA_9 (1544) | L_001452LANHAM_T9-001544HENRIETA_9C1 | 138 | Bus High Volts | 1.05 | - | 1.0975 | - | 1.0687 | 1.1034 | 1.0999 | -
TONCOR | NORTH | HENRITAW_9 (1543) | L_001426FISHRDSS1_8-001543HENRITAW_9C1 | 138 | Bus High Volts | 1.05 | - | 1.1049 | - | 1.0723 | 1.1095 | 1.1033 | -
TONCOR | NORTH_CE | HERTG3_8 (2091) | L_002091HERTG3_8-003009HERTG3_T8C1 | 138 | Bus High Volts | 1.05 | 1.0693 | - | - | - | - | - | -
RHHGT | SOUTH_CE | HHGT_1_5 (170245) | Pre-contingency | 345 | Bus High Volts | 1.05 | - | 1.1144 | - | - | - | - | -
RHHGT | SOUTH_CE | HHGT_1_8 (170238) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.2041 | - | - | - | - | -
RHHGT | SOUTH_CE | HHGT_2_5 (170246) | Pre-contingency | 345 | Bus High Volts | 1.05 | - | 1.1144 | - | - | - | - | -
RHHGT | SOUTH_CE | HHGT_2_8 (170239) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.1997 | - | - | - | - | -
RHHGT | SOUTH_CE | HHGT_3_8 (170240) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.2025 | - | - | - | - | -
RHHGT | SOUTH_CE | HHGT_4_8 (170241) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.2097 | - | - | - | - | -
RHHGT | SOUTH_CE | HHGT_5_8 (170242) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.1997 | - | - | - | - | -
RHHGT | SOUTH_CE | HHGT_X1_8 (170243) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.1989 | - | - | - | - | -
RHHGT | SOUTH_CE | HHGT_X2_8 (170244) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.199 | - | - | - | - | -
TAEN | SOUTH_CE | HICROS_DB1 (9147) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86154 | - | -
TAEN | SOUTH_CE | HICROS_MB1 (9148) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86158 | - | -
TLCRA | SOUTH_CE | HIDDENVL (9207) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.9455 | - | - | -
TLCRA | SOUTH_CE | HIDDENVL (9207) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86285 | - | -
TBREC | NORTH_CE | HIGHPOINT (439) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91734 | - | -
TONCOR | FAR_WEST | HOBLTZL_8 (2299) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86856 | 0.83428 | 0.89517 | -
TAEPTN | FAR_WEST | HOEFSROA4A (60808) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91894 | - | - | - | -
TAEPTN | FAR_WEST | HOEFSROA4A (60808) | L_060383LINTERNA4A-132331REROCK_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91997 | - | - | - | -
TAEPTN | FAR_WEST | HOEFSROA4A (60808) | L_060385SOLSTICE4A-060393PIGCREEK4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.9174 | - | - | - | -
TAEPTN | FAR_WEST | HOEFSROA4A (60808) | L_060385SOLSTICE4A-060716SGSA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.90584 | - | - | - | -
TAEPTN | FAR_WEST | HOEFSROA4A (60808) | L_060385SOLSTICE4A-060808HOEFSROA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.80667 | - | - | - | -
TAEPTN | FAR_WEST | HOEFSROA4A (60808) | L_060393PIGCREEK4A-134245TAYGETE_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91878 | - | - | - | -
TAEPTN | FAR_WEST | HOEFSROA4A (60808) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.0618 | - | - | - | - | - | -
TAEPTN | FAR_WEST | HOEFSROA4A (60808) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.92837 | - | - | - | -
TAEPTN | FAR_WEST | HOEFSROA4A (60808) | SAND LAKE - SOLSTICE 345 KV DCKT LINE (DOUBLE B TO B) WIN 2027 - FUTURE | 138 | Bus Low Volts | 0.92 | - | - | 0.91415 | - | - | - | -
TONCOR | NORTH | HOLLIDAY_8 (11527) | BOWMAN-HOLLIDAY 138 KV SIESTA | 138 | Bus High Volts | 1.05 | - | 1.0673 | - | - | - | - | -
TONCOR | NORTH | HOLLIDAY_8 (11527) | L_001424BOWMAN_B8-011528PECANTRE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.062 | - | - | - | - | -
TONCOR | NORTH | HOLLIDAY_8 (11527) | L_011527HOLLIDAY_8-011528PECANTRE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0673 | - | - | - | - | -
TONCOR | EAST | HOLLY_8 (3277) | JEW-LONG_LAKE-PAL_S_8 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0543 | - | - | - | - | - | -
TONCOR | EAST | HOLLY_8 (3277) | L_003279LONGLKTA_8-003280LONGLAKE_8C1 | 138 | Bus High Volts | 1.05 | 1.0528 | - | - | - | - | - | -
TONCOR | EAST | HOLLY_8 (3277) | L_003280LONGLAKE_8-003284BETO_8C1 | 138 | Bus High Volts | 1.05 | 1.0576 | - | - | - | - | - | -
TONCOR | EAST | HOLLY_8 (3277) | L_003281TENNCLNY_8-003284BETO_8C1 | 138 | Bus High Volts | 1.05 | 1.0568 | - | - | - | - | - | -
TONCOR | EAST | HOLLY_8 (3277) | L_003499BLAKFTAP_8-003509BBRN_OPN_8C1 | 138 | Bus High Volts | 1.05 | 1.0552 | - | - | - | - | - | -
TONCOR | EAST | HOLLY_8 (3277) | L_003509BBRN_OPN_8-003510PINOAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0572 | - | - | - | - | - | -
TAEN | SOUTH_CE | HOLMAN (9073) | AEN_FPP-HO¦LY | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94521 | - | -
TAEN | SOUTH_CE | HOLMAN (9073) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94257 | - | -
TAEN | SOUTH_CE | HOLMAN (9073) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94919 | - | -
TAEN | SOUTH_CE | HOLMAN (9073) | DVCPA1C21B_1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.95 | - | -
TAEN | SOUTH_CE | HOLMAN (9073) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.85713 | - | -
TAEN | SOUTH_CE | HOLMAN (9073) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.90422 | - | -
TAEN | SOUTH_CE | HOLMAN (9073) | L_005133ELMCREEK-005380SHAULAC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94105 | - | -
TAEN | SOUTH_CE | HOLMAN (9073) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94094 | - | -
TAEPTC | SOUTHERN | HOMEPORT4A (8808) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86107 | - | -
TAEPTC | SOUTHERN | HOMEPORT4A (8808) | E_LGE_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91882 | - | -
TAEPTC | SOUTHERN | HOMEPORT4A (8808) | E_NUECES_B_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90614 | - | -
TAEPTC | SOUTHERN | HOMEPORT4A (8808) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91766 | - | -
TAEPTC | SOUTHERN | HOMEPORT4A (8808) | L_008422I_DUPSW4A-008425INGLESID4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.84573 | 0.82703 | 0.72965 | 0.83775 | -
TAEPTC | SOUTHERN | HOMEPORT4A (8808) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87521 | - | -
TAEPTC | SOUTHERN | HOMEPORT4A (8808) | L_008579KATOEN7A-008606GODDARD7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90802 | - | -
TAEPTC | SOUTHERN | HOMEPORT4A (8808) | M105311105321 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91874 | - | -
TAEPTC | SOUTHERN | HOMEPORT4A (8808) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88968 | - | -
TAEPTC | SOUTHERN | HOTIRON4A (8566) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89027 | - | -
TAEPTC | SOUTHERN | HOTIRON4A (8566) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89721 | - | -
TAEPTC | SOUTHERN | HOTIRON4A (8566) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91273 | - | -
TAEPTC | SOUTHERN | HOTIRON4B (8569) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89025 | - | -
TAEPTC | SOUTHERN | HOTIRON4B (8569) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89719 | - | -
TAEPTC | SOUTHERN | HOTIRON4B (8569) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91272 | - | -
RBARIL | FAR_WEST | HOVEY_8 (181652) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.0728 | - | - | - | - | - | -
RBARIL | FAR_WEST | HOVEY_8 (181652) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.9449 | - | - | - | -
TAEN | SOUTH_CE | HOWARDLN (9217) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.92892 | - | 0.94756 | -
TAEN | SOUTH_CE | HOWARDLN (9217) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.8537 | - | -
TAEN | SOUTH_CE | HOWARDLN (9217) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94732 | - | -
TONCOR | FAR_WEST | HOWD2599_8 (11325) | BIG SPRING WEST SWITCH - BIG SPRING 138 KV WIN 2025 - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | 0.89857 | - | - | - | - | - | -
TONCOR | FAR_WEST | HOWD2599_8 (11325) | L_001322BIGSPRIG_8-010044STEER_8C1 | 138 | Bus Low Volts | 0.9 | 0.88295 | - | - | - | - | - | -
TONCOR | FAR_WEST | HOWD2599_8 (11325) | L_010044STEER_8-011316BSPGWSW_8C1 | 138 | Bus Low Volts | 0.9 | 0.88297 | - | - | - | - | - | -
TONCOR | SOUTH_CE | HUTTO_SUB1_8 (3657) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87623 | - | -
TONCOR | SOUTH_CE | HUTTO_SUB2_8 (3656) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87627 | - | -
TONCOR | SOUTH_CE | HUTTOSS__5 (3696) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | 0.88818 | 0.89892 | 0.87472 | 0.82969 | - | 0.86135 | -
TONCOR | SOUTH_CE | HUTTOSS__5 (3696) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.81352 | - | -
TONCOR | SOUTH_CE | HUTTOSS__5 (3696) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89256 | - | -
TONCOR | SOUTH_CE | HUTTOSS__5 (3696) | LCRA TSC_T510_T775 | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89251 | 0.89172 | - | -
TONCOR | SOUTH_CE | HUTTOSS__5 (3696) | LCRATSC_4_WHISVA_HORNSB | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89862 | 0.89692 | - | -
TONCOR | SOUTH_CE | HUTTOSS__5 (3696) | LCRATSC_5_HORNSB_EUCLID | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89058 | 0.89016 | - | -
TONCOR | SOUTH_CE | HUTTOSS__5 (3696) | LCRATSC_6_EUCLID_JOHNDU | 345 | Bus Low Volts | 0.9 | - | - | - | 0.8703 | 0.86164 | 0.87948 | -
TONCOR | SOUTH_CE | HUTTOSS__5 (3696) | LCRATSC_7_JOHNDU_ZORN__ | 345 | Bus Low Volts | 0.9 | - | - | - | 0.8907 | 0.8958 | - | -
TONCOR | SOUTH_CE | HUTTOSS__5 (3696) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | 0.93334 | 0.93253 | 0.94787 | -
TONCOR | SOUTH_CE | HUTTOSS1_8 (3666) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87632 | - | -
TAEN | SOUTH_CE | HV138_CAP (9008) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94553 | - | - | -
TAEN | SOUTH_CE | HV138_CAP (9008) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86288 | - | -
TBREC | EAST | HWY6 (6) | L_032878BRYN_GRNPRAI-032895BRYN_WBRN138C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89702 | 0.90095 | -
TAEPTC | SOUTHERN | I_DUPP14A (8817) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87242 | - | -
TAEPTC | SOUTHERN | I_DUPP14A (8817) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89561 | - | -
TAEPTC | SOUTHERN | I_DUPP14A (8817) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90902 | - | -
TAEPTC | SOUTHERN | I_DUPP14B (8819) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87232 | - | -
TAEPTC | SOUTHERN | I_DUPP14B (8819) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89573 | - | -
TAEPTC | SOUTHERN | I_DUPP14B (8819) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90914 | - | -
TAEPTC | SOUTHERN | I_DUPSW4A (8422) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87772 | - | -
TAEPTC | SOUTHERN | I_DUPSW4A (8422) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89284 | - | -
TAEPTC | SOUTHERN | I_DUPSW4A (8422) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90623 | - | -
TONCOR | FAR_WEST | IMPERIAL_8 (11240) | L_011242CRTNYCRK_8-060792ATHEY4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88426 | 0.85397 | 0.87039 | -
TONCOR | NORTH_CE | INDUST_W8 (2974) | INDUSTRIAL-SARGENT RD DCKT (DOUBLE B TO B) A | 138 | Bus High Volts | 1.05 | 1.0638 | - | 1.0666 | 1.0671 | 1.0688 | - | -
RINERT | NORTH | INERTIA_T1 (144066) | Pre-contingency | 125 | Bus High Volts | 1.05 | 1.0517 | 1.0545 | 1.0513 | 1.0537 | 1.0539 | 1.0549 | -
TAEPTC | SOUTHERN | INGLCOSW4A (8968) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87207 | - | -
TAEPTC | SOUTHERN | INGLCOSW4A (8968) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89602 | - | -
TAEPTC | SOUTHERN | INGLCOSW4A (8968) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90943 | - | -
TAEPTC | SOUTHERN | INGLESID4A (8425) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86631 | - | -
TAEPTC | SOUTHERN | INGLESID4A (8425) | E_NUECES_B_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9108 | - | -
TAEPTC | SOUTHERN | INGLESID4A (8425) | L_008422I_DUPSW4A-008425INGLESID4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.85128 | 0.83295 | 0.73688 | 0.84331 | -
TAEPTC | SOUTHERN | INGLESID4A (8425) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88026 | - | -
TAEPTC | SOUTHERN | INGLESID4A (8425) | L_008579KATOEN7A-008606GODDARD7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91265 | - | -
TAEPTC | SOUTHERN | INGLESID4A (8425) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89454 | - | -
TONCOR | NORTH_CE | IRV_VR1_5 (2389) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | 0.94982 | 0.94302 | - | -
TONCOR | NORTH_CE | JARRELL_E_8 (3688) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88277 | - | - | -
TONCOR | NORTH_CE | JARRELL_E_8 (3688) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.82449 | - | -
TAEPTC | SOUTHERN | JCKSLPOI4A (88173) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89136 | - | -
TAEPTC | SOUTHERN | JCKSLPOI4A (88173) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89762 | - | -
TAEPTC | SOUTHERN | JCKSLPOI4A (88173) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91363 | - | -
TAEPTN | WEST | JERRY4A (6559) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91632 | 0.89501 | 0.90181 | -
TAEPTN | WEST | JERRY4A (6559) | L_006536BIGLAKE4B-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90993 | - | -
TAEPTN | WEST | JERRY4A (6559) | L_006648HARGROVE4A-060374PUMPJACK4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91819 | - | -
TAEPTN | WEST | JERRY4A (6559) | L_006648HARGROVE4A-076011L_TWINBU8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91256 | - | -
TAEPTN | WEST | JERRY4A (6559) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88786 | 0.86959 | 0.88559 | -
TAEPTN | WEST | JERRY4A (6559) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88491 | 0.86589 | 0.88216 | -
TAEPTN | WEST | JERRY4A (6559) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88019 | 0.86001 | 0.87667 | -
TAEPTN | WEST | JERRY4A (6559) | L2020944-A | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88498 | 0.86601 | 0.88223 | -
TAEPTN | WEST | JERRY4A (6559) | LCRA TSC_T429_T9426 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91297 | - | -
TAEPTN | WEST | JERRY4A (6559) | T_006535BIGLAKE4A-006536BIGLAKE4BC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91449 | - | -
TBREC | NORTH_CE | JESSICA (404) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.90753 | 0.87768 | - | -
TBREC | NORTH_CE | JESSICA (404) | KEMP RANCH - SOAP CREEK / SARDIS 138 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91761 | - | -
TBREC | NORTH_CE | JESSICA (404) | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91057 | - | -
TBREC | NORTH_CE | JESSICA (404) | L_002305AIRPRD_T8-002307MDLTHTXI1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91321 | - | -
TBREC | NORTH_CE | JESSICA (404) | L_002308MDLTH_S_8-002309WAX_NW_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91652 | - | -
TAEN | SOUTH_CE | JETT (9220) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93732 | - | - | -
TAEN | SOUTH_CE | JETT (9220) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85487 | - | -
TAEN | SOUTH_CE | JETT (9220) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94804 | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | 3WT_001302WILLOWVAL_5_001301WILLOWVAL_8_018537WILLOWVAL_3 C 3 | 138 | Bus High Volts | 1.05 | - | 1.0537 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001163LAMESA_8-001307KEYLYNTE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0601 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001163LAMESA_8-010008LAMESA2_8C1 | 138 | Bus High Volts | 1.05 | 1.0548 | 1.0655 | 1.051 | 1.0563 | 1.0511 | 1.0529 | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001163LAMESA_8-011363HARDYMGN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0517 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0537 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0538 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001177TEXMABEE_8-011175BAIRDLAK_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0558 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0555 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0559 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001181ANDHWY87_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0576 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0535 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0525 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0553 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0624 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001307KEYLYNTE_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0606 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001308GAILLYNT_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0607 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_001355BUZZDRAW_8-011363HARDYMGN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0526 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_010008LAMESA2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | 1.0517 | 1.0623 | - | 1.0532 | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0521 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_011167ALKALILK2_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.052 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_011167ALKALILK2_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0558 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | LAMESA - BUZZARD DRAW 138 KV LINE 2018 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0517 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | LAMESA - BUZZARD DRAW 69/138 KV DCKT LINE 2019 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0532 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | 1.0627 | 1.0846 | 1.0614 | 1.061 | 1.0577 | 1.0603 | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | MIDLAND COUNTY NW - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.058 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | MIDLAND COUNTY NW - MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0575 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | - | 1.0543 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0532 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | NORTH ANDREWS - MCKENZIE 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0523 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | WILLOW VALLEY - LAMESA 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0602 | - | - | - | - | -
TONCOR | FAR_WEST | JIMPAYNE_8 (18880) | WILLOW VALLEY TRANSFORMER 1 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0537 | - | - | - | - | -
TAEN | SOUTH_CE | JOLLYVIL (9223) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.9341 | - | - | -
TAEN | SOUTH_CE | JOLLYVIL (9223) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85479 | - | -
TONCOR | SOUTH_CE | JONAH_8 (3540) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87765 | - | - | -
TONCOR | SOUTH_CE | JONAH_8 (3540) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.81855 | - | -
TONCOR | SOUTH_CE | JONAHT_8 (3539) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87934 | - | - | -
TONCOR | SOUTH_CE | JONAHT_8 (3539) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.82036 | - | -
TCNPE | COAST | JONCRK__B345 (42530) | P7-1_E1>>T1827A | 345 | Bus High Volts | 1.05 | 1.0536 | - | 1.0535 | 1.0538 | - | - | -
TCNPE | COAST | JONCRK18LR (47531) | P7-1_E1>>T1827A | 345 | Bus High Volts | 1.05 | 1.0509 | - | - | 1.0503 | - | - | -
TBREC | NORTH_CE | JOPLIN (562) | L_000562JOPLIN-000579JCKCNTY8C1 | 138 | Bus High Volts | 1.05 | 1.0506 | 1.0506 | 1.0506 | 1.0506 | 1.0506 | 1.0506 | -
TBREC | NORTH_CE | JOSHUA (398) | L_000394CONCORD8-000398JOSHUAC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9132 | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | 3WT_001302WILLOWVAL_5_001301WILLOWVAL_8_018537WILLOWVAL_3 C 3 | 138 | Bus High Volts | 1.05 | - | 1.0537 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001163LAMESA_8-001307KEYLYNTE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0601 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001163LAMESA_8-010008LAMESA2_8C1 | 138 | Bus High Volts | 1.05 | 1.0548 | 1.0655 | 1.051 | 1.0563 | 1.0511 | 1.0529 | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001163LAMESA_8-011363HARDYMGN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0517 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0537 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0538 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001177TEXMABEE_8-011175BAIRDLAK_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0558 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0555 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0559 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001181ANDHWY87_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0576 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0535 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0525 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0553 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0624 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001307KEYLYNTE_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0606 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001308GAILLYNT_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0607 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_001355BUZZDRAW_8-011363HARDYMGN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0526 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_010008LAMESA2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | 1.0517 | 1.0623 | - | 1.0532 | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0521 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_011167ALKALILK2_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.052 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_011167ALKALILK2_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0558 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | LAMESA - BUZZARD DRAW 138 KV LINE 2018 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0517 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | LAMESA - BUZZARD DRAW 69/138 KV DCKT LINE 2019 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0532 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | 1.0627 | 1.0846 | 1.0614 | 1.061 | 1.0577 | 1.0603 | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | MIDLAND COUNTY NW - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.058 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | MIDLAND COUNTY NW - MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0575 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | - | 1.0543 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0532 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | NORTH ANDREWS - MCKENZIE 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0523 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | WILLOW VALLEY - LAMESA 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0602 | - | - | - | - | -
TGSEC | FAR_WEST | JPAYNE_CB_8 (9419) | WILLOW VALLEY TRANSFORMER 1 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0537 | - | - | - | - | -
TONCOR | FAR_WEST | JUDKINS_8 (1102) | L_001013WOLFSS_8-001103SANDHLTA_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0615 | - | - | - | - | -
TAEN | SOUTH_CE | JV138_CAP (9009) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93413 | - | - | -
TAEN | SOUTH_CE | JV138_CAP (9009) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85482 | - | -
RKEECH | NORTH_CE | KEECHI_8 (150982) | L_000562JOPLIN-000579JCKCNTY8C1 | 138 | Bus High Volts | 1.05 | 1.0511 | 1.051 | 1.0511 | 1.0511 | 1.0511 | 1.0511 | -
TONCOR | NORTH_CE | KEENE_8 (2294) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88369 | - | -
TONCOR | NORTH_CE | KEENE_8 (2294) | BEPC_306 | 138 | Bus Low Volts | 0.9 | 0.89786 | 0.87351 | - | - | - | - | -
TONCOR | NORTH_CE | KEENE_8 (2294) | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.87989 | 0.84912 | - | - | - | -
TONCOR | NORTH_CE | KEENE_8 (2294) | L_000442RAILPORT-001908VENUSC1 | 138 | Bus Low Volts | 0.9 | - | 0.87968 | 0.84561 | - | - | - | -
TONCOR | NORTH_CE | KEENE_8 (2294) | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | Bus Low Volts | 0.9 | 0.89782 | 0.87291 | - | - | - | - | -
TONCOR | FAR_WEST | KELTONWND_8 (11145) | L_001023MIDLNDE_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0563 | - | - | - | - | -
TONCOR | FAR_WEST | KELTONWND_8 (11145) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | 1.0509 | 1.0642 | - | - | - | - | -
TONCOR | FAR_WEST | KELTONWND_8 (11145) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0629 | - | - | - | - | -
TONCOR | FAR_WEST | KELTONWND_8 (11145) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0512 | 1.0639 | - | - | - | - | -
TONCOR | FAR_WEST | KELTONWND_8 (11145) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0536 | 1.0654 | - | 1.0514 | - | - | -
TONCOR | NORTH_CE | KEMPRNCH_8 (2303) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.8685 | 0.83422 | 0.89511 | -
TGSEC | WEST | KETCHUM_8 (60379) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91865 | - | -
TGSEC | WEST | KETCHUM_8 (60379) | L_006648HARGROVE4A-060374PUMPJACK4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91097 | - | -
TGSEC | WEST | KETCHUM_8 (60379) | L_006648HARGROVE4A-076011L_TWINBU8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91462 | 0.90368 | 0.91543 | -
TGSEC | WEST | KETCHUM_8 (60379) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91711 | 0.90058 | 0.91466 | -
TGSEC | WEST | KETCHUM_8 (60379) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91469 | 0.89754 | 0.91187 | -
TGSEC | WEST | KETCHUM_8 (60379) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91103 | 0.89295 | 0.90762 | -
TGSEC | WEST | KETCHUM_8 (60379) | L2020944-A | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91476 | 0.89765 | 0.91193 | -
TGSEC | WEST | KETCHUM_8 (60379) | LCRA TSC_T429_T9426 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.9151 | 0.9041 | 0.91566 | -
TONCOR | FAR_WEST | KEYLYNTE_8 (1307) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.063 | - | - | - | - | -
TONCOR | FAR_WEST | KEYLYNTE_8 (1307) | L_001307KEYLYNTE_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0593 | - | - | - | - | -
TONCOR | FAR_WEST | KEYLYNTE_8 (1307) | L_001308GAILLYNT_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0595 | - | - | - | - | -
TONCOR | NORTH_CE | KILL_SS__5 (3422) | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus High Volts | 1.05 | 1.102 | - | 1.1065 | 1.0951 | 1.1017 | 1.1041 | -
TONCOR | NORTH_CE | KILL_SS__5 (3422) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89003 | - | -
TSHARL | SOUTHERN | KINGFISHER (79501) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | 0.90446 | - | - | -
TSHARL | SOUTHERN | KINGFISHER (79501) | E5DVA1C1_1_B | 345 | Bus Low Volts | 0.95 | - | - | - | 0.91126 | - | - | -
TSHARL | SOUTHERN | KINGFISHER (79501) | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | Bus Low Volts | 0.95 | - | - | - | 0.94892 | 0.94043 | - | -
TAEN | SOUTH_CE | KINGSB_DB1 (9123) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.9464 | - | - | -
TAEN | SOUTH_CE | KINGSB_DB1 (9123) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86024 | - | -
TAEN | SOUTH_CE | KINGSB_MB1 (9122) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94635 | - | - | -
TAEN | SOUTH_CE | KINGSB_MB1 (9122) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86019 | - | -
TONCOR | NORTH_CE | KLEBRG1_8 (3078) | L_002429WATMLL_8-003083WILMER1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89279 | 0.88207 | - | -
TONCOR | NORTH_CE | KLEBRG1_8 (3078) | L_002434SGVLSW1_8-003076SGVL1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89318 | - | -
TONCOR | NORTH_CE | KLEBRG1_8 (3078) | L_003076SGVL1_8-003077KLEBRG1T_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8992 | - | -
TONCOR | NORTH_CE | KLEBRG1T_8 (3077) | L_002429WATMLL_8-003083WILMER1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89415 | 0.88343 | - | -
TONCOR | NORTH_CE | KLEBRG1T_8 (3077) | L_002434SGVLSW1_8-003076SGVL1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89451 | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 345 | Bus High Volts | 1.05 | 1.0578 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-1 | 345 | Bus High Volts | 1.05 | 1.0559 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 345 | Bus High Volts | 1.05 | 1.0645 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-1 | 345 | Bus High Volts | 1.05 | 1.0559 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 345 | Bus High Volts | 1.05 | 1.0645 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 345 | Bus High Volts | 1.05 | 1.0575 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 345 | Bus High Volts | 1.05 | 1.0665 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 345 | Bus High Volts | 1.05 | 1.0589 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 345 | Bus High Volts | 1.05 | 1.068 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 345 | Bus High Volts | 1.05 | 1.0575 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 345 | Bus High Volts | 1.05 | 1.0665 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 345 | Bus High Volts | 1.05 | 1.0589 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 345 | Bus High Volts | 1.05 | 1.068 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-1 | 345 | Bus High Volts | 1.05 | 1.0538 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 345 | Bus High Volts | 1.05 | 1.0623 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-1 | 345 | Bus High Volts | 1.05 | 1.0538 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 345 | Bus High Volts | 1.05 | 1.0622 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN-MOSES 345-138 AUTO-2 | 345 | Bus High Volts | 1.05 | 1.0569 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLEN-MOSES 345-138W/O AUTO-2 | 345 | Bus High Volts | 1.05 | 1.0568 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 345 | Bus High Volts | 1.05 | 1.0589 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 345 | Bus High Volts | 1.05 | 1.0684 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 345 | Bus High Volts | 1.05 | 1.0581 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 345 | Bus High Volts | 1.05 | 1.0673 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | ANNA 345 KV - KRUM WEST/CEDAR ELM (DOUBLE B TO B) | 345 | Bus High Volts | 1.05 | 1.0519 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | BEPC_22 | 345 | Bus High Volts | 1.05 | 1.0523 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | G_001729VAL_STH_5UB1 | 345 | Bus High Volts | 1.05 | 1.0531 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | L_001690VALLYSES1_5-011683PACIFICSW_5C1 | 345 | Bus High Volts | 1.05 | 1.0526 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 345 | Bus High Volts | 1.05 | 1.0568 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | L_140077KMCHI_1_5-140078KMCHI_2_5C1 | 345 | Bus High Volts | 1.05 | 1.0671 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | L_140077KMCHI_1_5-140078KMCHI_2_5C2 | 345 | Bus High Volts | 1.05 | 1.0671 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 345 | Bus High Volts | 1.05 | 1.0568 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | PINEFOREST_CON | 345 | Bus High Volts | 1.05 | 1.0531 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | Pre-contingency | 345 | Bus High Volts | 1.05 | - | 1.1066 | 1.0988 | 1.1415 | 1.1584 | 1.1122 | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | S_002374ANNASW_81 | 345 | Bus High Volts | 1.05 | 1.0506 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | Bus High Volts | 1.05 | 1.0549 | - | - | - | - | - | -
RKIOWA | NORTH | KMCHI_1_5 (140077) | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | Bus High Volts | 1.05 | 1.0543 | - | - | - | - | - | -
TONCOR | NORTH_CE | KNGSCRK2_5 (15203) | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89295 | - | - | -
TONCOR | NORTH_CE | KNGSCRK2_5 (15203) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89867 | - | -
TONCOR | NORTH_CE | KNGSCRK2_5 (15203) | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88952 | - | -
TONCOR | NORTH_CE | KNGSCRK2_5 (15203) | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89949 | - | -
TONCOR | NORTH_CE | KNGSCRK2_5 (15203) | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89872 | - | -
TONCOR | NORTH_CE | KNGSCRK2_5 (15203) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88953 | - | -
TONCOR | NORTH_CE | KNGSCRK2_5 (15203) | TRIN-SK*ME (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88026 | - | -
TONCOR | NORTH_CE | KNGSCRK2_5 (15203) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8975 | - | -
TAEN | SOUTH_CE | KRAMER (9276) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93401 | - | - | -
TAEN | SOUTH_CE | KRAMER (9276) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85387 | - | -
TAEN | SOUTH_CE | KRAMER (9276) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94665 | - | -
TLCRA | SOUTH_CE | L_ALUMCR8_1Y (7318) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87854 | - | -
TLCRA | SOUTH_CE | L_AUSTRO5_1Y (7040) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.82451 | - | -
TLCRA | SOUTH_CE | L_AUSTRO5_1Y (7040) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91209 | - | -
TLCRA | SOUTH_CE | L_AVERRA8_1Y (7534) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85478 | - | -
TLCRA | SOUTH_CE | L_BALCRE8_1Y (78221) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8556 | - | -
TLCRA | SOUTH_CE | L_BARETA8_1Y (78220) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8556 | - | -
TLCRA | SOUTH_CE | L_BASTCI8_1Y (7322) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8675 | - | -
TLCRA | SOUTH_CE | L_BASTCI8_2Y (7319) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86601 | - | -
TLCRA | SOUTH_CE | L_BASTEN5_1Y (7049) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.82278 | - | -
TLCRA | SOUTH_CE | L_BASTEN5_1Y (7049) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90691 | - | -
TLCRA | SOUTH_CE | L_BASTWE8_1Y (7555) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86238 | - | -
TLCRA | SOUTH_CE | L_BASTWE8_1Y (7555) | L_007310L_SIMGID8_1Y-007555L_BASTWE8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | - | 0.91268 | -
TLCRA | SOUTH_CE | L_BEBACK8_1Y (7187) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91625 | - | -
TLCRA | SOUTH_CE | L_BEECRE8_1Y (7540) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87913 | - | -
TLCRA | SOUTH_CE | L_BELLNO8_1Y (7287) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8841 | - | -
TLCRA | SOUTH_CE | L_BELLNO8_1Y (7287) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90931 | - | -
TLCRA | SOUTH_CE | L_BELLSO8_1Y (7270) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89629 | - | -
TLCRA | SOUTH_CE | L_BELLSO8_1Y (7270) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91771 | - | -
TLCRA | SOUTH_CE | L_BERGHE5_1Y (7770) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91295 | - | -
TLCRA | SOUTH_CE | L_BERRCR8_1Y (7361) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91918 | - | - | -
TLCRA | SOUTH_CE | L_BERRCR8_1Y (7361) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85405 | - | -
TLCRA | SOUTH_CE | L_BLUEBO8_1Y (7556) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.84786 | - | -
TLCRA | SOUTH_CE | L_BLUEBO8_1Y (7556) | L_007310L_SIMGID8_1Y-007555L_BASTWE8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | - | 0.91044 | -
TLCRA | SOUTH_CE | L_BLUEBO8_1Y (7556) | L_007555L_BASTWE8_1Y-007556L_BLUEBO8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | - | 0.90723 | -
TLCRA | SOUTH_CE | L_BRENHA8_1Y (7292) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91164 | - | -
TLCRA | SOUTH_CE | L_BRENHA8_1Y (7292) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9148 | - | -
TLCRA | SOUTH_CE | L_BRENHA8_1Y (7292) | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91969 | - | -
TLCRA | SOUTH_CE | L_BRENHA8_1Y (7292) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8376 | - | -
TLCRA | SOUTH_CE | L_BRENHA8_1Y (7292) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88224 | - | -
TLCRA | SOUTH_CE | L_BRENHA8_1Y (7292) | L_005133ELMCREEK-005380SHAULAC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91555 | - | -
TLCRA | SOUTH_CE | L_BRENHA8_1Y (7292) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91806 | - | -
TLCRA | SOUTH_CE | L_BRENNO8_1Y (7294) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91975 | - | -
TLCRA | SOUTH_CE | L_BRENNO8_1Y (7294) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85362 | - | -
TLCRA | SOUTH_CE | L_BRENNO8_1Y (7294) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89362 | - | -
TLCRA | SOUTH_CE | L_BURNET8_1Y (7100) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91245 | - | -
TLCRA | SOUTH_CE | L_BUTLER8_1Y (7324) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88227 | - | -
TLCRA | SOUTH_CE | L_CAMPGA9_1Y (7196) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88143 | - | -
TLCRA | SOUTH_CE | L_CANYON8_1Y (7200) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87897 | - | -
TLCRA | SOUTH_CE | L_CARLSO8_1Y (7338) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88376 | - | -
TLCRA | SOUTH_CE | L_CEDAHI8_1Y (7331) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.84423 | - | -
TLCRA | SOUTH_CE | L_CHAPHI8_1Y (7574) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91957 | - | -
TLCRA | SOUTH_CE | L_CHAPHI8_1Y (7574) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85977 | - | -
TLCRA | SOUTH_CE | L_CHAPHI8_1Y (7574) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89587 | - | -
TLCRA | SOUTH_CE | L_CHEAPS8_1Y (7243) | BAY5_BF | 138 | Bus Low Volts | 0.92 | - | - | 0.91832 | - | 0.91932 | - | -
TLCRA | SOUTH_CE | L_CHEAPS8_1Y (7243) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90498 | - | -
TLCRA | SOUTH_CE | L_CHEAPS8_1Y (7243) | L_007243L_CHEAPS8_1Y-007251L_LINDEN8_1YC1 | 138 | Bus Low Volts | 0.92 | 0.77138 | - | 0.77347 | 0.79079 | 0.77789 | 0.7713 | -
TLCRA | SOUTH_CE | L_CHEAPS8_1Y (7243) | L_007251L_LINDEN8_1Y-007253L_GUADAL8_1YC1 | 138 | Bus Low Volts | 0.92 | 0.77104 | 0.91461 | 0.77429 | 0.77894 | 0.76319 | 0.75491 | -
TLCRA | SOUTH_CE | L_CHEAPS8_1Y (7243) | LCRA TSC_T579 | 138 | Bus Low Volts | 0.92 | 0.77149 | - | 0.77359 | 0.79095 | 0.77811 | 0.77146 | -
TLCRA | SOUTH_CE | L_CHIEBR8_1Y (7366) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | 0.90525 | - | - | -
TLCRA | SOUTH_CE | L_CHIEBR8_1Y (7366) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.83911 | - | -
TLCRA | SOUTH_CE | L_CLEAFO9_1Y (7195) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86867 | - | -
TLCRA | SOUTH_CE | L_CLEASP5_1Y (7050) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.88497 | - | -
TLCRA | SOUTH_CE | L_COLTON8_1Y (7208) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85283 | - | -
TLCRA | SOUTH_CE | L_COLTON8_1Y (7208) | L_007208L_COLTON8_1Y-007325L_MENDOZ8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90222 | - | -
TLCRA | SOUTH_CE | L_COOKPO8_1Y (7569) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.84891 | - | -
TLCRA | SOUTH_CE | L_COOKPO8_1Y (7569) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90606 | - | -
TLCRA | SOUTH_CE | L_CROSSW8_1Y (7503) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86304 | - | -
TLCRA | SOUTH_CE | L_CUERO_8_1Y (7244) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9181 | - | -
TLCRA | SOUTHERN | L_DANFOR8_1Y (7241) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9081 | - | -
TLCRA | SOUTHERN | L_DANFOR8_1Y (7241) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91014 | - | -
TLCRA | SOUTHERN | L_DANFOR8_1Y (7241) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9195 | - | -
TLCRA | SOUTH_CE | L_DRAFTH8_1Y (7295) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85361 | - | -
TLCRA | SOUTH_CE | L_DRAFTH8_1Y (7295) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9014 | - | -
TLCRA | SOUTH_CE | L_ELGISW8_1Y (7321) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88532 | - | -
TLCRA | SOUTH_CE | L_ELROY_8_1Y (7209) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.84644 | - | -
TLCRA | SOUTH_CE | L_ELROY_8_1Y (7209) | L_007208L_COLTON8_1Y-007209L_ELROY_8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91382 | - | -
TLCRA | SOUTH_CE | L_ELROY_8_1Y (7209) | L_007208L_COLTON8_1Y-007325L_MENDOZ8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9031 | - | -
TLCRA | SOUTH_CE | L_ENGLE_8_1Y (7250) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91277 | - | -
TLCRA | SOUTH_CE | L_ESCARP8_1Y (7672) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85914 | - | -
TLCRA | SOUTH_CE | L_EUCLID5_1Y (7510) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.92 | - | - | - | 0.90054 | - | - | -
TLCRA | SOUTH_CE | L_EUCLID5_1Y (7510) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.83856 | - | -
TLCRA | SOUTH_CE | L_EUCLID5_1Y (7510) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91613 | - | -
TLCRA | SOUTH_CE | L_EUCLID5_1Y (7510) | L_007042L_ZORN__5_1Y-007510L_EUCLID5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | 0.91472 | 0.86043 | 0.85962 | 0.87021 | -
TLCRA | SOUTH_CE | L_EUCLID5_1Y (7510) | LCRATSC_6_EUCLID_JOHNDU | 345 | Bus Low Volts | 0.92 | 0.90219 | 0.88429 | 0.88396 | 0.82024 | 0.80855 | 0.82807 | -
TLCRA | SOUTH_CE | L_EUCLID5_1Y (7510) | LCRATSC_7_JOHNDU_ZORN__ | 345 | Bus Low Volts | 0.92 | 0.91909 | 0.91765 | 0.90998 | 0.84328 | 0.84724 | 0.86423 | -
TLCRA | SOUTH_CE | L_FAIRLA8_1Y (7518) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89733 | - | -
RLCRA | SOUTH_CE | L_FARIPU8_1Y (7280) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90647 | - | -
TLCRA | SOUTH_CE | L_FAYEPL8_1Y (7278) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90644 | - | -
TLCRA | SOUTH_CE | L_FAYETT5_1Y (7057) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.85069 | - | -
TLCRA | SOUTH_CE | L_FAYETT5_1Y (7057) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90482 | - | -
TLCRA | SOUTH_CE | L_FAYETT5_1Y (7057) | L_007056L_FPPYD15_1Y-007057L_FAYETT5_1YC1 | 345 | Bus High Volts | 1.05 | - | 1.0682 | - | - | - | - | -
TLCRA | SOUTH_CE | L_FAYETT5_1Y (7057) | LCRA TSC_T210_T211 | 345 | Bus High Volts | 1.05 | - | 1.0625 | - | - | - | - | -
TLCRA | SOUTH_CE | L_FAYETT8_1Y (7286) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90499 | - | -
TLCRA | SOUTH_CE | L_FLATON8_1Y (7248) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91523 | - | -
TLCRA | SOUTH_CE | L_FLOREN8_1Y (7521) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91101 | - | - | -
TLCRA | SOUTH_CE | L_FLOREN8_1Y (7521) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.84608 | - | -
TLCRA | SOUTH_CE | L_FPPYD15_1Y (7056) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.85829 | - | -
TLCRA | SOUTH_CE | L_FPPYD15_1Y (7056) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91442 | - | -
TLCRA | SOUTH_CE | L_FPPYD25_1Y (7055) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.85824 | - | -
TLCRA | SOUTH_CE | L_FPPYD25_1Y (7055) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9143 | - | -
TLCRA | SOUTH_CE | L_FRELSB8_1Y (7263) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91459 | - | -
TLCRA | SOUTH_CE | L_GABRIE8_1Y (7346) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88688 | - | 0.91274 | -
TLCRA | SOUTH_CE | L_GABRIE8_1Y (7346) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.82493 | - | -
TLCRA | SOUTH_CE | L_GARFIE5_1Y (7048) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.82234 | - | -
TLCRA | SOUTH_CE | L_GARFIE5_1Y (7048) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90647 | - | -
TBBEC | SOUTH_CE | L_GAYHIL8_1Y (7572) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91104 | - | -
TBBEC | SOUTH_CE | L_GAYHIL8_1Y (7572) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.912 | - | -
TBBEC | SOUTH_CE | L_GAYHIL8_1Y (7572) | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91719 | - | -
TBBEC | SOUTH_CE | L_GAYHIL8_1Y (7572) | DVCPA1C21B_1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91949 | - | -
TBBEC | SOUTH_CE | L_GAYHIL8_1Y (7572) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.83346 | - | -
TBBEC | SOUTH_CE | L_GAYHIL8_1Y (7572) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88106 | - | -
TBBEC | SOUTH_CE | L_GAYHIL8_1Y (7572) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91843 | - | -
TBBEC | SOUTH_CE | L_GAYHIL8_1Y (7572) | L_005133ELMCREEK-005380SHAULAC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91612 | - | -
TBBEC | SOUTH_CE | L_GAYHIL8_1Y (7572) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91897 | - | -
TBBEC | SOUTH_CE | L_GAYHIL8_1Y (7572) | P7-1_E1>>T1839X2_ERC | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91981 | - | -
TBBEC | SOUTH_CE | L_GAYHIL8_1Y (7572) | P7-1_E1>>T3944Z_ERC | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91912 | - | -
TLCRA | SOUTH_CE | L_GEOREA8_1Y (7528) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | 0.87697 | - | 0.90478 | -
TLCRA | SOUTH_CE | L_GEOREA8_1Y (7528) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.81908 | - | -
TLCRA | SOUTH_CE | L_GEOREA8_1Y (7528) | L_003664RNDRCKWH_T_8-003669RNDRCKWH1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9199 | - | -
TLCRA | SOUTH_CE | L_GEOREA8_1Y (7528) | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | Bus Low Volts | 0.92 | 0.91898 | - | - | 0.9059 | 0.902 | 0.90673 | -
TLCRA | SOUTH_CE | L_GEOREA8_1Y (7528) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91982 | - | -
TLCRA | SOUTH_CE | L_GEOREA8_1Y (7528) | LCRATSC_6_EUCLID_JOHNDU | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91206 | - | -
TLCRA | SOUTH_CE | L_GEORGE8_1Y (7343) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89639 | - | - | -
TLCRA | SOUTH_CE | L_GEORGE8_1Y (7343) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.83182 | - | -
TONCOR | SOUTH_CE | L_GEORSO8_1Y (7532) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | 0.87672 | - | 0.90622 | -
TONCOR | SOUTH_CE | L_GEORSO8_1Y (7532) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8238 | - | -
TONCOR | SOUTH_CE | L_GEORSO8_1Y (7532) | L_003664RNDRCKWH_T_8-003667RNDRCKNE2_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91357 | 0.9102 | 0.91443 | -
TONCOR | SOUTH_CE | L_GEORSO8_1Y (7532) | L_003664RNDRCKWH_T_8-003669RNDRCKWH1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91336 | 0.91 | 0.91422 | -
TONCOR | SOUTH_CE | L_GEORSO8_1Y (7532) | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | Bus Low Volts | 0.92 | 0.90504 | - | 0.90926 | 0.89164 | 0.88754 | 0.89237 | -
TONCOR | SOUTH_CE | L_GEORSO8_1Y (7532) | LCRATSC_6_EUCLID_JOHNDU | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91183 | - | -
TLCRA | SOUTH_CE | L_GIDDIN8_1Y (7302) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8942 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | AEN_DL-AU¦LP_2013 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91919 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | AEN_LP-AU¦DL_2013 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91762 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | AEN_LY-FPP¦CIS | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91481 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | BAS_RANCH_CON | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9182 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | E_B_DAVIS_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91944 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | E_BASTEN_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91904 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | E_FERGCC_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91597 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91975 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | E_NUECES_B_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91837 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | G_170126CALAVER_JKS2UL2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91475 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | G_888839BAS_RANCH_POIUC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91823 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | G_RIO_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91255 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.92 | 0.89743 | 0.90571 | 0.88423 | 0.83901 | - | 0.86972 | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | J5LCA1C1_B | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91239 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91398 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91436 | - | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91094 | - | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91558 | 0.80639 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | L_003696HUTTOSS__5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.9133 | 0.90924 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | L_003696HUTTOSS__5-003699SALADOSS_5C2 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.9133 | 0.90924 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.88798 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91962 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | L_005133ELMCREEK-005380SHAULAC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91798 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | L_005915SO_TEX__345A-008715RADIANT7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91579 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91706 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | L_007041L_JOHNDU5_1Y-007047L_HORNSB5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.89587 | 0.89251 | 0.90697 | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | L_007041L_JOHNDU5_1Y-007050L_CLEASP5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91741 | - | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | L_007042L_ZORN__5_1Y-007510L_EUCLID5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.90694 | 0.90889 | 0.9177 | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | L_007047L_HORNSB5_1Y-007738L_WHISVA5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.90359 | 0.90197 | 0.91187 | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91904 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | L_007340L_GILLCR5_1Y-007738L_WHISVA5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91825 | 0.91779 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | L_007341L_LIMMER5_1Y-007510L_EUCLID5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91954 | - | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | LCRA TSC_T227_T388 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91843 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | LCRA TSC_T255_TAE3121_1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90974 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | LCRA TSC_T510_1 | 345 | Bus Low Volts | 0.92 | - | - | 0.90581 | 0.90266 | 0.90917 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | LCRA TSC_T510_T511_3 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.90275 | 0.91917 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | LCRA TSC_T510_T512_1 | 345 | Bus Low Volts | 0.92 | - | - | 0.9135 | 0.91324 | 0.91796 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | LCRA TSC_T510_T738_1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.90571 | 0.91107 | 0.91501 | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | LCRA TSC_T510_T775 | 345 | Bus Low Volts | 0.92 | - | 0.90937 | 0.90996 | 0.88 | 0.87896 | 0.89024 | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | LCRA TSC_T511_T625_2 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91716 | - | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | LCRATSC_1_HUTTO__LIMMER | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91875 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | LCRATSC_3_GILLCR_WHISVA | 345 | Bus Low Volts | 0.92 | - | - | - | 0.90303 | 0.90528 | 0.91294 | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | LCRATSC_4_WHISVA_HORNSB | 345 | Bus Low Volts | 0.92 | - | - | 0.91959 | 0.88782 | 0.88571 | 0.89566 | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | LCRATSC_5_HORNSB_EUCLID | 345 | Bus Low Volts | 0.92 | - | 0.90938 | 0.90954 | 0.8782 | 0.87744 | 0.8888 | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | LCRATSC_6_EUCLID_JOHNDU | 345 | Bus Low Volts | 0.92 | 0.91624 | 0.89855 | 0.90015 | 0.85948 | 0.85068 | 0.8674 | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | LCRATSC_7_JOHNDU_ZORN__ | 345 | Bus Low Volts | 0.92 | - | - | - | 0.88664 | 0.8956 | 0.91123 | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | LCRATSC_8_ZORN___CLEASP | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91633 | - | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | M10000271115801 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91983 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | MB100002711580 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91983 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | N5GSU2_B | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91475 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | P7-1_E1>>T3944Z_ERC | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91733 | - | -
TLCRA | SOUTH_CE | L_GILLCR5_1Y (7340) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | 0.94356 | 0.92959 | 0.92962 | 0.94259 | -
TLCRA | SOUTH_CE | L_GILLCR8_1Y (7336) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87212 | - | -
TLCRA | SOUTH_CE | L_GLASSC8_1Y (7523) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89965 | - | - | -
TLCRA | SOUTH_CE | L_GLASSC8_1Y (7523) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.83525 | - | -
TLCRA | SOUTH_CE | L_GOFORT8_1Y (7501) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86463 | - | -
TLCRA | SOUTH_CE | L_GONZAL8_1Y (7245) | BAY5_BF | 138 | Bus Low Volts | 0.92 | 0.91238 | - | 0.90839 | 0.91881 | 0.90595 | - | -
TLCRA | SOUTH_CE | L_GONZAL8_1Y (7245) | E_B_DAVIS_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91894 | - | -
TLCRA | SOUTH_CE | L_GONZAL8_1Y (7245) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91949 | - | -
TLCRA | SOUTH_CE | L_GONZAL8_1Y (7245) | E_NUECES_B_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91681 | - | -
TLCRA | SOUTH_CE | L_GONZAL8_1Y (7245) | E_VICTORIA_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91736 | - | -
TLCRA | SOUTH_CE | L_GONZAL8_1Y (7245) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89481 | - | -
TLCRA | SOUTH_CE | L_GONZAL8_1Y (7245) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91033 | - | -
TLCRA | SOUTH_CE | L_GONZAL8_1Y (7245) | L_007243L_CHEAPS8_1Y-007245L_GONZAL8_1YC1 | 138 | Bus Low Volts | 0.92 | 0.82239 | - | 0.822 | 0.8274 | 0.8307 | 0.82318 | -
TLCRA | SOUTH_CE | L_GONZAL8_1Y (7245) | L_007243L_CHEAPS8_1Y-007251L_LINDEN8_1YC1 | 138 | Bus Low Volts | 0.92 | 0.77458 | - | 0.77678 | 0.79424 | 0.78154 | 0.77499 | -
TLCRA | SOUTH_CE | L_GONZAL8_1Y (7245) | L_007244L_CUERO_8_1Y-007253L_GUADAL8_1YC1 | 138 | Bus Low Volts | 0.92 | 0.91319 | - | 0.91155 | 0.91874 | 0.90766 | - | -
TLCRA | SOUTH_CE | L_GONZAL8_1Y (7245) | L_007244L_CUERO_8_1Y-089450THOMASTN4BC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91794 | - | -
TLCRA | SOUTH_CE | L_GONZAL8_1Y (7245) | L_007251L_LINDEN8_1Y-007253L_GUADAL8_1YC1 | 138 | Bus Low Volts | 0.92 | 0.77485 | 0.91814 | 0.77823 | 0.78311 | 0.76764 | 0.75944 | -
TLCRA | SOUTH_CE | L_GONZAL8_1Y (7245) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91767 | - | -
TLCRA | SOUTH_CE | L_GONZAL8_1Y (7245) | LCRA TSC_T579 | 138 | Bus Low Volts | 0.92 | 0.77469 | - | 0.77691 | 0.7944 | 0.78176 | 0.77515 | -
TLCRA | SOUTH_CE | L_GONZAL8_1Y (7245) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.93545 | 0.94829 | -
TLCRA | SOUTH_CE | L_GUADAL8_1Y (7253) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91745 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | BAS_RANCH_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91945 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90859 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91154 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91637 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | DVCPA1C21B_1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91739 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | G_888839BAS_RANCH_POIUC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91948 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | G_RIO_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91885 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | J5LCA1C1_B | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91879 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.83082 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87784 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91657 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | L_005133ELMCREEK-005380SHAULAC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91184 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | L_005915SO_TEX__345A-008715RADIANT7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91894 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91406 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | L_007289L_SALEM_8_1Y-007564L_GUYBUR8_1YC1 | 138 | Bus Low Volts | 0.92 | 0.91529 | - | 0.91514 | 0.91671 | 0.89144 | 0.90689 | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | LCRA TSC_T255_TAE3121_1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91726 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | P7-1_E1>>T1839X2_ERC | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91769 | - | -
TLCRA | SOUTH_CE | L_GUYBUR8_1Y (7564) | P7-1_E1>>T3944Z_ERC | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91698 | - | -
TLCRA | SOUTH_CE | L_HALLET8_1Y (7246) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89683 | - | -
TLCRA | SOUTH_CE | L_HARRBR8_1Y (7333) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.84163 | - | -
TLCRA | SOUTH_CE | L_HAYSEN5_1Y (7043) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.87421 | - | -
TLCRA | FAR_WEST | L_HAYTER8_1Y (78925) | L_060385SOLSTICE4A-060444HAYTER4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.84598 | 0.85574 | 0.83804 | 0.91357 | -
TLCRA | FAR_WEST | L_HAYTER8_1Y (78925) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.0732 | - | - | - | - | - | -
TLCRA | FAR_WEST | L_HAYTER8_1Y (78925) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.94338 | - | - | - | -
TLCRA | SOUTH_CE | L_HENNE_8_1Y (7174) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91984 | - | -
TLCRA | SOUTH_CE | L_HENNE_8_2Y (7172) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91582 | - | -
TLCRA | SOUTH_CE | L_HICROS8_1Y (7202) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86156 | - | -
TLCRA | SOUTH_CE | L_HIDDVA8_1Y (78207) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86287 | - | -
TLCRA | SOUTH_CE | L_HIGH368_1Y (7291) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.913 | - | -
TLCRA | SOUTH_CE | L_HIGH368_1Y (7291) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91614 | - | -
TLCRA | SOUTH_CE | L_HIGH368_1Y (7291) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.84148 | - | -
TLCRA | SOUTH_CE | L_HIGH368_1Y (7291) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88456 | - | -
TLCRA | SOUTH_CE | L_HIGH368_1Y (7291) | L_005133ELMCREEK-005380SHAULAC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91753 | - | -
TLCRA | SOUTH_CE | L_HIGH468_1Y (7177) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91688 | - | -
TLCRA | SOUTH_CE | L_HILBIG8_1Y (7576) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86731 | - | -
TLCRA | SOUTH_CE | L_HILLTO8_1Y (7190) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88888 | - | -
TLCRA | SOUTH_CE | L_HORNSB5_1Y (7047) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.92 | 0.91436 | - | 0.89927 | 0.85445 | - | 0.8888 | -
TLCRA | SOUTH_CE | L_HORNSB5_1Y (7047) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.81799 | - | -
TLCRA | SOUTH_CE | L_HORNSB5_1Y (7047) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.902 | - | -
TLCRA | SOUTH_CE | L_HORNSB5_1Y (7047) | L_007041L_JOHNDU5_1Y-007047L_HORNSB5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | 0.91888 | 0.88822 | 0.88483 | 0.89946 | -
TLCRA | SOUTH_CE | L_HORNSB5_1Y (7047) | LCRA TSC_T510_1 | 345 | Bus Low Volts | 0.92 | - | - | 0.91912 | 0.91897 | - | - | -
TLCRA | SOUTH_CE | L_HORNSB5_1Y (7047) | LCRA TSC_T510_T511_3 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.90731 | - | - | -
TLCRA | SOUTH_CE | L_HORNSB5_1Y (7047) | LCRA TSC_T510_T775 | 345 | Bus Low Volts | 0.92 | - | 0.90049 | 0.90534 | 0.87216 | 0.87111 | 0.88253 | -
TLCRA | SOUTH_CE | L_HORNSB5_1Y (7047) | LCRATSC_5_HORNSB_EUCLID | 345 | Bus Low Volts | 0.92 | - | 0.9005 | 0.90492 | 0.87034 | 0.86958 | 0.88107 | -
TLCRA | SOUTH_CE | L_HORNSB5_1Y (7047) | LCRATSC_6_EUCLID_JOHNDU | 345 | Bus Low Volts | 0.92 | 0.9127 | 0.88954 | 0.89545 | 0.85138 | 0.84247 | 0.8594 | -
TLCRA | SOUTH_CE | L_HORNSB5_1Y (7047) | LCRATSC_7_JOHNDU_ZORN__ | 345 | Bus Low Volts | 0.92 | - | - | - | 0.8911 | 0.90795 | - | -
TLCRA | SOUTH_CE | L_HORNSB5_1Y (7047) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | 0.94351 | 0.94423 | - | -
TLCRA | SOUTH_CE | L_HOWALA8_1Y (7335) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85367 | - | -
TLCRA | SOUTH_CE | L_JOHNDU5_1Y (7041) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.87309 | - | -
TLCRA | SOUTH_CE | L_JOHNDU5_1Y (7041) | LCRATSC_7_JOHNDU_ZORN__ | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91857 | - | - | -
TLCRA | SOUTH_CE | L_KENTST8_1Y (7530) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85486 | - | -
TLCRA | SOUTH_CE | L_KIMBRO8_1Y (7337) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.884 | - | -
TLCRA | FAR_WEST | L_KUNITZ8_1Y (7387) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.0522 | - | - | - | - | -
TLCRA | SOUTH_CE | L_LACIMA8_1Y (7185) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89419 | - | -
TLCRA | SOUTH_CE | L_LAGRAN8_1Y (7276) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90795 | - | -
TLCRA | SOUTH_CE | L_LAKEAE8_1Y (7349) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86834 | - | -
TLCRA | SOUTH_CE | L_LAKEWA8_1Y (7538) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87489 | - | -
TLCRA | SOUTH_CE | L_LEXING8_1Y (7571) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86995 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | AEN_LY-FPP¦CIS | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91723 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | E_FERGCC_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91812 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | G_170126CALAVER_JKS2UL2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91711 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | G_RIO_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91517 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.92 | 0.88963 | 0.90011 | 0.87599 | 0.83105 | - | 0.86283 | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | J5LCA1C1_B | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91503 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91268 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91582 | - | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91257 | - | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91715 | 0.8116 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | L_003696HUTTOSS__5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91189 | 0.90769 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | L_003696HUTTOSS__5-003699SALADOSS_5C2 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91189 | 0.90769 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89109 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | L_005133ELMCREEK-005380SHAULAC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91955 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | L_005915SO_TEX__345A-008715RADIANT7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91812 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | L_007041L_JOHNDU5_1Y-007047L_HORNSB5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.90872 | 0.90514 | 0.91934 | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | L_007042L_ZORN__5_1Y-007510L_EUCLID5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.90324 | 0.90457 | 0.91432 | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | L_007047L_HORNSB5_1Y-007738L_WHISVA5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.9149 | 0.91309 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | L_007341L_LIMMER5_1Y-007510L_EUCLID5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91873 | - | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | LCRA TSC_T255_TAE3121_1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9126 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | LCRA TSC_T510_1 | 345 | Bus Low Volts | 0.92 | - | - | 0.9005 | 0.89576 | 0.90342 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | LCRA TSC_T510_T511_3 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.90676 | 0.91961 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | LCRA TSC_T510_T512_1 | 345 | Bus Low Volts | 0.92 | - | 0.91526 | 0.88209 | 0.86944 | 0.88078 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | LCRA TSC_T510_T738_1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.9102 | 0.91577 | 0.91995 | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | LCRA TSC_T510_T775 | 345 | Bus Low Volts | 0.92 | - | - | 0.91939 | 0.88929 | 0.88878 | 0.90111 | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | LCRATSC_1_HUTTO__LIMMER | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91775 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | LCRATSC_2_LIMMER_GILLCR | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91642 | 0.91851 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | LCRATSC_3_GILLCR_WHISVA | 345 | Bus Low Volts | 0.92 | - | - | - | 0.90739 | 0.90997 | 0.91776 | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | LCRATSC_4_WHISVA_HORNSB | 345 | Bus Low Volts | 0.92 | - | - | - | 0.89561 | 0.89417 | 0.90504 | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | LCRATSC_5_HORNSB_EUCLID | 345 | Bus Low Volts | 0.92 | - | - | 0.9189 | 0.88737 | 0.88731 | 0.89957 | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | LCRATSC_6_EUCLID_JOHNDU | 345 | Bus Low Volts | 0.92 | - | 0.90881 | 0.90849 | 0.86633 | 0.85795 | 0.87569 | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | LCRATSC_7_JOHNDU_ZORN__ | 345 | Bus Low Volts | 0.92 | - | - | - | 0.88744 | 0.89321 | 0.90881 | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | LIMMER SS - GILLELAND/ZORN_5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91834 | - | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | N5GSU2_B | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91711 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | P7-1_E1>>T3944Z_ERC | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91979 | - | -
TLCRA | SOUTH_CE | L_LIMMER5_1Y (7341) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | 0.93213 | 0.93148 | 0.94824 | -
TLCRA | SOUTH_CE | L_LINCOL8_1Y (7568) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88823 | - | -
TLCRA | SOUTH_CE | L_LINDEN8_1Y (7251) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9137 | - | -
TLCRA | SOUTH_CE | L_LINDEN8_1Y (7251) | L_007251L_LINDEN8_1Y-007253L_GUADAL8_1YC1 | 138 | Bus Low Volts | 0.92 | 0.77049 | 0.91431 | 0.77373 | 0.77836 | 0.76258 | 0.75429 | -
TLCRA | SOUTH_CE | L_LOCKHA8_1Y (7216) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86786 | - | -
TLCRA | SOUTH_CE | L_LULING8_1Y (7224) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88093 | - | -
TLCRA | SOUTH_CE | L_LYLEWO8_1Y (7567) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85172 | - | -
TLCRA | SOUTH_CE | L_LYLEWO8_1Y (7567) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90862 | - | -
TBBEC | SOUTH_CE | L_LYONS_8_1Y (7573) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.84169 | - | -
TBBEC | SOUTH_CE | L_LYONS_8_1Y (7573) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89344 | - | -
TLCRA | SOUTH_CE | L_MANOR_8_1Y (7330) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.83831 | - | -
TLCRA | SOUTH_CE | L_MARION5_1Y (7044) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89628 | - | -
TLCRA | SOUTH_CE | L_MARSFO8_1Y (7356) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86386 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | BAS_RANCH_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91681 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90616 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90813 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91318 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | DVCPA1C21B_1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91494 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | DVCPA1C21B_2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91919 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | G_170101FPPYD_FPP_G1UL1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91932 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | G_170126CALAVER_JKS2UL2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91761 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | G_888839BAS_RANCH_POIUC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91684 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | G_RIO_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91636 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | J5LCA1C1_B | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9163 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8282 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87572 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91398 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | L_005133ELMCREEK-005380SHAULAC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91044 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | L_005915SO_TEX__345A-008715RADIANT7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9165 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91305 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | L_007289L_SALEM_8_1Y-007564L_GUYBUR8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90081 | 0.91609 | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | LCRA TSC_T255_TAE3121_1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91601 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91924 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | N5GSU2_B | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91761 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | P7-1_E1>>T1839X1_ERC | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91955 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | P7-1_E1>>T1839X2_ERC | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91525 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | P7-1_E1>>T2764Y_ERCa | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91995 | - | -
TBBEC | SOUTH_CE | L_MAXZUE8_1Y (7565) | P7-1_E1>>T3944Z_ERC | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91456 | - | -
TLCRA | SOUTH_CE | L_MCCALA8_1Y (7182) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90987 | - | -
TLCRA | SOUTH_CE | L_MCNEIL8_1Y (7334) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85401 | - | -
TLCRA | SOUTH_CE | L_MENDOZ8_1Y (7325) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87348 | - | -
TLCRA | SOUTH_CE | L_MILLER8_1Y (7479) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91425 | - | -
TLCRA | SOUTH_CE | L_MONT__8_1Y (7249) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89714 | - | -
TLCRA | SOUTH_CE | L_MOULSO8_1Y (7237) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90729 | - | -
TLCRA | SOUTH_CE | L_MOULTO8_1Y (7236) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90889 | - | -
TLCRA | SOUTH_CE | L_NEWBRE8_1Y (7271) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8952 | - | -
TLCRA | SOUTH_CE | L_PAIGE_8_1Y (7308) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87463 | - | -
TLCRA | SOUTH_CE | L_PALEFA8_1Y (7476) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91019 | - | -
TLCRA | SOUTH_CE | L_PHJOCI8_1Y (7478) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91342 | - | -
TLCRA | SOUTH_CE | L_PILOGR8_1Y (7234) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89977 | - | -
TLCRA | SOUTH_CE | L_PINECR8_1Y (7307) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91137 | - | -
TLCRA | FAR_WEST | L_PINNAC8_1Y (7389) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.0515 | - | - | - | - | -
TLCRA | SOUTH_CE | L_PISEK_8_1Y (7296) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88027 | - | -
TLCRA | SOUTH_CE | L_PLUM__8_1Y (7274) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91525 | - | -
TLCRA | SOUTH_CE | L_POOLRO8_1Y (7222) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8897 | - | -
TLCRA | SOUTH_CE | L_RARO128_1Y (7186) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8948 | - | -
TLCRA | SOUTH_CE | L_RATTLE8_1Y (7184) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90301 | - | -
TLCRA | SOUTH_CE | L_REDROC8_1Y (7560) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86569 | - | -
TLCRA | SOUTH_CE | L_REDWOO8_1Y (7188) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89759 | - | -
TLCRA | SOUTH_CE | L_RIDGMA8_1Y (7368) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8523 | - | -
TLCRA | SOUTH_CE | L_RIVEOA8_1Y (7173) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91594 | - | -
TLCRA | SOUTH_CE | L_RIVERS8_1Y (7275) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90989 | - | -
TLCRA | SOUTH_CE | L_RIVERY8_1Y (7347) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | 0.8915 | - | 0.91667 | -
TLCRA | SOUTH_CE | L_RIVERY8_1Y (7347) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.82799 | - | -
TLCRA | SOUTH_CE | L_ROBRJR9_1Y (7194) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87892 | - | -
TLCRA | SOUTH_CE | L_ROHR__8_1Y (7515) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87216 | - | -
TLCRA | SOUTH_CE | L_ROTOTA8_1Y (7297) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87136 | - | -
TLCRA | SOUTH_CE | L_ROUNTO8_1Y (7299) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90394 | - | -
TLCRA | SOUTH_CE | L_ROUNTO8_2Y (7298) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87137 | - | -
TLCRA | SOUTH_CE | L_SALEM_5_1Y (7058) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89305 | - | -
TLCRA | SOUTH_CE | L_SALEM_8_1Y (7289) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91142 | - | -
TLCRA | SOUTH_CE | L_SALEM_8_1Y (7289) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9146 | - | -
TLCRA | SOUTH_CE | L_SALEM_8_1Y (7289) | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91936 | - | -
TLCRA | SOUTH_CE | L_SALEM_8_1Y (7289) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.83396 | - | -
TLCRA | SOUTH_CE | L_SALEM_8_1Y (7289) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8807 | - | -
TLCRA | SOUTH_CE | L_SALEM_8_1Y (7289) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91942 | - | -
TLCRA | SOUTH_CE | L_SALEM_8_1Y (7289) | L_005133ELMCREEK-005380SHAULAC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91442 | - | -
TLCRA | SOUTH_CE | L_SALEM_8_1Y (7289) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91655 | - | -
TLCRA | SOUTH_CE | L_SALEM_8_1Y (7289) | LCRA TSC_T255_TAE3121_1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91984 | - | -
TLCRA | SOUTH_CE | L_SALEM_8_1Y (7289) | P7-1_E1>>T3944Z_ERC | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9198 | - | -
TBBEC | SOUTH_CE | L_SANDHI8_1Y (7570) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9131 | - | -
TBBEC | SOUTH_CE | L_SANDHI8_1Y (7570) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91495 | - | -
TBBEC | SOUTH_CE | L_SANDHI8_1Y (7570) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.84121 | - | -
TBBEC | SOUTH_CE | L_SANDHI8_1Y (7570) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88505 | - | -
TBBEC | SOUTH_CE | L_SANDHI8_1Y (7570) | L_005133ELMCREEK-005380SHAULAC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91883 | - | -
TLCRA | SOUTH_CE | L_SANMAR8_1Y (7192) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88706 | - | -
TLCRA | SOUTH_CE | L_SCHULE8_1Y (7252) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91093 | - | -
TLCRA | SOUTH_CE | L_SETTLE8_1Y (7327) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85777 | - | -
TLCRA | SOUTH_CE | L_SETTLE8_1Y (7327) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91151 | - | -
TLCRA | SOUTH_CE | L_SETTLE8_2Y (7328) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8539 | - | -
TLCRA | SOUTH_CE | L_SETTLE8_2Y (7328) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9039 | - | -
TLCRA | SOUTH_CE | L_SHADGL8_1Y (7323) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.83889 | - | -
TLCRA | SOUTH_CE | L_SHINER8_1Y (7238) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90457 | - | -
TLCRA | SOUTH_CE | L_SIMGID8_1Y (7310) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87716 | - | -
TLCRA | SOUTH_CE | L_SMITHV8_1Y (7314) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.882 | - | -
TLCRA | SOUTH_CE | L_SPANOA8_1Y (7367) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85034 | - | -
TLCRA | SOUTH_CE | L_SPICEW8_1Y (7542) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85813 | - | -
TLCRA | SOUTH_CE | L_STEGER8_1Y (7339) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87724 | - | -
TLCRA | SOUTH_CE | L_STRAHA8_1Y (7193) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88796 | - | -
TLCRA | SOUTH_CE | L_SWEEHO8_1Y (7235) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89816 | - | -
TLCRA | SOUTH_CE | L_SWIFTE8_1Y (7326) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85602 | - | -
TLCRA | SOUTH_CE | L_TAHIVI8_1Y (7575) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87234 | - | -
TLCRA | SOUTH_CE | L_TEXIND8_1Y (7454) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91642 | - | -
TLCRA | SOUTH_CE | L_TURNER8_1Y (7500) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86249 | - | -
TLCRA | COAST | L_WALLER8_1Y (7272) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89094 | - | -
TLCRA | COAST | L_WALLER8_1Y (7272) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91456 | - | -
TLCRA | SOUTH_CE | L_WARDA_8_1Y (7312) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89606 | - | -
TLCRA | SOUTH_CE | L_WEBBER8_1Y (7329) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87105 | - | -
TLCRA | SOUTH_CE | L_WEBBER8_1Y (7329) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91266 | - | -
TLCRA | SOUTH_CE | L_WEIMAR8_1Y (7254) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91295 | - | -
TLCRA | SOUTH_CE | L_WELCOM8_1Y (7577) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85199 | - | -
TLCRA | SOUTH_CE | L_WELCOM8_1Y (7577) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89967 | - | -
TLCRA | SOUTH_CE | L_WELLBR8_1Y (7288) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85197 | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | AEN_LY-FPP¦CIS | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91991 | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | G_170126CALAVER_JKS2UL2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91896 | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | G_RIO_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91624 | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.92 | 0.90523 | 0.9119 | 0.89048 | 0.84411 | - | 0.87669 | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | J5LCA1C1_B | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91605 | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91852 | - | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91512 | - | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91983 | 0.80955 | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | L_003696HUTTOSS__5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91889 | 0.91482 | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | L_003696HUTTOSS__5-003699SALADOSS_5C2 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91889 | 0.91482 | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89268 | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | L_007041L_JOHNDU5_1Y-007047L_HORNSB5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.88958 | 0.8862 | 0.90079 | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | L_007041L_JOHNDU5_1Y-007050L_CLEASP5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91749 | - | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | L_007042L_ZORN__5_1Y-007510L_EUCLID5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91297 | 0.91556 | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | L_007047L_HORNSB5_1Y-007738L_WHISVA5_1YC1 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.89887 | 0.89724 | 0.9072 | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | LCRA TSC_T255_TAE3121_1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91461 | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | LCRA TSC_T510_1 | 345 | Bus Low Volts | 0.92 | - | - | 0.9112 | 0.90845 | 0.91525 | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | LCRA TSC_T510_T511_3 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.90275 | - | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | LCRA TSC_T510_T512_1 | 345 | Bus Low Volts | 0.92 | - | - | 0.9191 | 0.91835 | - | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | LCRA TSC_T510_T775 | 345 | Bus Low Volts | 0.92 | - | 0.90393 | 0.90666 | 0.87356 | 0.87252 | 0.8839 | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | LCRA TSC_T511_T625_2 | 345 | Bus Low Volts | 0.92 | - | - | - | 0.91723 | - | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | LCRATSC_4_WHISVA_HORNSB | 345 | Bus Low Volts | 0.92 | - | - | 0.91769 | 0.88301 | 0.88088 | 0.89089 | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | LCRATSC_5_HORNSB_EUCLID | 345 | Bus Low Volts | 0.92 | - | 0.90393 | 0.90624 | 0.87175 | 0.87099 | 0.88245 | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | LCRATSC_6_EUCLID_JOHNDU | 345 | Bus Low Volts | 0.92 | 0.91401 | 0.89302 | 0.8968 | 0.85284 | 0.84395 | 0.86084 | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | LCRATSC_7_JOHNDU_ZORN__ | 345 | Bus Low Volts | 0.92 | - | - | - | 0.88654 | 0.89948 | 0.91527 | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | LCRATSC_8_ZORN___CLEASP | 345 | Bus Low Volts | 0.92 | - | - | - | 0.9164 | - | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | N5GSU2_B | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91896 | - | -
TLCRA | SOUTH_CE | L_WHISVA5_1Y (7738) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | 0.9476 | 0.93434 | 0.93473 | 0.9476 | -
TLCRA | SOUTH_CE | L_WILLSP8_1Y (7273) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90098 | - | -
TLCRA | SOUTH_CE | L_WINCHE5_1Y (77306) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.83421 | - | -
TLCRA | SOUTH_CE | L_WINCHE5_1Y (77306) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89723 | - | -
TLCRA | SOUTH_CE | L_WINCHE8_1Y (7306) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90661 | - | -
TLCRA | WEST | L_WINGAR8_1Y (7868) | L_008005CARRIZO4A-008283ASHERTON4AC1 | 138 | Bus High Volts | 1.05 | 1.051 | - | 1.0509 | 1.0536 | 1.0521 | 1.053 | -
RLCRA | SOUTH_CE | L_WIPOPA8_1Y (7309) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91146 | - | -
RLCRA | SOUTH_CE | L_WIPOPA8_2Y (7304) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91147 | - | -
TLCRA | SOUTH_CE | L_WOLFLA8_1Y (7212) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.83928 | - | -
TLCRA | SOUTH_CE | L_WOLFLA8_1Y (7212) | L_007208L_COLTON8_1Y-007209L_ELROY_8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91402 | - | -
TLCRA | SOUTH_CE | L_WOLFLA8_1Y (7212) | L_007208L_COLTON8_1Y-007325L_MENDOZ8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9043 | - | -
TLCRA | SOUTH_CE | L_WOLFLA8_1Y (7212) | L_007209L_ELROY_8_1Y-007212L_WOLFLA8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91566 | - | -
TLCRA | SOUTH_CE | L_WOLFLA8_1Y (7212) | L_007310L_SIMGID8_1Y-007555L_BASTWE8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | - | 0.9164 | -
TLCRA | SOUTH_CE | L_WOLFLA8_1Y (7212) | L_007555L_BASTWE8_1Y-007556L_BLUEBO8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | - | 0.91593 | -
TLCRA | SOUTH_CE | L_WYLDWO8_1Y (7210) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.84478 | - | -
TLCRA | SOUTH_CE | L_WYLDWO8_1Y (7210) | L_007310L_SIMGID8_1Y-007555L_BASTWE8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | - | 0.91172 | -
TLCRA | SOUTH_CE | L_WYLDWO8_1Y (7210) | L_007555L_BASTWE8_1Y-007556L_BLUEBO8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | - | 0.90939 | -
TLCRA | SOUTH_CE | L_YARRIN8_1Y (7514) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87175 | - | -
TLCRA | SOUTH_CE | L_YOAKUM8_1Y (7242) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90487 | - | -
TLCRA | SOUTH_CE | L_ZORN__5_1Y (7042) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.86996 | - | -
TAEPTC | SOUTHERN | LA_PALMA7A (8317) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | 0.89286 | - | - | -
TAEPTC | SOUTHERN | LA_PALMA7A (8317) | E5DVA1C1_1_B | 345 | Bus Low Volts | 0.92 | - | - | - | 0.89949 | - | - | -
TAEPTC | SOUTHERN | LADKPOI7A (80509) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | 0.84697 | - | - | -
TAEPTC | SOUTHERN | LADKPOI7A (80509) | E5DVA1C1_1_B | 345 | Bus Low Volts | 0.92 | - | - | - | 0.8508 | - | - | -
TAEPTC | SOUTHERN | LADKPOI7A (80509) | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | Bus Low Volts | 0.92 | - | - | - | 0.87395 | 0.86813 | - | -
TAEN | SOUTH_CE | LAKESHORE (9228) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94415 | - | - | -
TAEN | SOUTH_CE | LAKESHORE (9228) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85618 | - | -
TAEN | SOUTH_CE | LAKEWY_LD1 (9235) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94808 | - | - | -
TAEN | SOUTH_CE | LAKEWY_LD1 (9235) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86834 | - | -
TAEN | SOUTH_CE | LAKEWY_LD2 (9236) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94808 | - | - | -
TAEN | SOUTH_CE | LAKEWY_LD2 (9236) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86834 | - | -
TONCOR | FAR_WEST | LAMESA_8 (1163) | L_001163LAMESA_8-001307KEYLYNTE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0585 | - | - | - | - | -
TONCOR | FAR_WEST | LAMESA_8 (1163) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0618 | - | - | - | - | -
TONCOR | FAR_WEST | LAMESA_8 (1163) | L_001307KEYLYNTE_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0592 | - | - | - | - | -
TONCOR | FAR_WEST | LAMESA_8 (1163) | L_001308GAILLYNT_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0593 | - | - | - | - | -
TONCOR | FAR_WEST | LAMESA_8 (1163) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | - | 1.0552 | - | - | - | - | -
TONCOR | FAR_WEST | LAMESA_8 (1163) | WILLOW VALLEY - LAMESA 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0586 | - | - | - | - | -
TONCOR | FAR_WEST | LAMESA2_8 (10008) | L_001163LAMESA_8-001307KEYLYNTE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0586 | - | - | - | - | -
TONCOR | FAR_WEST | LAMESA2_8 (10008) | L_001163LAMESA_8-010008LAMESA2_8C1 | 138 | Bus High Volts | 1.05 | 1.0557 | 1.0664 | 1.0519 | 1.0572 | 1.052 | 1.0538 | -
TONCOR | FAR_WEST | LAMESA2_8 (10008) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0618 | - | - | - | - | -
TONCOR | FAR_WEST | LAMESA2_8 (10008) | L_001307KEYLYNTE_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0592 | - | - | - | - | -
TONCOR | FAR_WEST | LAMESA2_8 (10008) | L_001308GAILLYNT_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0593 | - | - | - | - | -
TONCOR | FAR_WEST | LAMESA2_8 (10008) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | - | 1.0555 | - | - | - | - | -
TONCOR | FAR_WEST | LAMESA2_8 (10008) | WILLOW VALLEY - LAMESA 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0586 | - | - | - | - | -
TBREC | NORTH | LANHAM (775) | L_001426FISHRDSS1_8-001543HENRITAW_9C1 | 138 | Bus High Volts | 1.05 | - | 1.1049 | - | 1.072 | 1.1092 | 1.103 | -
TONCOR | NORTH | LANHAM_T9 (1452) | L_001426FISHRDSS1_8-001543HENRITAW_9C1 | 138 | Bus High Volts | 1.05 | - | 1.1049 | - | 1.0723 | 1.1095 | 1.1033 | -
TONCOR | NORTH_CE | LAVNPMP1_8 (2695) | L_002472ROYSE_N_8-002693WYLIE_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0624 | 1.0553 | - | -
TONCOR | NORTH_CE | LAVNPMP1_8 (2695) | L_002475LAVONSW_8-002693WYLIE_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0735 | 1.0663 | - | -
TONCOR | NORTH_CE | LAVNPMP2_8 (2692) | L_002472ROYSE_N_8-002693WYLIE_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0614 | 1.0543 | - | -
TONCOR | NORTH_CE | LAVNPMP2_8 (2692) | L_002475LAVONSW_8-002693WYLIE_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0724 | 1.0652 | - | -
TONCOR | NORTH_CE | LAVON1_8 (2694) | L_002472ROYSE_N_8-002693WYLIE_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0698 | 1.0626 | - | -
TONCOR | NORTH_CE | LAVON1_8 (2694) | L_002475LAVONSW_8-002693WYLIE_P8C1 | 138 | Bus High Volts | 1.05 | - | - | 1.0535 | 1.0817 | 1.0743 | 1.0515 | -
TONCOR | NORTH_CE | LAVONSW_8 (2475) | L_002472ROYSE_N_8-002693WYLIE_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0699 | 1.0627 | - | -
TONCOR | NORTH_CE | LAVONSW_8 (2475) | L_002475LAVONSW_8-002693WYLIE_P8C1 | 138 | Bus High Volts | 1.05 | - | - | 1.0536 | 1.0818 | 1.0745 | 1.0517 | -
TBREC | EAST | LAWRIDGE (10) | L_032878BRYN_GRNPRAI-032895BRYN_WBRN138C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8952 | 0.89915 | -
TONCOR | FAR_WEST | LEANCLAY_8 (11078) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88305 | - | -
TONCOR | FAR_WEST | LEANCLAY_8 (11078) | L_001086BARSTOWNW_8-011105PECONE_P8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8978 | - | -
TONCOR | FAR_WEST | LEANCLAY_8 (11078) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87714 | 0.85992 | - | -
TONCOR | FAR_WEST | LEANCLAY_8 (11078) | L_038097TNBCCASTLE1-038099TNCOTTNWD_1C1 | 138 | Bus High Volts | 1.05 | 1.0548 | - | - | - | - | - | -
RGREG | SOUTHERN | LGE4A (160205) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87968 | - | -
RGREG | SOUTHERN | LGE4A (160205) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8948 | - | -
TONCOR | NORTH_CE | LIGGETT_1T5 (1926) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89598 | - | -
TONCOR | NORTH_CE | LIGGETT_1T5 (1926) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93581 | - | -
TONCOR | NORTH_CE | LIGGETT_1T5 (1926) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89395 | - | -
TONCOR | NORTH_CE | LIGGETT_1T5 (1926) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89886 | - | -
TONCOR | NORTH_CE | LIGGETT_2T5 (1927) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89599 | - | -
TONCOR | NORTH_CE | LIGGETT_2T5 (1927) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93574 | - | -
TONCOR | NORTH_CE | LIGGETT_2T5 (1927) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89393 | - | -
TONCOR | NORTH_CE | LIGGETT_2T5 (1927) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89892 | - | -
TONCOR | NORTH_CE | LIGGETT_3T5 (1928) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89608 | - | -
TONCOR | NORTH_CE | LIGGETT_3T5 (1928) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93581 | - | -
TONCOR | NORTH_CE | LIGGETT_3T5 (1928) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89403 | - | -
TONCOR | NORTH_CE | LIGGETT_3T5 (1928) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.899 | - | -
TONCOR | NORTH_CE | LIGGETTA1_5 (1921) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89595 | - | -
TONCOR | NORTH_CE | LIGGETTA1_5 (1921) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93575 | - | -
TONCOR | NORTH_CE | LIGGETTA1_5 (1921) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89386 | - | -
TONCOR | NORTH_CE | LIGGETTA1_5 (1921) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89886 | - | -
TONCOR | NORTH_CE | LIGGETTA2_5 (1916) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89605 | - | -
TONCOR | NORTH_CE | LIGGETTA2_5 (1916) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93579 | - | -
TONCOR | NORTH_CE | LIGGETTA2_5 (1916) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89398 | - | -
TONCOR | NORTH_CE | LIGGETTA2_5 (1916) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89896 | - | -
TBREC | NORTH_CE | LILLIAN8 (419) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90211 | - | -
TONCOR | FAR_WEST | LINDRNCH_N8 (11100) | L_001094MASON_8-011083RIVERTON_8C1 | 138 | Bus High Volts | 1.05 | 1.0509 | - | 1.0504 | - | - | - | -
TAEPTN | FAR_WEST | LINTERNA4A (60383) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.0606 | - | - | - | - | - | -
RBNBLA | FAR_WEST | LMESASLR_8 (132883) | L_001163LAMESA_8-001307KEYLYNTE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0585 | - | - | - | - | -
RBNBLA | FAR_WEST | LMESASLR_8 (132883) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0618 | - | - | - | - | -
RBNBLA | FAR_WEST | LMESASLR_8 (132883) | L_001307KEYLYNTE_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0592 | - | - | - | - | -
RBNBLA | FAR_WEST | LMESASLR_8 (132883) | L_001308GAILLYNT_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0593 | - | - | - | - | -
RBNBLA | FAR_WEST | LMESASLR_8 (132883) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | - | 1.0552 | - | - | - | - | -
RBNBLA | FAR_WEST | LMESASLR_8 (132883) | WILLOW VALLEY - LAMESA 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0586 | - | - | - | - | -
TAEPTC | SOUTHERN | LMJDSW_5 (162745) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.9 | - | - | - | 0.80169 | - | - | -
TAEPTC | SOUTHERN | LMJDSW_5 (162745) | E5DVA1C1_1_B | 345 | Bus Low Volts | 0.9 | - | - | - | 0.80683 | - | - | -
TAEPTC | SOUTHERN | LMJDSW_5 (162745) | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | Bus Low Volts | 0.9 | - | - | - | 0.82973 | 0.82047 | - | -
RPSTOK | NORTH_CE | LNCRK2_1_8 (150313) | Pre-contingency | 138 | Bus High Volts | 1.05 | 1.1848 | 1.1632 | 1.183 | 1.1884 | 1.2009 | 1.1538 | -
RPSTOK | NORTH_CE | LNCRK2_2_8 (150314) | Pre-contingency | 138 | Bus High Volts | 1.05 | 1.1309 | 1.1175 | 1.1297 | 1.1329 | 1.1402 | 1.1094 | -
TONCOR | NORTH_CE | LNCST1_8 (3066) | L_002429WATMLL_8-003065REINDEER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88435 | - | -
TAEPTC | SOUTHERN | LOMAALTA (5962) | E_NEDIN_CC1_TRAIN | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89769 | - | - | -
TBREC | NORTH_CE | LONGBRANCH (280) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.92 | - | - | 0.9186 | 0.88815 | 0.85246 | 0.91635 | -
TBREC | NORTH_CE | LONGBRANCH (280) | KEMP RANCH - SARDIS 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90516 | - | -
TBREC | NORTH_CE | LONGBRANCH (280) | KEMP RANCH - SARDIS 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90516 | - | -
TBREC | NORTH_CE | LONGBRANCH (280) | KEMP RANCH - SOAP CREEK / SARDIS 138 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89906 | - | -
TBREC | NORTH_CE | LONGBRANCH (280) | L_000203SARDIS8-002309WAX_NW_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90403 | - | -
TBREC | NORTH_CE | LONGBRANCH (280) | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89454 | - | -
TBREC | NORTH_CE | LONGBRANCH (280) | L_002305AIRPRD_T8-002307MDLTHTXI1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89793 | - | -
TBREC | NORTH_CE | LONGBRANCH (280) | L_002307MDLTHTXI1_8-012307NEWBRCH_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90952 | - | -
TBREC | NORTH_CE | LONGBRANCH (280) | L_002308MDLTH_S_8-002309WAX_NW_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89794 | - | -
TBREC | NORTH_CE | LONGBRANCH (280) | L_002308MDLTH_S_8-012307NEWBRCH_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91291 | - | -
TBREC | NORTH_CE | LONGBRANCH (280) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94817 | - | -
TBREC | NORTH_CE | LONGBRANCH (280) | SOAP CREEK - CEDAR HILL / SARDIS 138 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90263 | - | -
TONCOR | EAST | LONGLAKE_8 (3280) | JEW-LONG_LAKE-PAL_S_8 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0572 | - | - | - | - | - | -
TONCOR | EAST | LONGLAKE_8 (3280) | L_003279LONGLKTA_8-003280LONGLAKE_8C1 | 138 | Bus High Volts | 1.05 | 1.0553 | - | - | - | - | - | -
TONCOR | FAR_WEST | LONGPAST_8 (11132) | L_001084ORLA_SW1_8-011080THRMIDRW_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0509 | - | - | - | - | -
TONCOR | FAR_WEST | LONGPAST_8 (11132) | L_001084ORLA_SW1_8-011132LONGPAST_8C1 | 138 | Bus High Volts | 1.05 | 1.0523 | 1.0558 | - | - | - | - | -
TONCOR | FAR_WEST | LONGSHRE_8 (10035) | L_001333MCDONALD_8-001334GLASSCNTYN_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89256 | 0.89064 | 0.88584 | 0.89134 | -
TONCOR | FAR_WEST | LONGSHRE_8 (10035) | L_001334GLASSCNTYN_8-001335FORSANTA_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89778 | 0.89558 | 0.88797 | 0.89612 | -
TONCOR | FAR_WEST | LONGSHRE_8 (10035) | L_001335FORSANTA_8-011337POLECAT1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89141 | 0.88976 | 0.88552 | 0.8907 | -
TONCOR | FAR_WEST | LONGSHRE_8 (10035) | MCDONALD RD - POLECAT 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | 0.89148 | 0.88984 | 0.88567 | 0.89076 | -
TAEPTC | SOUTHERN | LONHILL7A (8455) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91141 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | 0.88872 | - | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89992 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8996 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89402 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88386 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88801 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89598 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89684 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | GLASGOW_CON | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89695 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89402 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89684 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89562 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89859 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | L_003159ELROD_5-068091NAVARROC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89996 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88878 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88828 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89513 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.87883 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88921 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89392 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88971 | - | -
TONCOR | NORTH_CE | LOOP9_5 (2847) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | Bus Low Volts | 0.9 | - | - | - | 0.87578 | - | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89688 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89427 | - | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89687 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88578 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89015 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | DESOTO - PEBBLE CREEK 138 KV SWITCH (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89237 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89998 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | GLASGOW_CON | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89994 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | L_002217BATCHLRD_8-002466BIGONION_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89687 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | L_002217BATCHLRD_8-003159ELROD_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89998 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | L_002229PEBBLCRK_8-002328RED_OAK1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89078 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | L_002328RED_OAK1_8-002424DESSW1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88791 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89613 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89231 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89102 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89807 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.94959 | 0.94154 | 0.92472 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88228 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89234 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89784 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89268 | - | -
TONCOR | NORTH_CE | LOOP9_8 (2848) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87989 | - | - | -
TONCOR | WEST | LORAINES_8 (11342) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.84633 | - | - | - | - | -
ERCOT | SOUTH_CE | LOSTPINE5 (170174) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.82907 | - | -
TAEN | SOUTH_CE | LOSTPINES (9041) | AEN_LY-FPP:CIS-HO | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94199 | - | -
TAEN | SOUTH_CE | LOSTPINES (9041) | AEN_LY-FPP¦CIS | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93121 | - | -
TAEN | SOUTH_CE | LOSTPINES (9041) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94503 | - | -
TAEN | SOUTH_CE | LOSTPINES (9041) | G_RIO_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94895 | - | -
TAEN | SOUTH_CE | LOSTPINES (9041) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | 0.94089 | - | - | -
TAEN | SOUTH_CE | LOSTPINES (9041) | J5LCA1C1_B | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94886 | - | -
TAEN | SOUTH_CE | LOSTPINES (9041) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.82902 | - | -
TAEN | SOUTH_CE | LOSTPINES (9041) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.90483 | - | -
TAEN | SOUTH_CE | LOSTPINES (9041) | L_005133ELMCREEK-005380SHAULAC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9408 | - | -
TAEN | SOUTH_CE | LOSTPINES (9041) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94118 | - | -
TAEN | SOUTH_CE | LOSTPINES (9041) | LCRA TSC_T255_TAE3121_1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.92298 | - | -
TAEN | SOUTH_CE | LOSTPINES (9041) | P7-1_E1>>T3944Z_ERC | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94885 | - | -
TAEN | SOUTH_CE | LOSTPINES (9041) | Pre-contingency | 345 | Bus Low Volts | 0.98 | - | - | - | - | 0.97195 | - | -
TONCOR | FAR_WEST | LOTEBUSH4A (60392) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0711 | - | - | - | - | -
TAEPTC | SOUTHERN | LUCERO7A (80039) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89898 | - | -
TONCOR | SOUTH_CE | LUND_8 (3569) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88375 | - | -
ERCOT | COAST | LUNIS_CK_S1 (113111) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89585 | - | -
ERCOT | COAST | LUNIS_CK_S1 (113111) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88148 | - | -
RLOSVI | SOUTHERN | LV3_5 (160885) | G_160881LV3_UNIT1UW1 | 345 | Bus High Volts | 1.05 | - | 1.0512 | - | - | - | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | AEN_FPP-HO¦LY | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94432 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | AEN_LP-AU¦DL_2013 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93052 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | AEN_LY-FPP:CIS-HO | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94764 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | AEN_LY-FPP¦CIS | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93362 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | AEN_P1-1_GEN_SH5A+5C | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94587 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | AEN_P7 FPP-LP.DC_1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93974 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | AEN_P7 FPP-LP.DC_2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94371 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | AUSTROP - BEULAH/TORTOISE_5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94605 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | BAS_RANCH_CON | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93947 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93653 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94059 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9437 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | DVCPA1C21B_1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94012 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | DVCPA1C21B_2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94361 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | E_B_DAVIS_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94403 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | E_BASTEN_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93976 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | E_BRAUNIG_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94692 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | E_DUKE_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94926 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | E_FERGCC_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94214 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | E_GUADG_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9461 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | E_GUADG_CC2_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94614 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | E_INGLCOSW_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94669 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | E_LOSTPI_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94743 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94435 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | E_NUECES_B_CC1_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94264 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | E_WHCCS2_CC2_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94949 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | G_007044L_MARION5_1YUN1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9465 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | G_007048L_GARFIE5_1YUN1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94142 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | G_150111CPSES_UNIT1UU1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94866 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | G_150112CPSES_UNIT2UU2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94859 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | G_170073GID_GIDEONG3UN3 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94612 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | G_170101FPPYD_FPP_G1UL1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9499 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | G_170126CALAVER_JKS2UL2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93612 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | G_170671CACHENA_S1US1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94911 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | G_888839BAS_RANCH_POIUC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9395 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | G_RIO_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93429 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | 0.9254 | - | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | J5GSU4_B | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94963 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | J5LCA1C1_B | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93416 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | J5ST1_B | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94963 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94942 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94867 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.81959 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_003696HUTTOSS__5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94471 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_003696HUTTOSS__5-003699SALADOSS_5C2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94471 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.89608 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93936 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_005133ELMCREEK-005380SHAULAC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93246 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9448 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_005380SHAULA-005915SO_TEX__345AC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94472 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_005915SO_TEX__345A-008715RADIANT7AC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93718 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93061 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_007042L_ZORN__5_1Y-009074LYTTON5C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93754 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93975 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_007048L_GARFIE5_1Y-009074LYTTON5C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94986 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_009043CISTERN-009074LYTTON5C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94486 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | L_080071ZORILLO7A-080076AJO7AC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94727 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | LCRA TSC_T185_T246 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.92729 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | LCRA TSC_T185_T352 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94673 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | LCRA TSC_T227_T388 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94281 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | LCRA TSC_T255_TAE3121_1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.92811 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | LCRATSC_1_HUTTO__LIMMER | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94958 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | LCRATSC_6_EUCLID_JOHNDU | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94555 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94697 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | M10000271115801 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94446 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | M115851115803 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94727 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | MB100002711580 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94446 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | MB1158011585 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94727 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | N4P3A1C1_B_MODIFIED_BY_MZ | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94866 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | N5GSU2_B | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93612 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94548 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | P7-1_E1>>T1839X1_ERC | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94395 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | P7-1_E1>>T1839X2_ERC | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94039 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | P7-1_E1>>T2764Y_ERCa | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94398 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | P7-1_E1>>T3944Z_ERC | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9356 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | P7-1_E1>LEG-OUTLAW_ERC | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94682 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | Pre-contingency | 345 | Bus Low Volts | 0.98 | - | - | - | - | 0.95804 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | R4U2A5C1_1_B | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9466 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | SAN_PAT_CON | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94773 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | STP - HOUDINI & STP - SHAULA | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94428 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94135 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94706 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94919 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | TORTOISE - BEULAH/AUSTROP_5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9477 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94677 | - | -
TLCRA | SOUTH_CE | LYTTON5 (9074) | WAP - HOUDINI & STP - SHAULA | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.9453 | - | -
TAEN | SOUTH_CE | LYTTON8 (9075) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.87465 | - | -
TAEN | SOUTH_CE | MAGPLANT (9238) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93616 | - | - | -
TAEN | SOUTH_CE | MAGPLANT (9238) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85441 | - | -
TAEN | SOUTH_CE | MAGPLANT (9238) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94781 | - | -
TONCOR | SOUTH_CE | MALLARD_8 (3693) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87323 | - | -
TONCOR | FAR_WEST | MARNSFLD1_8 (1174) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0563 | 1.0724 | 1.0548 | 1.0577 | 1.0516 | 1.0549 | -
TONCOR | FAR_WEST | MARNSFLD1_8 (1174) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0574 | 1.0735 | 1.0558 | 1.0588 | 1.0527 | 1.056 | -
TONCOR | FAR_WEST | MARNSFLD1_8 (1174) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0683 | - | - | - | - | -
TONCOR | FAR_WEST | MARNSFLD1_8 (1174) | NORTH ANDREWS - LAMESA - MCKENZIE 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0541 | - | 1.0526 | - | 1.0503 | -
TONCOR | FAR_WEST | MARNSFLD1_T8 (1200) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0563 | 1.0724 | 1.0548 | 1.0577 | 1.0516 | 1.0549 | -
TONCOR | FAR_WEST | MARNSFLD1_T8 (1200) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0574 | 1.0735 | 1.0558 | 1.0588 | 1.0527 | 1.056 | -
TONCOR | FAR_WEST | MARNSFLD1_T8 (1200) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0683 | - | - | - | - | -
TONCOR | FAR_WEST | MARNSFLD1_T8 (1200) | NORTH ANDREWS - LAMESA - MCKENZIE 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0541 | - | 1.0526 | - | 1.0503 | -
TONCOR | FAR_WEST | MARNSFLD2_8 (1194) | L_001023MIDLNDE_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0569 | - | - | - | - | -
TONCOR | FAR_WEST | MARNSFLD2_8 (1194) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | 1.0512 | 1.0643 | - | - | - | - | -
TONCOR | FAR_WEST | MARNSFLD2_8 (1194) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0631 | - | - | - | - | -
TONCOR | FAR_WEST | MARNSFLD2_8 (1194) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0515 | 1.0641 | - | - | - | - | -
TONCOR | FAR_WEST | MARNSFLD2_8 (1194) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | 1.0558 | 1.0666 | 1.051 | 1.0541 | - | 1.0522 | -
TONCOR | FAR_WEST | MARNSFLD2_8 (1194) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0538 | 1.0655 | - | 1.0515 | - | - | -
TONCOR | FAR_WEST | MARNSFLD2_T8 (1195) | L_001023MIDLNDE_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0569 | - | - | - | - | -
TONCOR | FAR_WEST | MARNSFLD2_T8 (1195) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | 1.0512 | 1.0643 | - | - | - | - | -
TONCOR | FAR_WEST | MARNSFLD2_T8 (1195) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0631 | - | - | - | - | -
TONCOR | FAR_WEST | MARNSFLD2_T8 (1195) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0515 | 1.0641 | - | - | - | - | -
TONCOR | FAR_WEST | MARNSFLD2_T8 (1195) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | 1.0558 | 1.0666 | 1.051 | 1.0541 | - | 1.0522 | -
TONCOR | FAR_WEST | MARNSFLD2_T8 (1195) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0538 | 1.0655 | - | 1.0515 | - | - | -
TGSEC | FAR_WEST | MARTIN_8 (9486) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.84929 | 0.82909 | 0.84535 | -
TONCOR | FAR_WEST | MASON_8 (1094) | L_001094MASON_8-011083RIVERTON_8C1 | 138 | Bus High Volts | 1.05 | 1.0606 | - | 1.0597 | 1.0585 | 1.0577 | 1.0577 | -
TRAYBN | EAST | MASSYRC (6940) | JEW-LONG_LAKE-PAL_S_8 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0585 | - | - | - | - | - | -
TRAYBN | EAST | MASSYRC (6940) | L_003279LONGLKTA_8-003280LONGLAKE_8C1 | 138 | Bus High Volts | 1.05 | 1.057 | - | - | - | - | - | -
TRAYBN | EAST | MASSYRC (6940) | L_003280LONGLAKE_8-003284BETO_8C1 | 138 | Bus High Volts | 1.05 | 1.0621 | - | - | - | - | - | -
TRAYBN | EAST | MASSYRC (6940) | L_003281TENNCLNY_8-003284BETO_8C1 | 138 | Bus High Volts | 1.05 | 1.0613 | - | - | - | - | - | -
TRAYBN | EAST | MASSYRC (6940) | L_003281TENNCLNY_8-003499BLAKFTAP_8C1 | 138 | Bus High Volts | 1.05 | 1.0594 | - | - | - | - | - | -
TRAYBN | EAST | MASSYRC (6940) | L_003281TENNCLNY_8-888840SKULLCREEK_POIC1 | 138 | Bus High Volts | 1.05 | - | - | 1.0542 | 1.051 | - | 1.0525 | -
TRAYBN | EAST | MASSYRC (6940) | L_003499BLAKFTAP_8-003509BBRN_OPN_8C1 | 138 | Bus High Volts | 1.05 | 1.0557 | - | - | - | - | - | -
TRAYBN | EAST | MASSYRC (6940) | L_003509BBRN_OPN_8-003510PINOAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0576 | - | - | - | - | - | -
TRAYBN | EAST | MASSYRC (6940) | SKULLCREEK_CON | 138 | Bus High Volts | 1.05 | - | - | 1.0543 | 1.0509 | - | 1.0526 | -
TONCOR | FAR_WEST | MAVRKDRW_8 (11082) | L_001097CULBERSON_8-011082MAVRKDRW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88792 | - | - | -
TAEN | SOUTH_CE | MC1013BT (9082) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93323 | - | 0.94977 | -
TAEN | SOUTH_CE | MC1013BT (9082) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.8539 | - | -
TAEN | SOUTH_CE | MC1013BT (9082) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94637 | - | -
TAEN | SOUTH_CE | MC138_CAP (9011) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93319 | - | 0.94974 | -
TAEN | SOUTH_CE | MC138_CAP (9011) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.8539 | - | -
TAEN | SOUTH_CE | MC138_CAP (9011) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94633 | - | -
TAEPTC | SOUTHERN | MCCAMPB4A (80470) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8814 | - | -
TAEPTC | SOUTHERN | MCCAMPB4A (80470) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8934 | - | -
TAEPTC | SOUTHERN | MCCAMPB4A (80470) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90721 | - | -
TTMPA | NORTH_CE | MCCREE_5 (973) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | 0.94904 | 0.92981 | - | -
TONCOR | FAR_WEST | MCHALAM_8 (11086) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8824 | - | -
TONCOR | FAR_WEST | MCHALAM_8 (11086) | L_001086BARSTOWNW_8-011105PECONE_P8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89708 | - | -
TONCOR | FAR_WEST | MCHALAM_8 (11086) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87734 | 0.8598 | - | -
TONCOR | FAR_WEST | MCHALAM_8 (11086) | L_038097TNBCCASTLE1-038099TNCOTTNWD_1C1 | 138 | Bus High Volts | 1.05 | 1.0543 | - | - | - | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | 3WT_001302WILLOWVAL_5_001301WILLOWVAL_8_018537WILLOWVAL_3 C 3 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0509 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | 3WT_011369EXPANSE1T_5_011368EXPANSE_8_011367EXPANSE1_3 C 1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | ADD_CONSAVVY-GREY WELL DRAW | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | ANDREWS COUNTY SOUTH - NORTH ANDREWS/HOLT 138 KV SUM 2023 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | ANDREWS NORTH - BLACKBIRD/FULLERTON 138 KV EAST DCKT 2 FALL 2022 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | BUFFALO - STANTON EAST 138 KV LINE BEG - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | C5-WETT-2_A-2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | CONSAVVY - GREY WELL DRAW/MIDLAND EAST 138 KV LINE 2028 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | CULBERSON - COALSON DRAW CKT 2 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | CULBERSON - COALSON DRAW DCKT 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | EILAND - BULLDOG 138 KV LINE 2027 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | G_132881LMESASLR_G1US1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | G_132882LMESASLR_S2US2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | G_134441LAPETUS_S1US1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | G_888856HOLLY_POIUS1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | HOLLY_CON | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | HOLT - N ANDREWS B SUM 2017 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | HORSESHOE SPRINGS - RIVERTON/THREE MILE DRAW DCKT 138 KV WIN 2023 - FUTURE (DOUBLE B TO B) E | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | HORSESHOE SPRINGS - THREE MILE DRAW 138 KV WIN 2023 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001018MOSS_5-001185MIDCONW_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001023MIDLNDE_8-001116WINDWOOD_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001023MIDLNDE_8-011230ELKINS_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001023MIDLNDE_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0505 | - | - | - | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001023MIDLNDE_8-011295MIDLDWNT_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001023MIDLNDE_8-011296MIDLDWNT2_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001116WINDWOOD_8-001117MIDLANDW_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001132MIDLDWNT_8-011295MIDLDWNT_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001134LITTMAN_8-001278PHILANDS_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001134LITTMAN_8-011273NELSON_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001141HOLTSS_8-001262EMMATAP_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001153ARENATAP_8-001159NOANDREW_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001153ARENATAP_8-001173ANDHWY181_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001154BAKKETAP_8-001159NOANDREW_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001154BAKKETAP_8-001161UNPKRBK_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001154BAKKETAP_8-001280BAKKE_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001157ANDRCOSO_8-900039Other_141C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001159NOANDREW_8-001167MUSTANG_8C1 | 138 | Bus High Volts | 1.05 | 1.0501 | - | - | 1.052 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001159NOANDREW_8-001262EMMATAP_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001161UNPKRBK_8-900099Other_36C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001163LAMESA_8-001307KEYLYNTE_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001163LAMESA_8-010008LAMESA2_8C1 | 138 | Bus High Volts | 1.05 | 1.0552 | - | 1.0518 | 1.0572 | 1.0522 | 1.054 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001163LAMESA_8-132883LMESASLR_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0508 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001167MUSTANG_8-001168PAULDTAP_8C1 | 138 | Bus High Volts | 1.05 | 1.0501 | - | - | 1.0521 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001168PAULDTAP_8-900060OTHER_140C1 | 138 | Bus High Volts | 1.05 | 1.05 | - | - | 1.0521 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001169ALKALILK_8-001170PAULDTAP2_8C1 | 138 | Bus High Volts | 1.05 | 1.0554 | - | 1.0523 | 1.0579 | 1.0531 | 1.0549 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001169ALKALILK_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0554 | - | 1.0524 | 1.0579 | 1.0532 | 1.0549 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001170PAULDTAP2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | 1.0559 | - | 1.0529 | 1.0584 | 1.0537 | 1.0554 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | 1.0573 | - | 1.0525 | 1.0554 | 1.0512 | 1.0535 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0561 | - | 1.0512 | 1.0542 | - | 1.0522 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0575 | - | 1.0528 | 1.0558 | 1.0516 | 1.0539 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001173ANDHWY181_8-900039Other_141C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0616 | - | 1.0575 | 1.0609 | 1.057 | 1.0593 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.062 | - | 1.058 | 1.0613 | 1.0574 | 1.0597 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001177TEXMABEE_8-001181ANDHWY87_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0511 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001177TEXMABEE_8-011175BAIRDLAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0592 | - | 1.0577 | 1.0607 | 1.0548 | 1.058 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001178ADOBEMEW_8-011280GODDARD2_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0584 | - | 1.0569 | 1.0599 | 1.0539 | 1.0571 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0589 | - | 1.0575 | 1.0605 | 1.0544 | 1.0577 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001181ANDHWY87_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0635 | - | 1.0623 | 1.0654 | 1.0595 | 1.0628 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001183MIDCONW_8-011186HIGHSKY_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0537 | - | 1.052 | 1.0549 | - | 1.052 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001183MIDCONW_8-023862TELPHRD_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001184GODDARD_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | 1.0594 | - | 1.055 | 1.0582 | 1.0541 | 1.0565 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0582 | - | 1.0567 | 1.0597 | 1.0537 | 1.0569 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001264SANADTAP_8-001269MIDFARMS_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001264SANADTAP_8-001283XTOBLOCK9_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001269MIDFARMS_8-001282AMOMIDFM_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001272FULLERTON_8-001275NIXPOD_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001275NIXPOD_8-001278PHILANDS_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001283XTOBLOCK9_8-900099Other_36C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001284SHAFTERLK_8-011284BLACKBIRD_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.051 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001307KEYLYNTE_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0508 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001308GAILLYNT_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0508 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001326STANTON_E_8-011229STANTON_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001328QUARTZSAND_8-010029LILDEWEY_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001329SPRABERY_8-001337CRMWDTAP_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001337CRMWDTAP_8-011394PINMID_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001355BUZZDRAW_8-023829KOCHTAP_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001393DAWSON115_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | 1.0506 | - | - | 1.0528 | - | 1.0506 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_001393DAWSON115_8-900060OTHER_140C1 | 138 | Bus High Volts | 1.05 | 1.0508 | - | - | 1.053 | - | 1.0508 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_009418PATRICIA_8-009419JPAYNE_CB_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_009424FTBLOCKS_8-131453KEO_2_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_010008LAMESA2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | 1.054 | - | 1.0505 | 1.056 | 1.051 | 1.0528 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_010029LILDEWEY_8-011350WRGRN_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_010036MUSTGSPG_8-023840GLSRNCH_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_010036MUSTGSPG_8-023855TALLCTY_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011078LEANCLAY_8-038099TNCOTTNWD_1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011104BARKETT_P8-038107TNGEMSBOKM1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0585 | - | 1.0539 | 1.057 | 1.0529 | 1.0552 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011167ALKALILK2_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0562 | - | 1.0529 | 1.0589 | 1.0534 | 1.057 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011167ALKALILK2_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | 1.0548 | - | 1.0514 | 1.0572 | 1.0516 | 1.0551 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0591 | - | 1.0577 | 1.0606 | 1.0547 | 1.0579 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011189QUARRYFLD_8-900004Other_10C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011229STANTON_8-023837BUFFLO_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011278GODDARD2_8-011280GODDARD2_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011280GODDARD2_T8-011301MOCKNGBRD_T8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011294MIDLDWNT2_8-900033OTHER_133C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011296MIDLDWNT2_T8-900033OTHER_133C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011325HOWD2599_8-011331BEALSCRK_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011325HOWD2599_8-023836NATDAM_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011337POLECAT1_8-011350WRGRN_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011372MEYERSDRW_P8-011394PINMID_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_011388CONSAVVY_8-011396GREYWELL_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_023829KOCHTAP_8-023835VLMOOR_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_023855TALLCTY_8-023862TELPHRD_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_023924FARMLAND_5-888856HOLLY_POIC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_038097TNBCCASTLE1-038099TNCOTTNWD_1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_038107TNGEMSBOKM1-038109TNGMSBKACC1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_038145TNCEDRVALE1-038146TNBCTRESTL1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_038190TNLONESTAR1-038191TNBCGWRWNK1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_038294TNFOXTAIL_1-038296TNBCATOKA_1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_038340TNAIRPORT41-038341TNBCLNCIUM1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_038355TNLEONCRK_1-038356TNBCLNCRK_1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_038380TNCOYANOSA1-038382TNBCCANYON1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_888856HOLLY_POI-059900LONG_DRAWC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_900004Other_10-900007Other_137C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_900005Other_44_SO-011610ONC900005_TAPC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | L_901397ONC900020_TAP-900020Other_135C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | LAMESA - MCKENZIE DRAW 138 KV SUM 2023 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0554 | - | 1.0524 | 1.0579 | 1.0532 | 1.0549 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | 1.098 | - | 1.0959 | 1.0954 | 1.0913 | 1.0938 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MIDESSA SOUTH - MIDLAND EAST & ODESSA CKT 2 138 KV SUM 2027 - FUT (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0514 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MIDESSA SOUTH - MIDLAND EAST 138 KV SUM 2022 - FUT (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0511 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MIDLAND COUNTY NW - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0639 | - | 1.0626 | 1.0656 | 1.0598 | 1.063 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MIDLAND COUNTY NW - MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0633 | - | 1.0624 | 1.0654 | 1.0595 | 1.0627 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MIDLAND EAST - CONSAVVY 138 KV SUM 2028 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MIDLAND EAST - CONSAVVY/MIDLAND DOWNTOWN 138 KV SUM 2028 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0508 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | 1.0626 | - | 1.0584 | 1.0616 | 1.0578 | 1.0601 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0622 | - | 1.0577 | 1.0607 | 1.0573 | 1.0593 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MIDLAND EAST - MIDLAND DOWNTOWN 138 KV WIN 2023 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MIDLAND EAST - SU_BUFFALO 138 KV SUM 2018 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MOSS - HOLT 138 KV/MIDLAND COUNTY NW SW 345 KV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MOSS - HOLT/YUCCA 138 KV/MIDLAND COUNTY NW SW 345 KV (DOUBLE B TO B) SUM 2025- FUTURE | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MOSS - MIDLAND COUNTY NW 138 KV 2019 SUM - FUTURE (DOUBLE B TO B) B | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MOSS - MIDLAND COUNTY NW 138 KV CKT 2 2019 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MOSS - MIDLAND COUNTY NW CKT 2 2019 SPG - FUTURE | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | MOSS - REITER 138KV 2026 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | NATURAL DAM - CALF CREEK - BIG SPRING 138 KV SUM 2026 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | NELSON - FULLERTON 138 KV WIN 2020 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | NORTH ANDREWS - ANDREWS COUNTY SOUTH 138 KV 2023 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | NORTH ANDREWS - LAMESA - MCKENZIE 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.071 | - | 1.0674 | 1.0753 | 1.0698 | 1.0724 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | NORTH ANDREWS - MCKENZIE 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0563 | - | 1.053 | 1.0589 | 1.0535 | 1.057 | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | ODESSA - MIDESSA SOUTH CKT 2 138 KV SUM 2027 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.0556 | - | - | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | QUARRY FIELD - BLUE MOUNTAIN CKT 2 138 KV SUM 2025 - FUTURE (SINGLE B TO B)_MODIFIED_BY_MZ | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | QUARRY FIELD - BLUE MOUNTAIN DBL CKT 138 KV SUM 2025 - FUTURE (DOUBLE B TO B)_MODIFIED_BY_MZ | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | QUARTZ SAND - POLECAT CREEK 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | RANGER CAMP - BARBER LAKE SW CKT 2 138 KV SUM 2026 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | RIVERTON - DELAWARE RIVER SWITCH 138 KV DCKT LINE (DOUBLE B TO B) WIN 2025 - SUM 2030 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | RIVERTON - DELAWARE RIVER SWITCH 138 KV LINE NORTH CKT 2 (SINGLE B TO B) WIN 2025 - SUM 2030 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | RIVERTON - DELAWARE RIVER SWITCH 138 KV LINE SOUTH CKT 1 SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | RIVERTON - QUARRY FIELD CKT 3 138 KV (SINGLE B TO B) WIN 2025 - FUTURE | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | S_011386CONSAVVY1_31 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | S_011389CONSAVVY2_31 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | SALE RANCH - GLASS RANCH 138 KV LINE SUM 2027 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | SALE RANCH - NATURAL DAM 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | SAND LAKE - YUCCA DR CKT 1 138 KV SUM 2019 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | SAND LAKE - YUCCA DR DCKT 138 KV SUM 2019 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | SPRABERRY - DEWEY LAKE TAP 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | STANTON EAST - SPRABERRY 69 KV/ BUFFALO 138 KV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | TALL CITY - PECAN GROVE/GLASS RANCH 138 KV DCKT LINE (DOUBLE B TO B) 2028 SUM - FUTURE | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | VEALMOOR - BUZZARD DRAW 138 KV LINE SUM 2022 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | WILLOW VALLEY - LAMESA 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | WILLOW VALLEY TRANSFORMER 1 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0509 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | WOLF - ODESSA EHV 138 KV SUM 2027 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCKENZIEDR_8 (11169) | XFMR-RANGER_5 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | MCLLVAIN_8 (11182) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89765 | - | -
TONCOR | FAR_WEST | MCLLVAIN_8 (11182) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86312 | 0.84334 | 0.88533 | -
RSHAKE | SOUTHERN | MCLNSLR_8 (162543) | STECL_4703 | 138 | Bus High Volts | 1.05 | 1.0527 | - | - | - | - | - | -
TAEN | SOUTH_CE | MCNEIL_DB1 (9076) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93316 | - | 0.94971 | -
TAEN | SOUTH_CE | MCNEIL_DB1 (9076) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85387 | - | -
TAEN | SOUTH_CE | MCNEIL_DB1 (9076) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.9463 | - | -
TAEN | SOUTH_CE | MCNEIL_MB1 (9079) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93317 | - | 0.94974 | -
TAEN | SOUTH_CE | MCNEIL_MB1 (9079) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85392 | - | -
TAEN | SOUTH_CE | MCNEIL_MB1 (9079) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94637 | - | -
TAEN | SOUTH_CE | MCNEIL_MB3 (9077) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93331 | - | 0.94983 | -
TAEN | SOUTH_CE | MCNEIL_MB3 (9077) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85393 | - | -
TAEN | SOUTH_CE | MCNEIL_MB3 (9077) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94641 | - | -
TONCOR | NORTH_CE | MDLTH_N_8 (2313) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87597 | - | -
TONCOR | NORTH_CE | MDLTH_N_T8 (2311) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87588 | - | -
TONCOR | NORTH_CE | MDLTH_S_8 (2308) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87813 | 0.84276 | - | -
TONCOR | NORTH_CE | MDLTH_S_8 (2308) | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89752 | - | -
TONCOR | NORTH_CE | MDLTHBOX_8 (2314) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88493 | - | -
TONCOR | NORTH_CE | MDLTHELP_N5 (1940) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94443 | - | -
TONCOR | NORTH_CE | MDLTHTXI1_8 (2307) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87231 | 0.83739 | 0.89955 | -
TONCOR | NORTH_CE | MDLTHTXI1_8 (2307) | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89521 | - | -
TONCOR | NORTH_CE | MDLTHTXI2_8 (2310) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88291 | 0.85033 | - | -
TONCOR | NORTH_CE | MDLTM1_8 (12445) | L_012441PARKD_1EN8-012445MDLTM1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0533 | - | - | - | - | -
TONCOR | NORTH_CE | MDLTM2_8 (12446) | L_012442PARKD_2EN8-012446MDLTM2_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.88983 | - | - | 0.89205 | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | AEN_LP-AU¦DL_2013 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91751 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | AEN_LY-FPP:CIS-HO | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9161 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | AEN_LY-FPP¦CIS | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91132 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9097 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | ARGENTA_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88867 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | BAS_RANCH_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91202 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91045 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91211 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91635 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | CALABAZA - GILA & CALABAZA - NUECES BAY | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91893 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | DVCPA1C21B_1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90804 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | DVCPA1C21B_2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90901 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | E_B_DAVIS_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88604 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | E_BRAUNIG_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91793 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | E_CCEC_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8956 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | E_DUKE_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90986 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88509 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | E_LGE_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90458 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | E_NEDIN_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90103 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | E_NUECES_B_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8694 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | E_VICTORIA_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91197 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | E5T5A1C1_B | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91991 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | G_080039LUCERO7AUS1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91466 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | G_080039LUCERO7AUS2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91718 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | G_160101B_D_B_DAVIG1UN1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90945 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | G_160131SAN_SANMIGG1UL1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91982 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | G_160151INGLCOS_CTG1UPE | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91902 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | G_160152INGLCOS_CTG2UPE | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91902 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | G_160153INGLCOSW_STGUPE | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91816 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | G_160201LGE_LGE_GT1UPE | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91964 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | G_160392COTTON_PAP2UW1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91939 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | G_163521PEREGRN_S1US1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91599 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | G_163641CHARGER_S1US1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90881 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | G_163931OUTPOST_S1US1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91798 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | G_170126CALAVER_JKS2UL2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90685 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | G_888839BAS_RANCH_POIUC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91204 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | G_888858ARGENTA_POIUS1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91881 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | G_RIO_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91655 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | J5LCA1C1_B | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91656 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88636 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87998 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90317 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_005133ELMCREEK-005380SHAULAC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90003 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90874 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_005380SHAULA-005915SO_TEX__345AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90842 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_005607WRBRTN8-008172VICTORIA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90192 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_005725PAWNEESW5-008164COLETO7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90546 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90179 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008027CLLCOTTE4A-008452LON_HILL4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91351 | 0.87453 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008027CLLCOTTE4A-008924PORTILLA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89285 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008144SEADRFTC4A-008189TUNGSTEN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90527 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008144SEADRFTC4A-080065MELNCRK4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90518 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008162COLETO4A-008172VICTORIA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91727 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008162COLETO4A-008172VICTORIA4AC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91636 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008172VICTORIA4A-110883VIC_SU5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91985 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008249ANGSTRM7A-008956WHITEPT7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91614 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008319RIOHONDO4A-160750LV1_AB_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91906 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008437RINCON4B-080065MELNCRK4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9159 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90399 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8509 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008455LONHILL7A-008624GRISSOM7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9145 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008458B_DAVIS4A-160105B_DAVIS_1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90945 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008458B_DAVIS4A-160106B_DAVIS_2_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90783 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008458B_DAVIS4A-160107B_DAVIS_3_9C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91947 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008458B_DAVIS4A-160108B_DAVIS_4_9C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91947 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008579KATOEN7A-008606GODDARD7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87619 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008606GODDARD7A-888858ARGENTA_POIC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89606 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008624GRISSOM7A-008673RAPTOR7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91843 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_008659NAISMITH7A-080039LUCERO7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91919 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9063 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_080071ZORILLO7A-080076AJO7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90445 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_080071ZORILLO7A-080171SARITA7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91464 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_080076AJO7A-085000N_SHARPE7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91498 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_080078REFORZAR7A-084555AMBER7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91537 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_080171SARITA7A-160299BAFFIN_2_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91467 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_080259PELICAN4A-160394COTTON_1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91939 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_080260GILA4A-160095NUECES_B_2_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91843 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_080260GILA4A-160096NUECES_B_3_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91846 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_084555AMBER7A-085000N_SHARPE7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91107 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_088670BLACKPOI7A-162915BLACKJAK_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91879 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_888858ARGENTA_POI-008689TANGO7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91158 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91647 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L10011585 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91464 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | L10012100 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91985 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | LCRA TSC_T185_T246 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91815 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | LCRA TSC_T255_TAE3121_1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91003 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91898 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | M10000242128101-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91955 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | M10000244128102-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91976 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | M10000254106503-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89219 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | M10000271115801 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89924 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | M102253112251-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91571 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | M105311105321 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90456 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | M105902106102-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91941 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | M115851115803 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90445 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | M128103100534 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91317 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | M128104100523 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91421 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | M128152129153 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91673 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | MB100002412810-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91971 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | MB100002711580 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89924 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | MB1005312810 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91333 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | MB106501000025-2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89266 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | MB1101411110-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91946 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | MB1158011585 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90445 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | MB1281010052 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91436 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | MB1291012930 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90465 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | MB1291512815a | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91683 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | MBAM-REFORnew | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91036 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | N5GSU2_B | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90685 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | NEW_CTG_P7.1_5725_8689_1_2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91789 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | P7-1_E1>>T1839X1_ERC | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90929 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | P7-1_E1>>T1839X2_ERC | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90831 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | P7-1_E1>>T2764Y_ERCa | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90694 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.92761 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | R4U2A5C1_1_B | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91784 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | S_008924PORTILLA4A1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91136 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88991 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | STECL_10262 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91982 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | STP - HOUDINI & STP - SHAULA | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9072 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91901 | - | -
TAEPTC | SOUTHERN | MEDIOCR4A (8912) | WAP - HOUDINI & STP - SHAULA | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90971 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | ARGENTA_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90611 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | E_B_DAVIS_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90525 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | E_CCEC_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91685 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87382 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | E_LGE_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90865 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | E_NEDIN_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91761 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | E_NUECES_B_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89203 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90327 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89525 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91898 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | L_005133ELMCREEK-005380SHAULAC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91704 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91849 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | L_008422I_DUPSW4A-008425INGLESID4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90791 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86965 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | L_008579KATOEN7A-008606GODDARD7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89385 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | L_008606GODDARD7A-888858ARGENTA_POIC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91411 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | L_008659NAISMITH7A-080039LUCERO7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91072 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | M10000271115801 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9171 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | M105311105321 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90861 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | MB100002711580 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9171 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | MB1291012930 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8325 | 0.91232 | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | MB1293012910 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89868 | - | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94053 | - | -
TAEPTC | SOUTHERN | MELNCRK4A (80065) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87727 | - | -
TONCOR | NORTH_CE | MELSSA_P8 (2340) | L_002340MELSSA_P8-002374ANNASW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.8967 | - | - | -
TONCOR | NORTH_CE | MEXIA2_1_8 (3632) | L_003597GROESBECP_8-888888FEWELL_S1C1 | 138 | Bus Low Volts | 0.9 | - | 0.89715 | - | - | - | - | -
TONCOR | NORTH_CE | MEXIA2_1_8 (3632) | L_003632MEXIA2_1_8-003634GROES_SE1_8C1 | 138 | Bus Low Volts | 0.9 | 0.83357 | - | 0.81973 | 0.80274 | 0.83263 | 0.82267 | -
TONCOR | NORTH_CE | MEXIA2_1_8 (3632) | L_888888FEWELL_S1-003634GROES_SE1_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88784 | - | - | - | - | -
TONCOR | NORTH_CE | MG_IND_8 (2323) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87806 | - | -
TONCOR | NORTH_CE | MG_IND_8 (2323) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.9464 | - | -
TONCOR | NORTH_CE | MG_IND_8 (2323) | STERRETT-SARDIS/DESOTO 138KV DCKT (DOULBE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89909 | - | - | -
TONCOR | NORTH_CE | MG_IND_T8 (2316) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87815 | - | -
TONCOR | NORTH_CE | MG_IND_T8 (2316) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94648 | - | -
TONCOR | NORTH_CE | MG_IND_T8 (2316) | STERRETT-SARDIS/DESOTO 138KV DCKT (DOULBE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89918 | - | - | -
TONCOR | FAR_WEST | MIDLD349_8 (1172) | L_001023MIDLNDE_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0547 | - | - | - | - | -
TONCOR | FAR_WEST | MIDLD349_8 (1172) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | 1.0507 | 1.0641 | - | - | - | - | -
TONCOR | FAR_WEST | MIDLD349_8 (1172) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0626 | - | - | - | - | -
TONCOR | SOUTH_CE | MIDNIGHT_8 (3677) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87489 | - | - | -
TONCOR | SOUTH_CE | MIDNIGHT_8 (3677) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.81885 | - | -
TONCOR | SOUTH_CE | MIDNIGHT_8 (3677) | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89814 | 0.89413 | 0.89891 | -
TBREC | SOUTH_CE | MILANO (64) | L_003740SLRPRTY_8-003750VOSSLAKE_8C1 | 138 | Bus Low Volts | 0.92 | - | 0.91757 | - | - | - | - | -
TBTU | EAST | MILL_SW138 (32856) | L_032878BRYN_GRNPRAI-032895BRYN_WBRN138C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89764 | - | -
TONCOR | NORTH_CE | MILLERRD_5 (2632) | L_001907VENUS_N5-002632MILLERRD_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89185 | - | -
TONCOR | NORTH_CE | MILLERRD_5 (2632) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.87272 | - | -
TRAYBN | NORTH_CE | MLSSA_RC (6873) | L_002340MELSSA_P8-002374ANNASW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.8967 | - | - | -
TONCOR | FAR_WEST | MOCKNBRD2_8 (11300) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0668 | - | - | - | - | -
TONCOR | FAR_WEST | MOCKNGBD2_T8 (11299) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0668 | - | - | - | - | -
TAEN | SOUTH_CE | MP138_CAP (9010) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93619 | - | - | -
TAEN | SOUTH_CE | MP138_CAP (9010) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85444 | - | -
TAEN | SOUTH_CE | MP138_CAP (9010) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94784 | - | -
ERCOT | SOUTH_CE | MPP_N1 (171091) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.87316 | - | -
TONCOR | WEST | MRGNCRK_8 (1032) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.77242 | - | - | - | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89575 | - | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89653 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88266 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88663 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89907 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | GLASGOW_CON | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89882 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89989 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89653 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89907 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89918 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89986 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89288 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88769 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8983 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88748 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89306 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89325 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89201 | - | -
TONCOR | NORTH_CE | MRRFLD_RD1_5 (15204) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | Bus Low Volts | 0.9 | - | - | - | 0.88882 | - | - | -
TAEN | SOUTH_CE | MTCNTR_MB1 (9164) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.8637 | - | -
TAEN | SOUTH_CE | MTCNTR_MB2 (9167) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86367 | - | -
TAEN | SOUTH_CE | MUELLER (9342) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94302 | - | - | -
TAEN | SOUTH_CE | MUELLER (9342) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85778 | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | ANDREWS COUNTY SOUTH - NORTH ANDREWS/HOLT 138 KV SUM 2023 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0519 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_001134LITTMAN_8-001278PHILANDS_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_001134LITTMAN_8-011273NELSON_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0512 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_001159NOANDREW_8-001167MUSTANG_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0618 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0514 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0512 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_001177TEXMABEE_8-011175BAIRDLAK_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0529 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0527 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.053 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_001181ANDHWY87_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0539 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0514 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0526 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_001272FULLERTON_8-001275NIXPOD_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0508 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_001275NIXPOD_8-001278PHILANDS_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0529 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | 1.0634 | 1.0738 | 1.062 | 1.0621 | 1.0592 | 1.0602 | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | MIDLAND COUNTY NW - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0542 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | MIDLAND COUNTY NW - MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0533 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | MUSTANG_8 (1167) | NELSON - FULLERTON 138 KV WIN 2020 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0508 | - | - | - | - | -
RBROAD | SOUTH_CE | N_FORK_8 (170572) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87349 | - | -
TAEPTC | SOUTHERN | NAISMITH4A (8660) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88744 | - | -
TAEPTC | SOUTHERN | NAISMITH4A (8660) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89343 | - | -
TAEPTC | SOUTHERN | NAISMITH4A (8660) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90438 | - | -
TAEPTC | SOUTHERN | NAISMITH7A (8659) | E_INGLCOSW_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89955 | - | -
TAEPTC | SOUTHERN | NAISMITH7A (8659) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89476 | - | -
TAEPTC | SOUTHERN | NAISMITH7A (8659) | SAN_PAT_CON | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90438 | - | -
TCCEC1 | EAST | NCNTRVL (6738) | L_003358CENTVILL_8-003394JEWETTA_8C1 | 138 | Bus High Volts | 1.05 | 1.0727 | - | - | - | - | - | -
TAEPTC | SOUTHERN | NEDIN4B (88381) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
TAEPTC | SOUTHERN | NEDIN4C (88382) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
TONCOR | NORTH_CE | NEWBRCH_8 (12307) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87302 | 0.83804 | - | -
TONCOR | NORTH_CE | NEWBRCH_8 (12307) | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89546 | - | -
TONCOR | SOUTH_CE | NEWSWEDEN_8 (3710) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87724 | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | 3WT_001302WILLOWVAL_5_001301WILLOWVAL_8_018537WILLOWVAL_3 C 3 | 138 | Bus High Volts | 1.05 | - | 1.0537 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001163LAMESA_8-001307KEYLYNTE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0601 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001163LAMESA_8-010008LAMESA2_8C1 | 138 | Bus High Volts | 1.05 | 1.0548 | 1.0655 | 1.051 | 1.0563 | 1.0511 | 1.0529 | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001163LAMESA_8-011363HARDYMGN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0517 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0537 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0538 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001177TEXMABEE_8-011175BAIRDLAK_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0558 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0555 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0559 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001181ANDHWY87_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0576 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0535 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0525 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0553 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0624 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001307KEYLYNTE_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0606 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001308GAILLYNT_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0607 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_001355BUZZDRAW_8-011363HARDYMGN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0526 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_010008LAMESA2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | 1.0517 | 1.0623 | - | 1.0532 | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0521 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_011167ALKALILK2_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.052 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_011167ALKALILK2_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0558 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | LAMESA - BUZZARD DRAW 138 KV LINE 2018 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0517 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | LAMESA - BUZZARD DRAW 69/138 KV DCKT LINE 2019 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0532 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | 1.0627 | 1.0846 | 1.0614 | 1.061 | 1.0577 | 1.0603 | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | MIDLAND COUNTY NW - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.058 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | MIDLAND COUNTY NW - MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0575 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | - | 1.0543 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0532 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | NORTH ANDREWS - MCKENZIE 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0523 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | WILLOW VALLEY - LAMESA 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0602 | - | - | - | - | -
TGSEC | FAR_WEST | NLAMESA_8 (9422) | WILLOW VALLEY TRANSFORMER 1 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0537 | - | - | - | - | -
TCCEC1 | EAST | NNCNTRVL (6739) | L_003358CENTVILL_8-003394JEWETTA_8C1 | 138 | Bus High Volts | 1.05 | 1.0727 | - | - | - | - | - | -
TONCOR | NORTH_CE | NNET1_8 (2861) | L_002903ENET1_8-002909DEEPELM_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0798 | 1.1017 | 1.0945 | 1.0961 | 1.0691 | -
TONCOR | NORTH_CE | NNET1_8 (2861) | L_002906NNET1T_8-002909DEEPELM_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0734 | 1.1083 | 1.1008 | 1.1019 | 1.0754 | -
TONCOR | NORTH_CE | NNET1_8 (2861) | L_012441PARKD_1EN8-012445MDLTM1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0534 | - | - | - | - | -
TONCOR | NORTH_CE | NNET1T_8 (2906) | L_002903ENET1_8-002909DEEPELM_8C1 | 138 | Bus High Volts | 1.05 | - | 1.08 | 1.1018 | 1.0946 | 1.0962 | 1.0692 | -
TONCOR | NORTH_CE | NNET1T_8 (2906) | L_002906NNET1T_8-002909DEEPELM_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0736 | 1.1084 | 1.1009 | 1.102 | 1.0756 | -
TONCOR | NORTH_CE | NNET1T_8 (2906) | L_012441PARKD_1EN8-012445MDLTM1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0535 | - | - | - | - | -
TONCOR | FAR_WEST | NOANDREW_8 (1159) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
TAEN | SOUTH_CE | NORTHL_MB1 (9128) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.9397 | - | - | -
TAEN | SOUTH_CE | NORTHL_MB1 (9128) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85457 | - | -
TAEN | SOUTH_CE | NORTHL_MB1 (9128) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94871 | - | -
TAEN | SOUTH_CE | NORTHL_MB3 (9127) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93971 | - | - | -
TAEN | SOUTH_CE | NORTHL_MB3 (9127) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85455 | - | -
TAEN | SOUTH_CE | NORTHL_MB3 (9127) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.9487 | - | -
TAEN | SOUTH_CE | NORTHWES_MB2 (9246) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.9343 | - | - | -
TAEN | SOUTH_CE | NORTHWES_MB2 (9246) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85416 | - | -
TAEN | SOUTH_CE | NORTHWES_MB2 (9246) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94919 | - | -
TAEN | SOUTH_CE | NORTHWEST (9245) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.9343 | - | - | -
TAEN | SOUTH_CE | NORTHWEST (9245) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85417 | - | -
TAEN | SOUTH_CE | NORTHWEST (9245) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94921 | - | -
TONCOR | NORTH_CE | NORWD_1T5 (2410) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89836 | - | -
TONCOR | NORTH_CE | NORWD_1T5 (2410) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | 0.94806 | 0.9347 | - | -
TONCOR | NORTH_CE | NORWD1_5 (2406) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89866 | - | -
TONCOR | NORTH_CE | NORWD1_5 (2406) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | 0.94823 | 0.9349 | - | -
RTEXSO | NORTH | NOVA1SLR_8 (143115) | P7-WETT-3 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
RTEXS2 | NORTH | NOVA2SLR_8 (144163) | P7-WETT-3 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TAEN | SOUTH_CE | OAKHILL (9247) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85966 | - | -
TSTEC | SOUTHERN | OAKSSW8 (5713) | L_005390SOMERSET-005718ROSSVILLESB8C1 | 138 | Bus Low Volts | 0.9 | 0.87811 | - | - | - | - | - | -
TCCEC1 | EAST | OAKWOD (6711) | L_003279LONGLKTA_8-003280LONGLAKE_8C1 | 138 | Bus High Volts | 1.05 | 1.0553 | - | - | - | - | - | -
TAEN | SOUTH_CE | OH138_CAP (9012) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85969 | - | -
TCPSE | COAST | OLD_HCKRY_5 (5323) | E5DVA1C1_1_B | 345 | Bus High Volts | 1.05 | - | 1.068 | - | - | - | - | -
TCPSE | COAST | OLD_HCKRY_5 (5323) | E5DVA1C1_1_B_1 | 345 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TCPSE | COAST | OLD_HCKRY_5 (5323) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus High Volts | 1.05 | - | 1.0676 | - | - | - | - | -
TCPSE | COAST | OLD_HCKRY_5 (5323) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | NORTH | OLDLAKE_8 (11540) | L_001426FISHRDSS1_8-001543HENRITAW_9C1 | 138 | Bus High Volts | 1.05 | - | 1.105 | - | 1.0726 | 1.1097 | 1.1036 | -
TONCOR | NORTH | OLDLAKE_8 (11540) | L_001452LANHAM_T9-001544HENRIETA_9C1 | 138 | Bus High Volts | 1.05 | - | 1.0982 | - | 1.0694 | 1.1041 | 1.1005 | -
TONCOR | NORTH | OLDLAKE_8 (11540) | L_001544HENRIETA_9-011540OLDLAKE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.1106 | - | 1.0811 | 1.1208 | 1.1122 | -
TAEPTC | SOUTHERN | OLMITO4A (8950) | E_NEDIN_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | 0.918 | - | - | -
1 | FAR_WEST | ONC900005_TAP (11610) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89075 | - | -
1 | FAR_WEST | ONC900005_TAP (11610) | L_011078LEANCLAY_8-011610ONC900005_TAPC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86794 | - | - | -
1 | FAR_WEST | ONC900005_TAP (11610) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87592 | 0.87062 | - | -
1 | FAR_WEST | ONC900009_TAP (11612) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87912 | - | -
1 | FAR_WEST | ONC900009_TAP (11612) | L_001086BARSTOWNW_8-011105PECONE_P8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89276 | - | -
1 | FAR_WEST | ONC900009_TAP (11612) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88274 | 0.86221 | - | -
1 | WEST | ONC900014_TAP (1298) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.86508 | - | - | - | - | -
1 | FAR_WEST | ONC900057_TAP (901396) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.84091 | - | - | - | - | -
1 | WEST | ONC900067_TAP (11613) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.89348 | - | - | - | - | -
1 | WEST | ONC900084_TAP (1289) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.86199 | - | - | - | - | -
TAEN | SOUTH_CE | ONIONCK (9251) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.88134 | - | -
TAEPTN | FAR_WEST | ORIGIN4A (60209) | L_060209ORIGIN4A-060716SGSA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89744 | 0.89837 | - | -
TAEPTN | FAR_WEST | ORIGIN4A (60209) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.0546 | - | - | - | - | - | -
TAEPTN | FAR_WEST | ORIGIN4A (60209) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.9193 | - | - | - | -
1 | FAR_WEST | Other_102 (900021) | New Shunt 900021 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.82127 | 0.80683 | 0.81346 | -
1 | FAR_WEST | Other_102 (900021) | Pre-contingency | 138 | Bus Low Volts | 0.9 | - | - | 0.87758 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_001009YUCCADR_8-011245RIVERVIEW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89615 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_006630FTST4A-132482RIGGINS_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89967 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_006673MUSQUIZ4A-060377CREOSOTE4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89984 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_011245RIVERVIEW_8-900064Other_134C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89683 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_038069TNFLATTOP_1-038294TNFOXTAIL_1C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89966 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_060207VERH4A-060209ORIGIN4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89405 | 0.89145 | 0.89205 | - | -
1 | FAR_WEST | Other_103 (900008) | L_060207VERH4A-060808HOEFSROA4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.86971 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_060209ORIGIN4A-060716SGSA4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.88729 | 0.88141 | 0.88061 | - | -
1 | FAR_WEST | Other_103 (900008) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89456 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_060383LINTERNA4A-060385SOLSTICE4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89673 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_060383LINTERNA4A-132331REROCK_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89563 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_060385SOLSTICE4A-060393PIGCREEK4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89295 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_060385SOLSTICE4A-060716SGSA4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.85849 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_060385SOLSTICE4A-060808HOEFSROA4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.80731 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_060392LOTEBUSH4A-060415BASIN4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89901 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_060393PIGCREEK4A-134245TAYGETE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89439 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_060393PIGCREEK4A-134705TYGTEII_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.8974 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_060397GASPADTA4A-060415BASIN4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89875 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_060397GASPADTA4A-900064Other_134C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89725 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L_060716SGSA4A-060721CRYO4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89832 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | L2020971-B2 | 138 | Bus Low Volts | 0.9 | - | - | 0.899 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | S_038340TNAIRPORT411 | 138 | Bus Low Volts | 0.9 | - | - | 0.89794 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | S_038380TNCOYANOSA11 | 138 | Bus Low Volts | 0.9 | - | - | 0.89924 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | S_060721CRYO4A1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89364 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | SAND LAKE - SOLSTICE 345 KV DCKT LINE (DOUBLE B TO B) WIN 2027 - FUTURE | 138 | Bus Low Volts | 0.9 | - | - | 0.88955 | - | - | - | -
1 | FAR_WEST | Other_103 (900008) | YUCCA DRIVE - LOTEBUSH (AEP) 138 KV 2021 SUM - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | 0.899 | - | - | - | -
1 | FAR_WEST | Other_104 (900026) | L_060385SOLSTICE4A-060808HOEFSROA4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.80079 | - | - | - | -
1 | FAR_WEST | Other_105 (900108) | L_060207VERH4A-060808HOEFSROA4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.8903 | - | - | - | -
1 | FAR_WEST | Other_105 (900108) | L_060385SOLSTICE4A-060716SGSA4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.86066 | - | - | - | -
1 | FAR_WEST | Other_105 (900108) | L_060385SOLSTICE4A-060808HOEFSROA4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.84182 | - | - | - | -
1 | FAR_WEST | Other_106 (900118) | L_060207VERH4A-060808HOEFSROA4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89634 | - | - | - | -
1 | FAR_WEST | Other_106 (900118) | L_060385SOLSTICE4A-060716SGSA4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.86692 | - | - | - | -
1 | FAR_WEST | Other_106 (900118) | L_060385SOLSTICE4A-060808HOEFSROA4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.84824 | - | - | - | -
1 | WEST | Other_108 (900014) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.86507 | - | - | - | - | -
1 | WEST | Other_109 (900084) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.86199 | - | - | - | - | -
1 | FAR_WEST | Other_115 (900052) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89427 | 0.87041 | 0.87711 | -
1 | FAR_WEST | Other_115 (900052) | L_006535BIGLAKE4A-900052Other_115C1 | 138 | Bus Low Volts | 0.9 | 0.80314 | - | 0.72428 | - | - | - | -
1 | FAR_WEST | Other_115 (900052) | L_006536BIGLAKE4B-060414OWLS4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88607 | - | -
1 | FAR_WEST | Other_115 (900052) | L_006648HARGROVE4A-060374PUMPJACK4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89743 | - | -
1 | FAR_WEST | Other_115 (900052) | L_006648HARGROVE4A-076011L_TWINBU8_1YC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89254 | - | -
1 | FAR_WEST | Other_115 (900052) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86431 | 0.84369 | 0.86005 | -
1 | FAR_WEST | Other_115 (900052) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86127 | 0.83987 | 0.85651 | -
1 | FAR_WEST | Other_115 (900052) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.85639 | 0.83376 | 0.8508 | -
1 | FAR_WEST | Other_115 (900052) | L_076011L_TWINBU8_1Y-900117Other_90_SOC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89484 | 0.87715 | 0.88823 | -
1 | FAR_WEST | Other_115 (900052) | L_900110Other_86_MO-900117Other_90_SOC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89066 | - | -
1 | FAR_WEST | Other_115 (900052) | L2020944-A | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86135 | 0.84 | 0.85658 | -
1 | FAR_WEST | Other_115 (900052) | LCRA TSC_T429_T9426 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8926 | - | -
1 | FAR_WEST | Other_115 (900052) | T_006535BIGLAKE4A-006536BIGLAKE4BC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89077 | - | -
1 | WEST | Other_116 (900042) | L_001064SUN_8-001311SACROC_8C1 | 138 | Bus Low Volts | 0.9 | 0.88979 | - | 0.89752 | - | - | 0.89808 | -
1 | WEST | Other_116 (900042) | L_001304DEEPCRK_8-001305SNYDER_8C1 | 138 | Bus Low Volts | 0.9 | 0.89704 | - | - | - | - | - | -
1 | WEST | Other_116 (900042) | L_001304DEEPCRK_8-001311SACROC_8C1 | 138 | Bus Low Volts | 0.9 | 0.89436 | - | - | - | - | - | -
1 | WEST | Other_116 (900042) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.88013 | - | - | - | - | -
1 | FAR_WEST | Other_117 (900093) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88969 | 0.89519 | -
1 | FAR_WEST | Other_117 (900093) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87814 | 0.8605 | 0.87641 | -
1 | FAR_WEST | Other_117 (900093) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87506 | 0.85665 | 0.87281 | -
1 | FAR_WEST | Other_117 (900093) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86995 | 0.85031 | 0.86685 | -
1 | FAR_WEST | Other_117 (900093) | L2020944-A | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87513 | 0.85678 | 0.87288 | -
1 | FAR_WEST | Other_118 (900062) | L_006535BIGLAKE4A-900050Other_70C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.8738 | 0.85651 | 0.8593 | -
1 | FAR_WEST | Other_118 (900062) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.8969 | 0.88405 | 0.89222 | -
1 | FAR_WEST | Other_118 (900062) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89464 | 0.88133 | 0.88954 | -
1 | FAR_WEST | Other_118 (900062) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89106 | 0.87699 | 0.8853 | -
1 | FAR_WEST | Other_118 (900062) | L_076032L_NORTMC8_1Y-900113Other_81_SOC1 | 138 | Bus Low Volts | 0.9 | 0.8996 | - | 0.89365 | 0.86274 | 0.84441 | 0.85348 | -
1 | FAR_WEST | Other_118 (900062) | L_900062Other_118-900113Other_81_SOC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88723 | 0.87198 | 0.8791 | -
1 | FAR_WEST | Other_118 (900062) | L2020944-A | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89464 | 0.88137 | 0.88953 | -
1 | FAR_WEST | Other_119 (900111) | COALSON DRAW - SAND LAKE CKT 1 138 KV SUM 2024 - FUTURE (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89274 | - | - | -
1 | FAR_WEST | Other_119 (900111) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88287 | 0.89375 | - | -
1 | FAR_WEST | Other_119 (900111) | L_001086BARSTOWNW_8-011105PECONE_P8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88889 | - | - | -
1 | FAR_WEST | Other_119 (900111) | L_001097CULBERSON_8-011082MAVRKDRW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88048 | - | - | -
1 | FAR_WEST | Other_119 (900111) | L_011069TOWA_P8-011082MAVRKDRW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89918 | - | - | -
1 | FAR_WEST | Other_119 (900111) | L_011069TOWA_P8-011610ONC900005_TAPC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89822 | - | - | -
1 | FAR_WEST | Other_119 (900111) | L_011078LEANCLAY_8-011182MCLLVAIN_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89039 | - | - | -
1 | FAR_WEST | Other_119 (900111) | L_011078LEANCLAY_8-011610ONC900005_TAPC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.8465 | - | - | -
1 | FAR_WEST | Other_119 (900111) | L_011097SANDLAKE_8-011612ONC900009_TAPC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89678 | - | - | -
1 | FAR_WEST | Other_119 (900111) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.8548 | 0.87206 | - | -
1 | FAR_WEST | Other_121 (900057) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.8409 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | 3WT_010049RANGER_5_010050RANGER_8_010051RANGER1_3 C 1 | 138 | Bus Low Volts | 0.9 | - | 0.89861 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | 3WT_010049RANGER_5_010050RANGER_8_010052RANGER2_3 C 2 | 138 | Bus Low Volts | 0.9 | - | 0.89861 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | 3WT_018548PRAIRILND_5_018549PRAIRILND_8_018550PRAIRILND1_3 C 1 | 138 | Bus Low Volts | 0.9 | - | 0.89887 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | 3WT_018548PRAIRILND_5_018549PRAIRILND_8_018551PRAIRILND2_3 C 2 | 138 | Bus Low Volts | 0.9 | - | 0.89887 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | 3WT_023849VLMOOR_5_023835VLMOOR_8_023847VLMOOR_3 C 1 | 138 | Bus Low Volts | 0.9 | - | 0.89967 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | 3WT_023849VLMOOR_5_023835VLMOOR_8_023848VLMOOR2_3 C 2 | 138 | Bus Low Volts | 0.9 | - | 0.89967 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | 3WT_023875EINSTN_5_023852EINSTN_8_023874EINSTN_3 C 1 | 138 | Bus Low Volts | 0.9 | - | 0.88471 | - | - | 0.89901 | 0.89993 | -
1 | FAR_WEST | Other_131 (900100) | BITTER CREEK SW (LCRA) - CATTLEMEN SW & BITTER CREEK SW (LCRA) - SWEETWATER EAST 345 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.89889 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | CARTERVILLE - EILAND 138 KV LINE SUM 2030 - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89143 | 0.89507 | -
1 | FAR_WEST | Other_131 (900100) | CATCLAW - RINGO CKT 138 KV BEG - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.89893 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | CATTLEMAN - MORGAN CREEK SW - BITTER CREEK SW (LCRA) 345 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.89887 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | CATTLEMAN - PRAIRIE LAND 345 KV 2026 SUM - 2027 SUM (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.89986 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | CATTLMAN - LONGSHORE/PRAIRIE LAND 345 KV WIN 2027 - SUM 2027 (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.89842 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | CONSAVVY - MIDESSA SOUTH & CONSAVVY - TESORO 345 KV 2024 WIN - FUTURE (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.89992 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | CONSAVVY - PRAIRIELAND 345 KV 2024 SUMMER - FUTURE (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.89959 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | DERMOTT - BLUFF CREEK SW & DERMOTT - ENNIS CREEK 138 KV (DOUBLE B TO B) 2023 WIN - FUTURE | 138 | Bus Low Volts | 0.9 | - | 0.89989 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | DERMOTT - BLUFF CREEK SW & ENNIS CREEK - GOLDEN SW 138 KV (DOUBLE B TO B) 2023 WIN - FUTURE | 138 | Bus Low Volts | 0.9 | - | 0.89998 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | E_OECCS_CC1_TRAIN | 138 | Bus Low Volts | 0.9 | - | 0.89841 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | E_OECCS_CC2_TRAIN | 138 | Bus Low Volts | 0.9 | - | 0.89808 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | EINSTEIN - CARTERVILLE 138 KV LINE 2025 SUM - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.87381 | 0.89949 | 0.89589 | 0.88816 | 0.89183 | -
1 | FAR_WEST | Other_131 (900100) | G_131141MCDLD_FCW1UW1 | 138 | Bus Low Volts | 0.9 | - | 0.89945 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | G_131251SWEC_G1UW1 | 138 | Bus Low Volts | 0.9 | - | 0.89997 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | G_131551OWF_OWFUW1 | 138 | Bus Low Volts | 0.9 | - | 0.89952 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | IRON_BELT_CON | 138 | Bus Low Volts | 0.9 | - | 0.89901 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_000844GPL_NEVILLSW-076000L_NORTMC5_1YC1 | 138 | Bus Low Volts | 0.9 | - | 0.89953 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_000844GPL_NEVILLSW-076002L_BAKERS5_1YC1 | 138 | Bus Low Volts | 0.9 | - | 0.89972 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001058LONGSHORE_5-010053CATTLEMEN_5C1 | 138 | Bus Low Volts | 0.9 | - | 0.89967 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001058LONGSHORE_5-018548PRAIRILND_5C1 | 138 | Bus Low Volts | 0.9 | - | 0.89955 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001058LONGSHORE_5-059903BEARKATC1 | 138 | Bus Low Volts | 0.9 | - | 0.89932 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001064SUN_8-001311SACROC_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89883 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001189BARBER_LK1_8-010050RANGER_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89448 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001298ONC900014_TAP-001305SNYDER_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89958 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001304DEEPCRK_8-001305SNYDER_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89894 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001304DEEPCRK_8-001311SACROC_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89889 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001309BLUFCKTA_8-001318CHINAGRV_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89892 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001312SCURYCHV_8-011306DERMOTT_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89999 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001326STANTON_E_8-023836NATDAM_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89998 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001326STANTON_E_8-131252SWEC_1_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89997 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001328QUARTZSAND_8-010029LILDEWEY_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.86572 | 0.89698 | 0.89797 | 0.88838 | 0.89239 | -
1 | FAR_WEST | Other_131 (900100) | L_001328QUARTZSAND_8-011372MEYERSDRW_P8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89756 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001328QUARTZSAND_8-018549PRAIRILND_8C2 | 138 | Bus Low Volts | 0.9 | - | 0.89922 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001328QUARTZSAND_8-018552HOGMNTN_P8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89875 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001329SPRABERY_8-001337CRMWDTAP_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.897 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001331DRUMRIGT_8-001335FORSANTA_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.8949 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001331DRUMRIGT_8-131552OWF_1_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89416 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001333MCDONALD_8-001334GLASSCNTYN_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.84086 | 0.87801 | 0.87599 | 0.87117 | 0.87641 | -
1 | FAR_WEST | Other_131 (900100) | L_001333MCDONALD_8-011282DESERTWD2_T8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89967 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001333MCDONALD_8-131143MCDLD_1_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88308 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_001334GLASSCNTYN_8-001335FORSANTA_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.84397 | 0.88324 | 0.88094 | 0.87331 | 0.88119 | -
1 | FAR_WEST | Other_131 (900100) | L_001335FORSANTA_8-011337POLECAT1_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.83316 | 0.87681 | 0.87506 | 0.87082 | 0.87571 | -
1 | FAR_WEST | Other_131 (900100) | L_001337CRMWDTAP_8-011394PINMID_P8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89723 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010018CARTVLRNCH_8-023851CARTRVL_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.87381 | 0.89949 | 0.89589 | 0.88816 | 0.89183 | -
1 | FAR_WEST | Other_131 (900100) | L_010018CARTVLRNCH_8-023852EINSTN_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.87383 | 0.89951 | 0.89591 | 0.88818 | 0.89185 | -
1 | FAR_WEST | Other_131 (900100) | L_010022EILANDRNCH_8-023851CARTRVL_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89144 | 0.89508 | -
1 | FAR_WEST | Other_131 (900100) | L_010022EILANDRNCH_8-023853EILAND_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89143 | 0.89507 | -
1 | FAR_WEST | Other_131 (900100) | L_010029LILDEWEY_8-011350WRGRN_P8C1 | 138 | Bus Low Volts | 0.9 | - | 0.86575 | 0.89703 | 0.89803 | 0.88845 | 0.89246 | -
1 | FAR_WEST | Other_131 (900100) | L_010030LILESTILE_8-023864RCKYRD_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89955 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010030LILESTILE_8-023869ESTILE_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89955 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010032LILLUTHER_8-023831LUTHER_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.8829 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010032LILLUTHER_8-023835VLMOOR_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.8829 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010038RINGORNCH_8-023866RINGO_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89922 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010038RINGORNCH_8-023868STILES_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89915 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010041SALEM_8-023832COYOTE_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88377 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010041SALEM_8-023833BULLDOG_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88377 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010049RANGER_5-010057FLCNSEABD_SC1 | 138 | Bus Low Volts | 0.9 | - | 0.89949 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010049RANGER_5-010057PRNGMOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | 0.89949 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010049RANGER_5-011048TONKAWAW_5C1 | 138 | Bus Low Volts | 0.9 | - | 0.89711 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010050RANGER_8-011393FRONTIER_P8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89373 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010053CATTLEMEN_5-076030L_GASCCR5_1YC1 | 138 | Bus Low Volts | 0.9 | - | 0.89881 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010057PRNGMOSS_5-010062ROUGH_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89961 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010058CATCLAW_8-011218SHIPWRCK_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89974 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010058CATCLAW_8-011345SLGRLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89947 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010062ROUGH_8-010057PRNGMOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | 0.89961 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_010080REDBERRY_8-023833BULLDOG_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.85191 | - | - | 0.8942 | 0.89554 | -
1 | FAR_WEST | Other_131 (900100) | L_010080REDBERRY_8-900043Other_132C1 | 138 | Bus Low Volts | 0.9 | - | 0.85066 | - | - | 0.8935 | 0.89485 | -
1 | FAR_WEST | Other_131 (900100) | L_011028ODESEHV2_5-059901GRELTONC1 | 138 | Bus Low Volts | 0.9 | - | 0.89994 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_011325HOWD2599_8-011331BEALSCRK_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89896 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_011325HOWD2599_8-023836NATDAM_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89884 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_011337POLECAT1_8-011350WRGRN_P8C1 | 138 | Bus Low Volts | 0.9 | - | 0.86725 | 0.89944 | - | 0.89149 | 0.89543 | -
1 | FAR_WEST | Other_131 (900100) | L_011345SLGRLAKE_8-023866RINGO_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89892 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_011353BLISSARD_8-023869ESTILE_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89992 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_011372MEYERSDRW_P8-011394PINMID_P8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89735 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_018549PRAIRILND_8-018552HOGMNTN_P8C1 | 138 | Bus Low Volts | 0.9 | - | 0.8988 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_023831LUTHER_8-023832COYOTE_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88318 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_023834ELBOW_8-900043Other_132C1 | 138 | Bus Low Volts | 0.9 | - | 0.85352 | - | - | 0.8964 | 0.89768 | -
1 | FAR_WEST | Other_131 (900100) | L_023834ELBOW_8-900100Other_131C1 | 138 | Bus Low Volts | 0.9 | - | 0.85581 | - | - | 0.89917 | - | -
1 | FAR_WEST | Other_131 (900100) | L_023849VLMOOR_5-059900LONG_DRAWC1 | 138 | Bus Low Volts | 0.9 | - | 0.89314 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_023851CARTRVL_8-023853EILAND_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.87519 | - | 0.89887 | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_023864RCKYRD_8-023868STILES_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89942 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_023875EINSTN_5-059903BEARKATC1 | 138 | Bus Low Volts | 0.9 | - | 0.88471 | - | - | 0.899 | - | -
1 | FAR_WEST | Other_131 (900100) | L_059900LONG_DRAW-888842IRON_BELT_POIC1 | 138 | Bus Low Volts | 0.9 | - | 0.89912 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_059901GRELTON-059910VOLTAC1 | 138 | Bus Low Volts | 0.9 | - | 0.89997 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_059902SAND_BLUFF-059907BERNOULLIC1 | 138 | Bus Low Volts | 0.9 | - | 0.89941 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_059903BEARKAT-059907BERNOULLIC1 | 138 | Bus Low Volts | 0.9 | - | 0.8987 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_059903BEARKAT-132993BEARKAT_5C1 | 138 | Bus Low Volts | 0.9 | - | 0.89944 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_076030L_GASCCR5_1Y-076090L_DIVIDE5_1YC1 | 138 | Bus Low Volts | 0.9 | - | 0.89999 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_131753PC_SOUTH_1_5-131754PC_SOUTH_2_5C1 | 138 | Bus Low Volts | 0.9 | - | 0.89953 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_131753PC_SOUTH_1_5-131755PC2_SWYD_1_5C1 | 138 | Bus Low Volts | 0.9 | - | 0.89859 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | L_888842IRON_BELT_POI-059910VOLTAC1 | 138 | Bus Low Volts | 0.9 | - | 0.89906 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | LCRA TSC_BAKERS_CEDACA_DC | 138 | Bus Low Volts | 0.9 | - | 0.89388 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | LCRA TSC_CEDACA_NOELKE_DC_1A-1 | 138 | Bus Low Volts | 0.9 | - | 0.89559 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | LCRA TSC_CEDACA_NOELKE_DC_1A-2 | 138 | Bus Low Volts | 0.9 | - | 0.89623 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | LCRA TSC_CEDACA_NOELKE_DC_1B-1 | 138 | Bus Low Volts | 0.9 | - | 0.89559 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | LCRA TSC_CEDACA_NOELKE_DC_1B-2 | 138 | Bus Low Volts | 0.9 | - | 0.89623 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | LCRA TSC_NOELK_SNGTR_NOELK_SNGTR2 | 138 | Bus Low Volts | 0.9 | - | 0.89676 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | LCRA TSC_SCHNDR_BIGHIL_DC | 138 | Bus Low Volts | 0.9 | - | 0.89878 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | LCRA TSC_SNGTR_SCHDR_SNGTR_SCHDR2 | 138 | Bus Low Volts | 0.9 | - | 0.89721 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | LCRA TSC_T558_T559_A | 138 | Bus Low Volts | 0.9 | - | 0.89955 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | LCRA TSC_T558_T559_B | 138 | Bus Low Volts | 0.9 | - | 0.89955 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | LCRA TSC_T558_T559_C | 138 | Bus Low Volts | 0.9 | - | 0.89956 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | LONGSHORE - PRAIRIELAND SUM 2026 - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.89955 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | LUTHER - VEALMOOR 138 KV LINE 2026 SUM - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.8829 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | MB2552825529 | 138 | Bus Low Volts | 0.9 | - | 0.89989 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | MB260000260001 | 138 | Bus Low Volts | 0.9 | - | 0.89993 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | MCDONALD RD - POLECAT 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.83316 | 0.87688 | 0.87514 | 0.87097 | 0.87578 | -
1 | FAR_WEST | Other_131 (900100) | MCDONALD ROAD - SHIPWRECK & MCDONALD ROAD - PECK TAP 138 KV DCKT LINE (DOUBLE B TO B) B 2025 WIN - FUTURE (PECK TO DRIVER UPDATE) | 138 | Bus Low Volts | 0.9 | - | 0.89908 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | New Cattleman - Meinan 345kV | 138 | Bus Low Volts | 0.9 | - | 0.89894 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | New Meinan - Champion and Cattleman 345kV Double | 138 | Bus Low Volts | 0.9 | - | 0.89893 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | New Meinan - Sweeteast and BitterCreek 345kV Double | 138 | Bus Low Volts | 0.9 | - | 0.89742 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | New Sweeteast - Meinan and BitterCreek 345kV Double | 138 | Bus Low Volts | 0.9 | - | 0.89972 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | Odessa EHV-Quail & Tesoro Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | - | 0.89992 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | P1.2_Rough to Blueacres_8 | 138 | Bus Low Volts | 0.9 | - | 0.8996 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | P7.2_ROUGH_SWITCH_8_Greywell and Blueacres | 138 | Bus Low Volts | 0.9 | - | 0.89958 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | P7-WETT-7 | 138 | Bus Low Volts | 0.9 | - | 0.89986 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | PECK - CATCLAW/MCDONALD ROAD 138 KV LINE (DOUBLE B TO B) WIN 2025 - FUTURE | 138 | Bus Low Volts | 0.9 | - | 0.89944 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | PECK - MCDONALD ROAD 138 KV LINE (SINGLE B TO B) WIN 2025 - FUTURE | 138 | Bus Low Volts | 0.9 | - | 0.89949 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | PRAIRIELAND_AUTO_2 2024 SUMMER - FUTURE | 138 | Bus Low Volts | 0.9 | - | 0.89887 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | Prairieland-Quartzsand 1 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | - | 0.89875 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | Prairieland-Quartzsand Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | - | 0.89027 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | Pre-contingency | 138 | Bus Low Volts | 0.9 | 0.89032 | - | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | QUARTZ SAND - POLECAT CREEK 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.8673 | 0.89947 | - | 0.89158 | 0.89546 | -
1 | FAR_WEST | Other_131 (900100) | RANGER CAMP - FALCON SEABOARD 345 KV (SINGLE B TO B) SUM 2026 - WIN 2027_MODIFIED_BY_MZ | 138 | Bus Low Volts | 0.9 | - | 0.89949 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | - | 0.88349 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | RINGO - STILES 138 KV LINE 2025 SUM - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.89915 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | ROCKY ROAD - EAST STILES 138 KV LINE 2026 SUM - 2027 SUM (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.89955 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | S_001394TRIBUTARY_81 | 138 | Bus Low Volts | 0.9 | - | 0.89988 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | S_011169MCKENZIEDR_81 | 138 | Bus Low Volts | 0.9 | - | 0.89997 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | S_011285DESERTWD2_81 | 138 | Bus Low Volts | 0.9 | - | 0.89919 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | S_011335BUCHRNCH_81 | 138 | Bus Low Volts | 0.9 | - | 0.89959 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | SAND LAKE - SOLSTICE 345 KV DCKT LINE (DOUBLE B TO B) WIN 2027 - FUTURE | 138 | Bus Low Volts | 0.9 | - | 0.89922 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | SNYDER - SUN SW 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.89893 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | SPRABERRY - DEWEY LAKE TAP 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.89773 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | STECL_4720 | 138 | Bus Low Volts | 0.9 | - | 0.8968 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | STECL_4721-1 | 138 | Bus Low Volts | 0.9 | - | 0.89559 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | STECL_4721-2 | 138 | Bus Low Volts | 0.9 | - | 0.89623 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | TESORO - MIDESSA SOUTH/CONSAVVY 345 KV WIN 2024 - FUTURE (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.89913 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | TESORO - QUAIL/ODESSA EHV 345 KV WIN 2024 - FUTURE (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.89934 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.89942 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | WETT LONG DRAW - WETT VOLTA 345 KV LINE (SINGLE B TO B)-1 | 138 | Bus Low Volts | 0.9 | - | 0.89912 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | WETT LONG DRAW - WETT VOLTA 345 KV LINE (SINGLE B TO B)-2 | 138 | Bus Low Volts | 0.9 | - | 0.89906 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.85524 | - | - | - | - | -
1 | FAR_WEST | Other_131 (900100) | YOSEMITE - BLUE ACRES 138 KV LINE WIN 2024 - SUM 2027 (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.8996 | - | - | - | - | -
1 | FAR_WEST | Other_132 (900043) | 3WT_023875EINSTN_5_023852EINSTN_8_023874EINSTN_3 C 1 | 138 | Bus Low Volts | 0.9 | - | 0.89037 | - | - | 0.89903 | - | -
1 | FAR_WEST | Other_132 (900043) | CARTERVILLE - EILAND 138 KV LINE SUM 2030 - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89388 | 0.89759 | -
1 | FAR_WEST | Other_132 (900043) | EINSTEIN - CARTERVILLE 138 KV LINE 2025 SUM - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.88087 | - | 0.89987 | 0.89061 | 0.89439 | -
1 | FAR_WEST | Other_132 (900043) | L_001189BARBER_LK1_8-010050RANGER_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89962 | - | - | - | - | -
1 | FAR_WEST | Other_132 (900043) | L_001328QUARTZSAND_8-010029LILDEWEY_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.87363 | - | - | 0.89059 | 0.89461 | -
1 | FAR_WEST | Other_132 (900043) | L_001333MCDONALD_8-001334GLASSCNTYN_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.85052 | 0.8839 | 0.88116 | 0.87389 | 0.87981 | -
1 | FAR_WEST | Other_132 (900043) | L_001333MCDONALD_8-131143MCDLD_1_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.89048 | - | - | - | - | -
1 | FAR_WEST | Other_132 (900043) | L_001334GLASSCNTYN_8-001335FORSANTA_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.85351 | 0.88892 | 0.88591 | 0.8761 | 0.88441 | -
1 | FAR_WEST | Other_132 (900043) | L_001335FORSANTA_8-011337POLECAT1_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.8435 | 0.88327 | 0.8808 | 0.87415 | 0.87969 | -
1 | FAR_WEST | Other_132 (900043) | L_010018CARTVLRNCH_8-023851CARTRVL_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88087 | - | 0.89988 | 0.89062 | 0.89439 | -
1 | FAR_WEST | Other_132 (900043) | L_010018CARTVLRNCH_8-023852EINSTN_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88089 | - | 0.89989 | 0.89063 | 0.89441 | -
1 | FAR_WEST | Other_132 (900043) | L_010022EILANDRNCH_8-023851CARTRVL_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89389 | 0.89761 | -
1 | FAR_WEST | Other_132 (900043) | L_010022EILANDRNCH_8-023853EILAND_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89388 | 0.8976 | -
1 | FAR_WEST | Other_132 (900043) | L_010029LILDEWEY_8-011350WRGRN_P8C1 | 138 | Bus Low Volts | 0.9 | - | 0.87365 | - | - | 0.89066 | 0.89468 | -
1 | FAR_WEST | Other_132 (900043) | L_010032LILLUTHER_8-023831LUTHER_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88739 | - | - | - | - | -
1 | FAR_WEST | Other_132 (900043) | L_010032LILLUTHER_8-023835VLMOOR_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.8874 | - | - | - | - | -
1 | FAR_WEST | Other_132 (900043) | L_010041SALEM_8-023832COYOTE_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88823 | - | - | - | - | -
1 | FAR_WEST | Other_132 (900043) | L_010041SALEM_8-023833BULLDOG_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88823 | - | - | - | - | -
1 | FAR_WEST | Other_132 (900043) | L_010050RANGER_8-011393FRONTIER_P8C1 | 138 | Bus Low Volts | 0.9 | - | 0.8987 | - | - | - | - | -
1 | FAR_WEST | Other_132 (900043) | L_010080REDBERRY_8-023833BULLDOG_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.85165 | - | - | 0.89333 | 0.89468 | -
1 | FAR_WEST | Other_132 (900043) | L_010080REDBERRY_8-900043Other_132C1 | 138 | Bus Low Volts | 0.9 | - | 0.84999 | - | - | 0.8922 | 0.89355 | -
1 | FAR_WEST | Other_132 (900043) | L_011337POLECAT1_8-011350WRGRN_P8C1 | 138 | Bus Low Volts | 0.9 | - | 0.87512 | - | - | 0.89365 | 0.89759 | -
1 | FAR_WEST | Other_132 (900043) | L_023831LUTHER_8-023832COYOTE_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88766 | - | - | - | - | -
1 | FAR_WEST | Other_132 (900043) | L_023849VLMOOR_5-059900LONG_DRAWC1 | 138 | Bus Low Volts | 0.9 | - | 0.89928 | - | - | - | - | -
1 | FAR_WEST | Other_132 (900043) | L_023851CARTRVL_8-023853EILAND_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88225 | - | - | - | - | -
1 | FAR_WEST | Other_132 (900043) | L_023875EINSTN_5-059903BEARKATC1 | 138 | Bus Low Volts | 0.9 | - | 0.89037 | - | - | 0.89903 | - | -
1 | FAR_WEST | Other_132 (900043) | LCRA TSC_BAKERS_CEDACA_DC | 138 | Bus Low Volts | 0.9 | - | 0.89869 | - | - | - | - | -
1 | FAR_WEST | Other_132 (900043) | LUTHER - VEALMOOR 138 KV LINE 2026 SUM - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.88739 | - | - | - | - | -
1 | FAR_WEST | Other_132 (900043) | MCDONALD RD - POLECAT 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.84351 | 0.88336 | 0.88089 | 0.87431 | 0.87976 | -
1 | FAR_WEST | Other_132 (900043) | Prairieland-Quartzsand Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | - | 0.89672 | - | - | - | - | -
1 | FAR_WEST | Other_132 (900043) | Pre-contingency | 138 | Bus Low Volts | 0.9 | 0.8965 | - | - | - | - | - | -
1 | FAR_WEST | Other_132 (900043) | QUARTZ SAND - POLECAT CREEK 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | 0.87517 | - | - | 0.89375 | 0.89763 | -
1 | FAR_WEST | Other_132 (900043) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | - | 0.88535 | - | - | 0.89883 | - | -
1 | FAR_WEST | Other_132 (900043) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.85457 | - | - | - | - | -
1 | FAR_WEST | Other_138 (900090) | L_011242CRTNYCRK_8-060792ATHEY4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88307 | 0.85251 | 0.86897 | -
1 | FAR_WEST | Other_139 (900097) | L_011242CRTNYCRK_8-060792ATHEY4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88276 | 0.85222 | 0.86868 | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_001159NOANDREW_8-001167MUSTANG_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_001163LAMESA_8-010008LAMESA2_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_001167MUSTANG_8-001168PAULDTAP_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_001169ALKALILK_8-001170PAULDTAP2_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0508 | - | - | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_001169ALKALILK_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0508 | - | - | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_001170PAULDTAP2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0512 | - | - | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | 1.0509 | - | - | - | - | - | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.051 | - | - | - | - | - | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0541 | - | 1.0509 | 1.0535 | 1.0501 | 1.0517 | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0546 | - | 1.0513 | 1.0539 | 1.0505 | 1.0521 | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_001177TEXMABEE_8-011175BAIRDLAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0522 | - | 1.0509 | 1.0532 | - | 1.0505 | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0516 | - | 1.0503 | 1.0525 | - | - | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.052 | - | 1.0507 | 1.053 | - | 1.0502 | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_001181ANDHWY87_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0556 | - | 1.0545 | 1.0568 | 1.052 | 1.0543 | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | 1.0525 | - | - | 1.0514 | - | - | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0514 | - | 1.0501 | 1.0524 | - | - | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0518 | - | - | 1.0506 | - | - | -
TONCOR | FAR_WEST | OTHER_140 (900060) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0522 | - | 1.0509 | 1.0531 | - | 1.0504 | -
TONCOR | FAR_WEST | OTHER_140 (900060) | LAMESA - MCKENZIE DRAW 138 KV SUM 2023 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0508 | - | - | -
TONCOR | FAR_WEST | OTHER_140 (900060) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | 1.0813 | - | 1.0795 | 1.0792 | 1.0756 | 1.0774 | -
TONCOR | FAR_WEST | OTHER_140 (900060) | MIDLAND COUNTY NW - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0559 | - | 1.0547 | 1.057 | 1.0522 | 1.0544 | -
TONCOR | FAR_WEST | OTHER_140 (900060) | MIDLAND COUNTY NW - MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0554 | - | 1.0546 | 1.0568 | 1.052 | 1.0542 | -
TONCOR | FAR_WEST | OTHER_140 (900060) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | 1.055 | - | 1.0517 | 1.0542 | 1.0508 | 1.0524 | -
TONCOR | FAR_WEST | OTHER_140 (900060) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0547 | - | 1.0511 | 1.0535 | 1.0504 | 1.0518 | -
TONCOR | FAR_WEST | OTHER_140 (900060) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
1 | WEST | Other_21_SO (900067) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.89346 | - | - | - | - | -
1 | WEST | Other_26_SO (900037) | L_001064SUN_8-001311SACROC_8C1 | 138 | Bus Low Volts | 0.9 | 0.88924 | - | 0.89697 | - | - | 0.89755 | -
1 | WEST | Other_26_SO (900037) | L_001304DEEPCRK_8-001305SNYDER_8C1 | 138 | Bus Low Volts | 0.9 | 0.89649 | - | - | - | - | - | -
1 | WEST | Other_26_SO (900037) | L_001304DEEPCRK_8-001311SACROC_8C1 | 138 | Bus Low Volts | 0.9 | 0.89381 | - | - | - | - | - | -
1 | WEST | Other_26_SO (900037) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.87983 | - | - | - | - | -
1 | FAR_WEST | Other_42_SO (900032) | 3WT_011098SANDLAKE_5_011097SANDLAKE_8_011099SANDLAKE1_3 C 1 | 138 | Bus Low Volts | 0.9 | 0.89987 | - | - | - | - | - | -
1 | FAR_WEST | Other_42_SO (900032) | 3WT_011098SANDLAKE_5_011097SANDLAKE_8_011109SANDLAKE2_3 C 2 | 138 | Bus Low Volts | 0.9 | 0.89972 | - | - | - | - | - | -
1 | FAR_WEST | Other_42_SO (900032) | New Shunt 900021 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.81855 | 0.8037 | 0.81036 | -
1 | FAR_WEST | Other_42_SO (900032) | Pre-contingency | 138 | Bus Low Volts | 0.9 | - | - | 0.87558 | - | - | - | -
1 | FAR_WEST | Other_43_SO (900023) | COALSON DRAW - SAND LAKE CKT 1 138 KV SUM 2024 - FUTURE (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87558 | - | - | -
1 | FAR_WEST | Other_43_SO (900023) | HORSESHOE SPRINGS - CULBERSON DCKT 138 KV SUM 2019 - FUTURE (DOUBLE B TO B) A | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89909 | - | - | -
1 | FAR_WEST | Other_43_SO (900023) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86544 | - | - | -
1 | FAR_WEST | Other_43_SO (900023) | L_001086BARSTOWNW_8-011105PECONE_P8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87163 | - | - | -
1 | FAR_WEST | Other_43_SO (900023) | L_001097CULBERSON_8-011082MAVRKDRW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86297 | - | - | -
1 | FAR_WEST | Other_43_SO (900023) | L_001097CULBERSON_8-011114ATLRESRC_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89987 | - | - | -
1 | FAR_WEST | Other_43_SO (900023) | L_011069TOWA_P8-011082MAVRKDRW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.8822 | - | - | -
1 | FAR_WEST | Other_43_SO (900023) | L_011069TOWA_P8-011610ONC900005_TAPC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88122 | - | - | -
1 | FAR_WEST | Other_43_SO (900023) | L_011078LEANCLAY_8-011182MCLLVAIN_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87317 | - | - | -
1 | FAR_WEST | Other_43_SO (900023) | L_011078LEANCLAY_8-011610ONC900005_TAPC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.899 | 0.82795 | - | - | -
1 | FAR_WEST | Other_43_SO (900023) | L_011086MCHALAM_8-011612ONC900009_TAPC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.8943 | - | - | -
1 | FAR_WEST | Other_43_SO (900023) | L_011097SANDLAKE_8-011612ONC900009_TAPC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87974 | - | - | -
1 | FAR_WEST | Other_43_SO (900023) | L_011105PECONE_P8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89952 | - | - | -
1 | FAR_WEST | Other_43_SO (900023) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89606 | 0.83652 | 0.8863 | - | -
1 | FAR_WEST | Other_43_SO (900023) | New Shunt 900012 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89673 | - | -
1 | FAR_WEST | Other_43_SO (900023) | S_038099TNCOTTNWD_11 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88765 | - | - | -
1 | FAR_WEST | Other_44_SO (900005) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89975 | 0.89021 | - | -
1 | FAR_WEST | Other_44_SO (900005) | L_001097CULBERSON_8-011082MAVRKDRW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89743 | - | - | -
1 | FAR_WEST | Other_44_SO (900005) | L_011078LEANCLAY_8-011610ONC900005_TAPC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86453 | - | - | -
1 | FAR_WEST | Other_44_SO (900005) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87256 | 0.86985 | - | -
1 | FAR_WEST | Other_45_SO (900009) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87479 | - | -
1 | FAR_WEST | Other_45_SO (900009) | L_001086BARSTOWNW_8-011105PECONE_P8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8885 | - | -
1 | FAR_WEST | Other_45_SO (900009) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87897 | 0.85779 | - | -
1 | FAR_WEST | Other_46_SO (900012) | COALSON DRAW - SAND LAKE CKT 1 138 KV SUM 2024 - FUTURE (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86545 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | COALSON DRAW - SAND LAKE CKT 2 138 KV WIN 2025- FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89251 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | HORSESHOE SPRINGS - CULBERSON DCKT 138 KV SUM 2019 - FUTURE (DOUBLE B TO B) A | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88928 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.85516 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | L_001086BARSTOWNW_8-011105PECONE_P8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86144 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | L_001097CULBERSON_8-011082MAVRKDRW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.85267 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | L_001097CULBERSON_8-011114ATLRESRC_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89006 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | L_011069TOWA_P8-011082MAVRKDRW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87216 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | L_011069TOWA_P8-011610ONC900005_TAPC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87116 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | L_011078LEANCLAY_8-011086MCHALAM_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89057 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | L_011078LEANCLAY_8-011182MCLLVAIN_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89978 | 0.86301 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | L_011078LEANCLAY_8-011610ONC900005_TAPC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89144 | 0.81712 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | L_011086MCHALAM_8-011612ONC900009_TAPC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88442 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | L_011097SANDLAKE_8-011612ONC900009_TAPC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86966 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | L_011105PECONE_P8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88971 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.88846 | 0.82582 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | L_038097TNBCCASTLE1-038099TNCOTTNWD_1C1 | 138 | Bus High Volts | 1.1 | - | - | - | - | 1.1152 | 1.105 | -
1 | FAR_WEST | Other_46_SO (900012) | New Shunt 900012 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88541 | 0.89913 | -
1 | FAR_WEST | Other_46_SO (900012) | RIVERTON - THREE MILE DRAW/HORSESHOE SPRINGS DCKT 138 KV SUM 2022 - FUTURE (DOUBLE B TO B) C | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89402 | - | - | -
1 | FAR_WEST | Other_46_SO (900012) | S_038099TNCOTTNWD_11 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87768 | - | - | -
1 | FAR_WEST | Other_47_SO (900038) | New Shunt 900021 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.83055 | 0.81725 | 0.82378 | -
1 | FAR_WEST | Other_47_SO (900038) | Pre-contingency | 138 | Bus Low Volts | 0.9 | - | - | 0.88426 | - | - | - | -
1 | FAR_WEST | Other_61 (900055) | L_011242CRTNYCRK_8-060792ATHEY4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88314 | 0.85257 | 0.86904 | -
1 | FAR_WEST | Other_70 (900050) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88742 | 0.89101 | -
1 | FAR_WEST | Other_70 (900050) | L_006535BIGLAKE4A-900050Other_70C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89041 | 0.85587 | 0.83697 | 0.83983 | -
1 | FAR_WEST | Other_70 (900050) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87972 | 0.86392 | 0.87568 | -
1 | FAR_WEST | Other_70 (900050) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.8771 | 0.86072 | 0.87258 | -
1 | FAR_WEST | Other_70 (900050) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87284 | 0.8555 | 0.86757 | -
1 | FAR_WEST | Other_70 (900050) | L_076032L_NORTMC8_1Y-900113Other_81_SOC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88185 | 0.86541 | 0.87421 | -
1 | FAR_WEST | Other_70 (900050) | L_900062Other_118-900113Other_81_SOC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88641 | 0.8934 | -
1 | FAR_WEST | Other_70 (900050) | L2020944-A | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87713 | 0.8608 | 0.87261 | -
1 | FAR_WEST | Other_71_MO (900096) | Pre-contingency | 138 | Bus Low Volts | 0.9 | 0.89097 | 0.86848 | 0.86565 | 0.87303 | 0.86945 | 0.87407 | -
1 | FAR_WEST | Other_81_SO (900113) | L_006535BIGLAKE4A-900050Other_70C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89732 | 0.89994 | -
1 | FAR_WEST | Other_81_SO (900113) | L_076032L_NORTMC8_1Y-900113Other_81_SOC1 | 138 | Bus Low Volts | 0.9 | 0.89551 | - | 0.88888 | 0.85723 | 0.83842 | 0.84756 | -
1 | FAR_WEST | Other_82_SO (900116) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89827 | 0.89999 | -
1 | FAR_WEST | Other_82_SO (900116) | L_006535BIGLAKE4A-900050Other_70C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86916 | 0.85143 | 0.85424 | -
1 | FAR_WEST | Other_82_SO (900116) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89239 | 0.87914 | 0.88736 | -
1 | FAR_WEST | Other_82_SO (900116) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89011 | 0.8764 | 0.88466 | -
1 | FAR_WEST | Other_82_SO (900116) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88651 | 0.87203 | 0.8804 | -
1 | FAR_WEST | Other_82_SO (900116) | L_076032L_NORTMC8_1Y-900113Other_81_SOC1 | 138 | Bus Low Volts | 0.9 | 0.89609 | - | 0.8896 | 0.85804 | 0.83926 | 0.84839 | -
1 | FAR_WEST | Other_82_SO (900116) | L_900062Other_118-900113Other_81_SOC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88267 | 0.86699 | 0.87416 | -
1 | FAR_WEST | Other_82_SO (900116) | L2020944-A | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89012 | 0.87645 | 0.88465 | -
1 | FAR_WEST | Other_84_MO (900034) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89041 | 0.8959 | -
1 | FAR_WEST | Other_84_MO (900034) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87883 | 0.86125 | 0.87714 | -
1 | FAR_WEST | Other_84_MO (900034) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87574 | 0.8574 | 0.87354 | -
1 | FAR_WEST | Other_84_MO (900034) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87064 | 0.85106 | 0.86759 | -
1 | FAR_WEST | Other_84_MO (900034) | L2020944-A | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87582 | 0.85752 | 0.87361 | -
1 | FAR_WEST | Other_85_MO (900040) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89335 | - | -
1 | FAR_WEST | Other_85_MO (900040) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88631 | 0.86788 | 0.88391 | -
1 | FAR_WEST | Other_85_MO (900040) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88335 | 0.86417 | 0.88048 | -
1 | FAR_WEST | Other_85_MO (900040) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87863 | 0.85828 | 0.87498 | -
1 | FAR_WEST | Other_85_MO (900040) | L2020944-A | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88342 | 0.86429 | 0.88054 | -
1 | WEST | Other_86_MO (900110) | L_006517RUSSEKST4A-006535BIGLAKE4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89411 | - | -
1 | WEST | Other_86_MO (900110) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88975 | 0.86566 | 0.87384 | -
1 | WEST | Other_86_MO (900110) | L_006535BIGLAKE4A-900052Other_115C1 | 138 | Bus Low Volts | 0.9 | 0.82731 | - | 0.75541 | - | - | - | -
1 | WEST | Other_86_MO (900110) | L_006536BIGLAKE4B-060414OWLS4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89878 | 0.87841 | - | -
1 | WEST | Other_86_MO (900110) | L_006559JERRY4A-060374PUMPJACK4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89024 | - | -
1 | WEST | Other_86_MO (900110) | L_006562FDRAN4A-136103BLUESKY_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89998 | - | -
1 | WEST | Other_86_MO (900110) | L_006648HARGROVE4A-060374PUMPJACK4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.8969 | 0.87866 | 0.89492 | -
1 | WEST | Other_86_MO (900110) | L_006648HARGROVE4A-076011L_TWINBU8_1YC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89248 | 0.87354 | 0.89097 | -
1 | WEST | Other_86_MO (900110) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86655 | 0.84399 | 0.86019 | -
1 | WEST | Other_86_MO (900110) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86374 | 0.84042 | 0.85693 | -
1 | WEST | Other_86_MO (900110) | L_060723CROSSOVE4A-060728PALOUSE4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89367 | - | -
1 | WEST | Other_86_MO (900110) | L_060723CROSSOVE4A-076032L_NORTMC8_1YC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89358 | - | -
1 | WEST | Other_86_MO (900110) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.85945 | 0.83499 | 0.8519 | -
1 | WEST | Other_86_MO (900110) | L_076011L_TWINBU8_1Y-900117Other_90_SOC1 | 138 | Bus Low Volts | 0.9 | 0.88837 | - | 0.88141 | 0.85631 | 0.83415 | 0.84601 | -
1 | WEST | Other_86_MO (900110) | L_076032L_NORTMC8_1Y-900113Other_81_SOC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89702 | - | -
1 | WEST | Other_86_MO (900110) | L_900110Other_86_MO-900117Other_90_SOC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89825 | 0.87574 | 0.85608 | 0.86608 | -
1 | WEST | Other_86_MO (900110) | L2020925 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8935 | - | -
1 | WEST | Other_86_MO (900110) | L2020944-A | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86382 | 0.84055 | 0.857 | -
1 | WEST | Other_86_MO (900110) | L2020944-B | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89367 | - | -
1 | WEST | Other_86_MO (900110) | LCRA TSC_T429_T9426 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89202 | 0.8731 | 0.89031 | -
1 | WEST | Other_86_MO (900110) | T_006535BIGLAKE4A-006536BIGLAKE4BC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88272 | - | -
1 | WEST | Other_90_SO (900117) | L_006535BIGLAKE4A-900052Other_115C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.85555 | - | - | - | -
1 | WEST | Other_90_SO (900117) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8967 | - | -
1 | WEST | Other_90_SO (900117) | L_076011L_TWINBU8_1Y-900117Other_90_SOC1 | 138 | Bus Low Volts | 0.9 | 0.88192 | - | 0.87422 | 0.84861 | 0.82597 | 0.83799 | -
1 | WEST | Other_91_MO (900103) | L_006535BIGLAKE4A-900052Other_115C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.85544 | - | - | - | -
1 | WEST | Other_91_MO (900103) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8966 | - | -
1 | WEST | Other_91_MO (900103) | L_076011L_TWINBU8_1Y-900117Other_90_SOC1 | 138 | Bus Low Volts | 0.9 | 0.88182 | - | 0.87411 | 0.8485 | 0.82585 | 0.83786 | -
TONCOR | NORTH_CE | OUTERLOOP_8 (12351) | L_000675ROCKHILL-002380WESTRIDGE1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | NORTH_CE | OUTERLOOP_8 (12351) | L_002350CELINASE1_8-002366WILSNCRK_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
TONCOR | NORTH_CE | OUTERLOOP_8 (12351) | L_002370COLLINSS1_8-002380WESTRIDGE1_8C1 | 138 | Bus Low Volts | 0.9 | 0.8908 | - | 0.88393 | 0.87863 | 0.87868 | 0.87941 | -
TONCOR | FAR_WEST | OWLHILLS2_8 (11267) | L_011141BRECK_8-011269OWLHILLS2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0552 | - | - | - | - | - | -
TONCOR | FAR_WEST | OWLHILLS2_8 (11267) | L_011180ARYOBLUFF_T8-011199RDRUNNER_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.86506 | - | -
TONCOR | FAR_WEST | OWLHILLS2_8 (11267) | L_011183TUNSTLL_8-011199RDRUNNER_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.83644 | - | -
TONCOR | FAR_WEST | OWLHILLS2_T8 (11269) | L_011141BRECK_8-011269OWLHILLS2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0552 | - | - | - | - | - | -
TONCOR | FAR_WEST | OWLHILLS2_T8 (11269) | L_011180ARYOBLUFF_T8-011199RDRUNNER_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.86506 | - | -
TONCOR | FAR_WEST | OWLHILLS2_T8 (11269) | L_011183TUNSTLL_8-011199RDRUNNER_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.83644 | - | -
TAEPTN | FAR_WEST | OWLS4A (60414) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.9183 | 0.85978 | 0.84326 | 0.85847 | -
TAEPTN | FAR_WEST | OWLS4A (60414) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91651 | 0.8568 | 0.83947 | 0.85509 | -
TAEPTN | FAR_WEST | OWLS4A (60414) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.9123 | 0.85198 | 0.83211 | 0.84828 | -
TAEPTN | FAR_WEST | OWLS4A (60414) | L2020944-A | 138 | Bus Low Volts | 0.92 | - | - | 0.9166 | 0.85687 | 0.83959 | 0.85515 | -
TAEPTC | SOUTHERN | OXY_INGL4A (8818) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87133 | - | -
TAEPTC | SOUTHERN | OXY_INGL4A (8818) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89459 | - | -
TAEPTC | SOUTHERN | OXY_INGL4A (8818) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90802 | - | -
TAEPTC | SOUTHERN | OXY_INGL4B (8820) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87129 | - | -
TAEPTC | SOUTHERN | OXY_INGL4B (8820) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89526 | - | -
TAEPTC | SOUTHERN | OXY_INGL4B (8820) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90868 | - | -
TPDEC0 | SOUTH_CE | P_ANDICE8_1_ (70522) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87276 | - | -
TPDEC0 | SOUTH_CE | P_BALCON8_1_ (70533) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85555 | - | -
TPDEC0 | SOUTH_CE | P_BERTRA8_1_ (70520) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88922 | - | -
TPDEC0 | SOUTH_CE | P_BLANCO8_1_ (70482) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91992 | - | -
TPDEC0 | SOUTH_CE | P_BLOCKH8_1_ (70527) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8541 | - | -
TPDEC0 | SOUTH_CE | P_BUDA__8_1_ (70498) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86361 | - | -
TPDEC0 | SOUTH_CE | P_BULLHO8_1_ (70535) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85953 | - | -
TPDEC0 | SOUTH_CE | P_BUTTER8_1_ (70531) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85436 | - | -
TPDEC0 | SOUTH_CE | P_CANYHY8_1_ (70487) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89485 | - | -
TPDEC0 | SOUTH_CE | P_CEBOCR8_1_ (70511) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87289 | - | -
TPDEC0 | SOUTH_CE | P_CEDAVA8_1_ (70506) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85611 | - | -
TPDEC0 | SOUTH_CE | P_CRANMI8_1_ (70490) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90266 | - | -
TPDEC0 | WEST | P_DCPROC8_1_ (70194) | L_008261WHITING4A-008991DLNCRK4AC1 | 138 | Bus High Volts | 1.05 | 1.0641 | - | 1.0586 | 1.0606 | 1.0579 | 1.0602 | -
TPDEC0 | SOUTH_CE | P_DEVIHI8_1_ (70493) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.915 | - | -
TPDEC0 | SOUTH_CE | P_DRIPSP8_1_ (70512) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87879 | - | -
TPDEC0 | SOUTH_CE | P_FISCHE8_1_ (70492) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88919 | - | -
TPDEC0 | SOUTH_CE | P_FRIEND8_1_ (70507) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86032 | - | -
TPDEC0 | SOUTH_CE | P_HENLY_8_1_ (70513) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89007 | - | -
TPDEC0 | SOUTH_CE | P_HEROWA8_1_ (70536) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85476 | - | -
TPDEC0 | SOUTH_CE | P_HIGH328_1_ (70546) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88542 | - | -
TPDEC0 | SOUTH_CE | P_HUNTER8_1_ (70491) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91005 | - | -
TPDEC0 | SOUTH_CE | P_KYLE__8_1_ (70502) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87507 | - | -
TPDEC0 | SOUTH_CE | P_LAGOVI8_1_ (70352) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86417 | - | -
TPDEC0 | SOUTH_CE | P_LEANDE8_1_ (70525) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85436 | - | -
TPDEC0 | SOUTH_CE | P_LEHIGH8_1_ (70198) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86716 | - | -
TPDEC0 | SOUTH_CE | P_MANCHA8_1_ (70504) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85987 | - | -
TPDEC0 | SOUTH_CE | P_NAMELE8_1_ (70526) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85723 | - | -
TPDEC0 | SOUTH_CE | P_PALEPE8_1_ (70477) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90592 | - | -
TPDEC0 | SOUTH_CE | P_PIPELI8_1_ (70390) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8637 | - | -
TPDEC0 | SOUTH_CE | P_PURGRO8_1_ (70489) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9007 | - | -
TPDEC0 | SOUTH_CE | P_RUTHER8_1_ (70509) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86414 | - | -
TPDEC0 | SOUTH_CE | P_SATTLE8_1_ (70488) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89765 | - | -
TPDEC0 | SOUTH_CE | P_SEWAJU8_1_ (70524) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86005 | - | -
TPDEC0 | SOUTH_CE | P_TRADPO8_1_ (70505) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85354 | - | -
TPDEC0 | SOUTH_CE | P_WHITES8_1_ (70529) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85365 | - | -
TPDEC0 | SOUTH_CE | P_WIMBER8_1_ (70496) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88158 | - | -
TONCOR | NORTH_CE | PADERA_8 (2286) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87255 | - | -
TAEPTN | NORTH | PADU4A (6135) | L_006048PAUL2A-006051QUAN2AC1 | 138 | Bus Low Volts | 0.92 | 0.87313 | - | 0.87633 | 0.87347 | 0.86986 | 0.87277 | -
TAEPTN | NORTH | PADU4A (6135) | L_006117EASTMUND4B-006320TARDIS4AC1 | 138 | Bus Low Volts | 0.92 | 0.90438 | - | 0.9102 | 0.90707 | 0.90807 | 0.9155 | -
TAEPTN | NORTH | PADU4A (6135) | L_006135PADU4A-006320TARDIS4AC1 | 138 | Bus Low Volts | 0.92 | 0.87464 | 0.9065 | 0.87621 | 0.87978 | 0.87519 | 0.87494 | -
TAEPTN | NORTH | PADU4A (6135) | MB2002820034 | 138 | Bus Low Volts | 0.92 | 0.87317 | - | 0.87483 | 0.87351 | 0.86981 | 0.87278 | -
TAEPTN | NORTH | PADU4A (6135) | T_006048PAUL2A-006050LKPAULS4AC1 | 138 | Bus Low Volts | 0.92 | 0.89124 | - | 0.89195 | 0.89085 | 0.8878 | 0.88859 | -
TAEPTN | NORTH | PADU4A (6135) | T200012 | 138 | Bus Low Volts | 0.92 | 0.88324 | - | 0.88443 | 0.88473 | 0.883 | 0.88497 | -
TSHARL | SOUTHERN | PALMITO138 (79600) | E_NEDIN_CC1_TRAIN | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89796 | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | 3WT_001302WILLOWVAL_5_001301WILLOWVAL_8_018537WILLOWVAL_3 C 3 | 138 | Bus High Volts | 1.05 | - | 1.0526 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001163LAMESA_8-001307KEYLYNTE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.059 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001163LAMESA_8-010008LAMESA2_8C1 | 138 | Bus High Volts | 1.05 | 1.053 | 1.0644 | - | 1.0541 | - | 1.0506 | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001163LAMESA_8-011363HARDYMGN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0525 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0526 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001177TEXMABEE_8-011175BAIRDLAK_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0547 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0543 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0548 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001181ANDHWY87_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0565 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0523 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0514 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0542 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0612 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001307KEYLYNTE_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0594 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001308GAILLYNT_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0595 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_001355BUZZDRAW_8-011363HARDYMGN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0514 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_010008LAMESA2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0612 | - | 1.051 | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0509 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_011167ALKALILK2_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0509 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_011167ALKALILK2_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0547 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | LAMESA - BUZZARD DRAW 138 KV LINE 2018 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | LAMESA - BUZZARD DRAW 69/138 KV DCKT LINE 2019 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.052 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | 1.0609 | 1.0835 | 1.0593 | 1.0588 | 1.0554 | 1.058 | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | MIDLAND COUNTY NW - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0569 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | MIDLAND COUNTY NW - MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0564 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | - | 1.0532 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0521 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | NORTH ANDREWS - MCKENZIE 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0512 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | WILLOW VALLEY - LAMESA 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.059 | - | - | - | - | -
TGSEC | FAR_WEST | PATRICIA_8 (9418) | WILLOW VALLEY TRANSFORMER 1 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0526 | - | - | - | - | -
TAEN | SOUTH_CE | PATTON_MB1 (9253) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85932 | - | -
TAEN | SOUTH_CE | PATTON_MB2 (9254) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85932 | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | 3WT_001021MIDLET_5_001023MIDLNDE_8_024989MDLNE_13 C 1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | 3WT_001185MIDCONW_5_001183MIDCONW_8_001186MIDCONW_3 C 3 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | 3WT_001302WILLOWVAL_5_001301WILLOWVAL_8_018537WILLOWVAL_3 C 3 | 138 | Bus High Volts | 1.05 | - | 1.0525 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | 3WT_011387CONSAVVY_5_011388CONSAVVY_8_011386CONSAVVY1_3 C 2 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | 3WT_011387CONSAVVY_5_011388CONSAVVY_8_011389CONSAVVY2_3 C 1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | ANDREWS COUNTY SOUTH - NORTH ANDREWS/HOLT 138 KV SUM 2023 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.055 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | ASP_WRG_P7F2 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | BIG SPRING - BUZZARD DRAW 138 KV (SINGLE B TO B) 2021 WIN - FUTURE | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | C5-WETT-2_A | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | C5-WETT-2_B | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | COALSON DRAW - SAND LAKE DCKT 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | CONSAVVY - GREY WELL DRAW/MIDLAND EAST 138 KV LINE 2026 SUM - 2028 SUM (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | CULBERSON - COALSON DRAW CKT 2 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | CULBERSON - COALSON DRAW DCKT 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | EILAND - BULLDOG 138 KV LINE 2026 SUM - 2027 SUM (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0519 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | Grey Well Draw - Blue Acres & Rockhound 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | HLX_NAV_P7F2 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | HOLT - N ANDREWS B SUM 2017 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0527 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | HORSESHOE SPRINGS - CULBERSON DCKT 138 KV SUM 2019 - FUTURE (DOUBLE B TO B) A | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | HORSESHOE SPRINGS - THREE MILE DRAW 138 KV WIN 2023 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001012PIRCOVE_8-011104BARKETT_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001023MIDLNDE_8-001116WINDWOOD_8C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001023MIDLNDE_8-001178ADOBEMEW_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001023MIDLNDE_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0556 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001023MIDLNDE_8-011295MIDLDWNT_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001074WINKSS_8-001286ONC900076_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001074WINKSS_8-011135RAILSIDE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001132MIDLDWNT_8-011295MIDLDWNT_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001134LITTMAN_8-001278PHILANDS_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.054 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001134LITTMAN_8-011273NELSON_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0544 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001141HOLTSS_8-001262EMMATAP_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0534 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001141HOLTSS_8-900079Other_53C1 | 138 | Bus High Volts | 1.05 | - | 1.0512 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001141HOLTSS_8-900127TODDESSE_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001147CHEYENTA_8-001149DOLRHIDE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001147CHEYENTA_8-011135RAILSIDE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001149DOLRHIDE_8-001150AMOCO3BA_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001150AMOCO3BA_T8-001157ANDRCOSO_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001153ARENATAP_8-001159NOANDREW_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0522 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001153ARENATAP_8-001173ANDHWY181_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0527 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001154BAKKETAP_8-001159NOANDREW_8C1 | 138 | Bus High Volts | 1.05 | - | 1.052 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001154BAKKETAP_8-001161UNPKRBK_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001154BAKKETAP_8-001280BAKKE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001157ANDRCOSO_8-131853NOTSW_1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001157ANDRCOSO_8-900039Other_141C1 | 138 | Bus High Volts | 1.05 | - | 1.0526 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001159NOANDREW_8-001167MUSTANG_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0618 | - | 1.0501 | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001159NOANDREW_8-001262EMMATAP_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0531 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001161UNPKRBK_8-900099Other_36C1 | 138 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001163LAMESA_8-001307KEYLYNTE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0545 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001163LAMESA_8-010008LAMESA2_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0558 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001163LAMESA_8-011363HARDYMGN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0519 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001167MUSTANG_8-001168PAULDTAP_8C1 | 138 | Bus High Volts | 1.05 | - | 1.061 | - | 1.05 | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001169ALKALILK_8-001170PAULDTAP2_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0547 | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001169ALKALILK_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0547 | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001170PAULDTAP2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0551 | - | 1.0507 | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | 1.0505 | 1.0584 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0579 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0506 | 1.0583 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001173ANDHWY181_8-900039Other_141C1 | 138 | Bus High Volts | 1.05 | - | 1.0527 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0537 | 1.0604 | 1.0505 | 1.053 | - | 1.0512 | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0541 | 1.0601 | 1.0509 | 1.0534 | 1.0501 | 1.0516 | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001177TEXMABEE_8-001181ANDHWY87_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0512 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001177TEXMABEE_8-011175BAIRDLAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0518 | 1.0629 | 1.0505 | 1.0527 | - | 1.0501 | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001178ADOBEMEW_8-011280GODDARD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0512 | 1.0626 | - | 1.0521 | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0516 | 1.0631 | 1.0503 | 1.0525 | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001180ECTRHILL_8-001287ONC900028_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001181ANDHWY87_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0551 | 1.0644 | 1.054 | 1.0563 | 1.0516 | 1.0537 | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001183MIDCONW_8-011186HIGHSKY_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0607 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001183MIDCONW_8-023862TELPHRD_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | 1.0521 | 1.0592 | - | 1.0511 | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.051 | 1.0625 | - | 1.0519 | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001264SANADTAP_8-001269MIDFARMS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0514 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001264SANADTAP_8-001283XTOBLOCK9_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001269MIDFARMS_8-001282AMOMIDFM_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001272FULLERTON_8-001275NIXPOD_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0541 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001275NIXPOD_8-001278PHILANDS_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0539 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001282AMOMIDFM_8-900079Other_53C1 | 138 | Bus High Volts | 1.05 | - | 1.051 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001283XTOBLOCK9_8-900099Other_36C1 | 138 | Bus High Volts | 1.05 | - | 1.0514 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001286ONC900076_TAP-131853NOTSW_1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001287ONC900028_TAP-011186HIGHSKY_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0552 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001307KEYLYNTE_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0547 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001308GAILLYNT_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0547 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001326STANTON_E_8-011229STANTON_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001328QUARTZSAND_8-010029LILDEWEY_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_001355BUZZDRAW_8-011363HARDYMGN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0522 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_009418PATRICIA_8-009419JPAYNE_CB_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_009424FTBLOCKS_8-131453KEO_2_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_010008LAMESA2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0548 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_010029LILDEWEY_8-011350WRGRN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_010036MUSTGSPG_8-023840GLSRNCH_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_010036MUSTGSPG_8-023855TALLCTY_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_010049RANGER_5-010057FLCNSEABD_SC1 | 138 | Bus High Volts | 1.05 | - | 1.051 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_010049RANGER_5-010057PRNGMOSS_5C1 | 138 | Bus High Volts | 1.05 | - | 1.051 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_010057PRNGMOSS_5-010062ROUGH_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_010062ROUGH_8-010057PRNGMOSS_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_011078LEANCLAY_8-038099TNCOTTNWD_1C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_011104BARKETT_P8-038107TNGEMSBOKM1C1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0514 | 1.0588 | - | 1.0502 | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0517 | 1.0629 | 1.0505 | 1.0527 | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_011189QUARRYFLD_8-900004Other_10C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_011229STANTON_8-023837BUFFLO_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_011280GODDARD2_T8-011301MOCKNGBRD_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_011296MIDLDWNT2_T8-900033OTHER_133C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_011318SCURCNTYS_5-059905FARADAYC1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_011337POLECAT1_8-011350WRGRN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_011388CONSAVVY_8-011396GREYWELL_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_023855TALLCTY_8-023862TELPHRD_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_023920ABERNATH_5-141607AEEC_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_038036TNCOLIYDT_1-038037TNCOLIET__1C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_038091TNPECOS___1-038095TNJACKRBT1C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_038095TNJACKRBT1-038114TNREEVSCOT1C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_038097TNBCCASTLE1-038099TNCOTTNWD_1C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_038107TNGEMSBOKM1-038109TNGMSBKACC1C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_038114TNREEVSCOT1-038117TNETOYAHT_1C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_038117TNETOYAHT_1-038121TNBLNGLEAT1C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_038121TNBLNGLEAT1-038124TNFAULKNER1C1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_038124TNFAULKNER1-900038Other_47_SOC1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_038145TNCEDRVALE1-038146TNBCTRESTL1C1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_038190TNLONESTAR1-038191TNBCGWRWNK1C1 | 138 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_038190TNLONESTAR1-038195TNCHOLLA__1C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_038355TNLEONCRK_1-038356TNBCLNCRK_1C1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_038430TNWHITEBKR1-038431TNCENTRY1_1C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_038432TNCENTRY2_1-038455TNHOLIDAY_1C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_059900LONG_DRAW-059905FARADAYC1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_076003L_BIGHIL5_1Y-076009L_TWINBU5_1YC1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_900004Other_10-900007Other_137C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_900005Other_44_SO-011610ONC900005_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L_900007Other_137-900015Other_50C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | L2020971-B2 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | LAMESA - BUZZARD DRAW 138 KV LINE 2018 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0519 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | LAMESA - BUZZARD DRAW 69/138 KV DCKT LINE 2019 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0523 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | LAMESA - MCKENZIE DRAW 138 KV SUM 2023 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0547 | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | LATIMER_REATA_P7F1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | 1.08 | 1.0953 | 1.0782 | 1.078 | 1.0744 | 1.0762 | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | MIDESSA SOUTH - MIDLAND EAST & ODESSA CKT 2 138 KV SUM 2022 - SUM 2027 (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | MIDESSA SOUTH - MIDLAND EAST 138 KV SUM 2022 - FUT (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | MIDLAND COUNTY NW - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0553 | 1.0648 | 1.0542 | 1.0564 | 1.0518 | 1.0539 | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | MIDLAND COUNTY NW - MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0549 | 1.0638 | 1.0541 | 1.0563 | 1.0515 | 1.0536 | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | MIDLAND EAST - CONSAVVY/MIDLAND DOWNTOWN 138 KV SUM 2026 - SUM 2028 (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | 1.0545 | 1.0606 | 1.0513 | 1.0537 | 1.0504 | 1.0519 | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0542 | 1.0589 | 1.0507 | 1.053 | - | 1.0514 | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | MIDLAND EAST - MIDLAND DOWNTOWN 138 KV WIN 2023 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | MOSS - MIDLAND COUNTY NW 138 KV 2019 SUM - FUTURE (DOUBLE B TO B) B | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | MOSS - MIDLAND COUNTY NW 138 KV CKT 2 2019 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | MOSS - MIDLAND COUNTY NW CKT 2 2019 SPG - FUTURE | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | MOSS - ODESSA NORTH 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | MOSS - REITER 138KV 2026 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | NATURAL DAM - CALF CREEK - BIG SPRING 138 KV SUM 2026 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | NELSON - FULLERTON 138 KV WIN 2020 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0541 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | NEW-SAM - FOURBROTHERS/TRADINGHOUSE_5 (DOUBLE B TO B)-1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | NEW-SAM - FOURBROTHERS/TRADINGHOUSE_5 (DOUBLE B TO B)-2 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | NORTH ANDREWS - ANDREWS COUNTY SOUTH 138 KV 2023 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0522 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | ODESSA - MIDESSA SOUTH CKT 2 138 KV WIN 2020 - SUM 2027 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | Odessa EHV-Quail & Tesoro Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | P1.2_M138K_F2 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | QUARRY FIELD - BLUE MOUNTAIN CKT 2 138 KV SUM 2025 - FUTURE (SINGLE B TO B)_MODIFIED_BY_MZ | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | QUARRY FIELD - RIVERTON 345 KV 2021 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | QUARTZ SAND - POLECAT CREEK 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | RANGER CAMP - BARBER LAKE SW CKT 2 138 KV SUM 2026 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.052 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | RANGER CAMP - FALCON SEABOARD 345 KV (SINGLE B TO B) SUM 2026 - WIN 2027_MODIFIED_BY_MZ | 138 | Bus High Volts | 1.05 | - | 1.051 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | 1.0522 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | REAT_SKYD_P7F2 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | Reiter-Moss & Wolf 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | Reiter-Moss 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | RIVERTON - DELAWARE RIVER SWITCH 138 KV DCKT LINE (DOUBLE B TO B) WIN 2025 - SUM 2030 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | RIVERTON - DELAWARE RIVER SWITCH 138 KV LINE NORTH CKT 2 (SINGLE B TO B) WIN 2025 - SUM 2030 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | RIVERTON - DELAWARE RIVER SWITCH 138 KV LINE SOUTH CKT 1 SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | RIVERTON - QUARRY FIELD CKT 3 138 KV (SINGLE B TO B) WIN 2025 - FUTURE | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | S_011010WOLFSS_51 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | S_011386CONSAVVY1_31 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | S_011389CONSAVVY2_31 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | S_024989MDLNE_131 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | SALE RANCH - GLASS RANCH 138 KV LINE WIN 2023 - 2027 SUM (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | SALE RANCH - NATURAL DAM 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | SAND LAKE - YUCCA DR CKT 1 138 KV SUM 2019 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | SAND LAKE - YUCCA DR DCKT 138 KV SUM 2019 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | SKYD_SAMS_P7F1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | SPRABERRY - DEWEY LAKE TAP 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | STANTON EAST - SPRABERRY 69 KV/SU BUFFALO 138 KV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | STANTON EAST - SU_BUFFALO 138 KV (SINGLE B TO B) A | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | T_001123ODESSANO_9-001122ODESSANO_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | TALL CITY - PECAN GROVE/GLASS RANCH 138 KV DCKT LINE (DOUBLE B TO B) 2024 SUM - 2028 SUM | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | TESORO - SPRABERRY & MIDESSA SOUTH 138 KV 2024 WIN - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | TRADINGHOUSE - SAM/FOURBROTHERS SWITCH_5 (DOUBLE B TO B)_MODIFIED_BY_MZ | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | WILLOW VALLEY - LAMESA 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0546 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | WILLOW VALLEY TRANSFORMER 1 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0525 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | WINK - ANDREWS COUNTY SOUTH 138 KV CKT 1 SPG 2020 - SUM 2027 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | WINK - ANDREWS COUNTY SOUTH/NOTREES 138 KV DCKT 1 SPG 2020 - SUM 2027 (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.051 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | WINK - ANDREWS COUNTY SOUTH/NOTREES 138 KV DCKT 2 SPG 2020 - SUM 2027 (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | WRG_HLX_P7F2 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | WSHACK_LATIMER_P7 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | YUCCA - COURTNEY CREEK SWITCH & COURTNEY CREEK SWITCH – WOLF CAMP 69 KV LINE (SINGLE B TO B) SUM 2025 - SUM 2028 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP_8 (1168) | YUCCA DRIVE - LOTEBUSH (AEP) 138 KV 2021 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | 3WT_001021MIDLET_5_001023MIDLNDE_8_024989MDLNE_13 C 1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | 3WT_001302WILLOWVAL_5_001301WILLOWVAL_8_018537WILLOWVAL_3 C 3 | 138 | Bus High Volts | 1.05 | - | 1.0563 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | 3WT_011387CONSAVVY_5_011388CONSAVVY_8_011386CONSAVVY1_3 C 2 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | 3WT_011387CONSAVVY_5_011388CONSAVVY_8_011389CONSAVVY2_3 C 1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | ANDREWS COUNTY SOUTH - NORTH ANDREWS/HOLT 138 KV SUM 2023 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0522 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | ASP_WRG_P7F2 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | BIG SPRING - BUZZARD DRAW 138 KV (SINGLE B TO B) 2021 WIN - FUTURE | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | BROWN - EXPANSE 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | C5-WETT-2_A | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | C5-WETT-2_B | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | COALSON DRAW - SAND LAKE DCKT 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | CONSAVVY - GREY WELL DRAW/MIDLAND EAST 138 KV LINE 2026 SUM - 2028 SUM (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0508 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | CULBERSON - COALSON DRAW CKT 2 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | CULBERSON - COALSON DRAW DCKT 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | EILAND - BULLDOG 138 KV LINE 2026 SUM - 2027 SUM (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0526 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | GUNSIGHT - BUZZARD DRAW WIN 2020 - FUTURE (SINGLE B TO B) C | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | HLX_NAV_P7F2 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | HOLT - N ANDREWS B SUM 2017 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | HORSESHOE SPRINGS - RIVERTON/THREE MILE DRAW DCKT 138 KV WIN 2023 - FUTURE (DOUBLE B TO B) E | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001023MIDLNDE_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0552 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001134LITTMAN_8-001278PHILANDS_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0515 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001134LITTMAN_8-011273NELSON_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0517 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001141HOLTSS_8-001262EMMATAP_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001141HOLTSS_8-900079Other_53C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001153ARENATAP_8-001159NOANDREW_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001153ARENATAP_8-001173ANDHWY181_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001154BAKKETAP_8-001159NOANDREW_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001154BAKKETAP_8-001161UNPKRBK_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001154BAKKETAP_8-001280BAKKE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001157ANDRCOSO_8-900039Other_141C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001159NOANDREW_8-001167MUSTANG_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0551 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001159NOANDREW_8-001262EMMATAP_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0509 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001161UNPKRBK_8-900099Other_36C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001163LAMESA_8-001307KEYLYNTE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0611 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001163LAMESA_8-010008LAMESA2_8C1 | 138 | Bus High Volts | 1.05 | 1.0551 | 1.0649 | 1.0515 | 1.0568 | 1.0518 | 1.0535 | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001163LAMESA_8-011363HARDYMGN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0547 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001164LAMESA_9-018920CENTDWSN_9C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001167MUSTANG_8-001168PAULDTAP_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0549 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001168PAULDTAP_8-900060OTHER_140C1 | 138 | Bus High Volts | 1.05 | - | 1.0548 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001170PAULDTAP2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | 1.0561 | 1.0631 | 1.053 | 1.0586 | 1.0538 | 1.0555 | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0584 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0579 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0584 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001173ANDHWY181_8-900039Other_141C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0511 | 1.0608 | - | 1.0503 | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0517 | 1.0608 | - | 1.0508 | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001177TEXMABEE_8-001181ANDHWY87_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001177TEXMABEE_8-011175BAIRDLAK_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0636 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0632 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0638 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001181ANDHWY87_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | 1.0526 | 1.0656 | 1.0513 | 1.0536 | - | 1.0518 | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0609 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001183MIDCONW_8-023862TELPHRD_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0595 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | - | 1.063 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001264SANADTAP_8-001269MIDFARMS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001264SANADTAP_8-001283XTOBLOCK9_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001269MIDFARMS_8-001282AMOMIDFM_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001272FULLERTON_8-001275NIXPOD_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001275NIXPOD_8-001278PHILANDS_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0514 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001282AMOMIDFM_8-900079Other_53C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001283XTOBLOCK9_8-900099Other_36C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0628 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001301WILLOWVAL_8-131955BULLCRK_3_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001307KEYLYNTE_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0614 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001308GAILLYNT_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0615 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001322BIGSPRIG_8-001358KNOTT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001355BUZZDRAW_8-001358KNOTT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001355BUZZDRAW_8-011362FLOWRGRVE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001355BUZZDRAW_8-011363HARDYMGN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0554 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001360GUNSIGHT_8-011149HOWDEN_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001393DAWSON115_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.055 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_001393DAWSON115_8-900060OTHER_140C1 | 138 | Bus High Volts | 1.05 | - | 1.0552 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_009418PATRICIA_8-009419JPAYNE_CB_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_009424FTBLOCKS_8-131453KEO_2_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0509 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_010008LAMESA2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | 1.0529 | 1.0626 | - | 1.0546 | - | 1.0513 | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_011078LEANCLAY_8-038099TNCOTTNWD_1C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_011104BARKETT_P8-038107TNGEMSBOKM1C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.059 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_011149HOWDEN_8-011362FLOWRGRVE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_011167ALKALILK2_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0581 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_011167ALKALILK2_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0572 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0636 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_011189QUARRYFLD_8-900004Other_10C1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_011280GODDARD2_T8-011301MOCKNGBRD_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_011318SCURCNTYS_5-059905FARADAYC1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_011388CONSAVVY_8-011396GREYWELL_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_023920ABERNATH_5-141607AEEC_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_023924FARMLAND_5-023930FIDLWD_5C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_038036TNCOLIYDT_1-038037TNCOLIET__1C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_038091TNPECOS___1-038095TNJACKRBT1C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_038095TNJACKRBT1-038114TNREEVSCOT1C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_038097TNBCCASTLE1-038099TNCOTTNWD_1C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_038107TNGEMSBOKM1-038109TNGMSBKACC1C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_038114TNREEVSCOT1-038117TNETOYAHT_1C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_038117TNETOYAHT_1-038121TNBLNGLEAT1C1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_038121TNBLNGLEAT1-038124TNFAULKNER1C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_038145TNCEDRVALE1-038146TNBCTRESTL1C1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_038190TNLONESTAR1-038191TNBCGWRWNK1C1 | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_038190TNLONESTAR1-038195TNCHOLLA__1C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_038355TNLEONCRK_1-038356TNBCLNCRK_1C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_038430TNWHITEBKR1-038431TNCENTRY1_1C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_038432TNCENTRY2_1-038455TNHOLIDAY_1C1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_059900LONG_DRAW-059905FARADAYC1 | 138 | Bus High Volts | 1.05 | - | 1.051 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_076003L_BIGHIL5_1Y-076009L_TWINBU5_1YC1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L_900004Other_10-900007Other_137C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | L2020971-B2 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | LAMESA - BUZZARD DRAW 138 KV LINE 2018 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0547 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | LAMESA - BUZZARD DRAW 69/138 KV DCKT LINE 2019 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0558 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | LAMESA -ACKERLY 69 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | LATIMER_REATA_P7F1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | 1.0783 | 1.099 | 1.0765 | 1.0761 | 1.0723 | 1.075 | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | MIDESSA SOUTH - MIDLAND EAST & ODESSA CKT 2 138 KV SUM 2022 - SUM 2027 (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0512 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | MIDESSA SOUTH - MIDLAND EAST 138 KV SUM 2022 - FUT (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | MIDLAND COUNTY NW - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0529 | 1.066 | 1.0516 | 1.0538 | - | 1.052 | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | MIDLAND COUNTY NW - MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0526 | 1.0652 | 1.0515 | 1.0537 | - | 1.0518 | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | MIDLAND EAST - CONSAVVY/MIDLAND DOWNTOWN 138 KV SUM 2026 - SUM 2028 (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | 1.0521 | 1.0613 | - | 1.0511 | - | 1.0501 | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.052 | 1.0598 | - | 1.0506 | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | MOSS - MIDLAND COUNTY NW 138 KV 2019 SUM - FUTURE (DOUBLE B TO B) B | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | MOSS - MIDLAND COUNTY NW 138 KV CKT 2 2019 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | MOSS - MIDLAND COUNTY NW CKT 2 2019 SPG - FUTURE | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | MOSS - REITER 138KV 2026 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | NATURAL DAM - CALF CREEK - BIG SPRING 138 KV SUM 2026 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0523 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | NELSON - FULLERTON 138 KV WIN 2020 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | NEW-SAM - FOURBROTHERS/TRADINGHOUSE_5 (DOUBLE B TO B)-1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | NEW-SAM - FOURBROTHERS/TRADINGHOUSE_5 (DOUBLE B TO B)-2 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | NORTH ANDREWS - ANDREWS COUNTY SOUTH 138 KV 2023 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | NORTH ANDREWS - MCKENZIE 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0584 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | ODESSA - MIDESSA SOUTH CKT 2 138 KV WIN 2020 - SUM 2027 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | P1.2_M138K_F2 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | QUARRY FIELD - BLUE MOUNTAIN CKT 2 138 KV SUM 2025 - FUTURE (SINGLE B TO B)_MODIFIED_BY_MZ | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | QUARRY FIELD - RIVERTON 345 KV 2021 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | RANGER CAMP - BARBER LAKE SW CKT 2 138 KV SUM 2026 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0523 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | REAT_SKYD_P7F2 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | Reiter-Moss & Wolf 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | Reiter-Moss 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | RIVERTON - DELAWARE RIVER SWITCH 138 KV DCKT LINE (DOUBLE B TO B) WIN 2025 - SUM 2030 | 138 | Bus High Volts | 1.05 | - | 1.0508 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | RIVERTON - DELAWARE RIVER SWITCH 138 KV LINE NORTH CKT 2 (SINGLE B TO B) WIN 2025 - SUM 2030 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | RIVERTON - DELAWARE RIVER SWITCH 138 KV LINE SOUTH CKT 1 SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | RIVERTON - QUARRY FIELD CKT 3 138 KV (SINGLE B TO B) WIN 2025 - FUTURE | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | S_011010WOLFSS_51 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | S_011386CONSAVVY1_31 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | S_011389CONSAVVY2_31 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | S_024989MDLNE_131 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | SAND LAKE - YUCCA DR CKT 1 138 KV SUM 2019 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | SAND LAKE - YUCCA DR DCKT 138 KV SUM 2019 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | SKYD_SAMS_P7F1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | TRADINGHOUSE - SAM/FOURBROTHERS SWITCH_5 (DOUBLE B TO B)_MODIFIED_BY_MZ | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | WILLOW VALLEY - LAMESA 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0611 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | WILLOW VALLEY TRANSFORMER 1 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0563 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | WINK - ANDREWS COUNTY SOUTH 138 KV CKT 1 SPG 2020 - SUM 2027 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | WINK - ANDREWS COUNTY SOUTH/NOTREES 138 KV DCKT 1 SPG 2020 - SUM 2027 (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | WINK - ANDREWS COUNTY SOUTH/NOTREES 138 KV DCKT 2 SPG 2020 - SUM 2027 (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0508 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | WRG_HLX_P7F2 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | WSHACK_LATIMER_P7 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
TONCOR | FAR_WEST | PAULDTAP2_8 (1170) | YUCCA DRIVE - LOTEBUSH (AEP) 138 KV 2021 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TAEN | SOUTH_CE | PE_MB1 (9118) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94591 | - | - | -
TAEN | SOUTH_CE | PE_MB1 (9118) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85654 | - | -
TAEN | SOUTH_CE | PE_MB1 (9118) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94977 | - | -
TAEN | SOUTH_CE | PE_MB3 (9117) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94588 | - | - | -
TAEN | SOUTH_CE | PE_MB3 (9117) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.8565 | - | -
TAEN | SOUTH_CE | PE_MB3 (9117) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94974 | - | -
TAEN | SOUTH_CE | PE138MB1_CAP (9014) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94594 | - | - | -
TAEN | SOUTH_CE | PE138MB1_CAP (9014) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85657 | - | -
TAEN | SOUTH_CE | PE138MB1_CAP (9014) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.9498 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89656 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89618 | - | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89819 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88706 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89142 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | DESOTO - PEBBLE CREEK 138 KV SWITCH (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8878 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | L_002217BATCHLRD_8-002466BIGONION_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89819 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | L_002229PEBBLCRK_8-002328RED_OAK1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88619 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | L_002328RED_OAK1_8-002424DESSW1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88292 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89702 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8938 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89236 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89938 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94302 | 0.92573 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88388 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89375 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89934 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89405 | - | -
TONCOR | NORTH_CE | PEBBLCRK_8 (2229) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88172 | - | - | -
TONCOR | NORTH | PECANTRE_8 (11528) | L_001424BOWMAN_B8-011528PECANTRE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0619 | - | - | - | - | -
TONCOR | FAR_WEST | PELCNSPG_8 (11243) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0687 | - | - | - | - | -
TONCOR | FAR_WEST | PEMBERTN_8 (11226) | L_001221TEXHARVY_8-001226ARUBA1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0703 | - | - | - | - | -
TONCOR | FAR_WEST | PEMBERTN_8 (11226) | L_001221TEXHARVY_8-011226PEMBERTN_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0713 | - | - | - | - | -
TONCOR | FAR_WEST | PEMBERTN_8 (11226) | L_001222PECKTAP_8-001226ARUBA1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.057 | - | - | - | - | -
TAEPTC | SOUTHERN | PEREGPOI7A (88673) | E_INGLCOSW_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91767 | - | -
TAEPTC | SOUTHERN | PEREGPOI7A (88673) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91686 | - | -
TAEPTC | SOUTHERN | PEREGPOI7A (88673) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89276 | - | -
TAEPTC | SOUTHERN | PEREGPOI7A (88673) | L_008579KATOEN7A-008606GODDARD7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91957 | - | -
ERCOT | SOUTHERN | PEREGRN_S1 (163521) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89287 | - | -
TONCOR | SOUTH_CE | PFLGRVIL1_8 (3665) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.86772 | - | -
TONCOR | SOUTH_CE | PFLGRVILS_8 (13665) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.86983 | - | -
TONCOR | SOUTH_CE | PFLGRVILS2_8 (13664) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8699 | - | -
TAEN | SOUTH_CE | PILOTKNOB (9259) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86782 | - | -
TONCOR | SOUTH_CE | PINTAIL_8 (3692) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87324 | - | -
TONCOR | FAR_WEST | PIRCOVE_8 (1012) | L_001012PIRCOVE_8-011104BARKETT_P8C1 | 138 | Bus High Volts | 1.05 | 1.0503 | - | - | - | - | 1.0501 | -
TAEN | SOUTH_CE | PK138_CAP (9015) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86784 | - | -
TONCOR | NORTH_CE | PL_TENNY_5 (2522) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94376 | - | -
THNEC1 | EAST | PLNTSP (6736) | L_003358CENTVILL_8-003394JEWETTA_8C1 | 138 | Bus High Volts | 1.05 | 1.0607 | - | - | - | - | - | -
TONCOR | EAST | PLSNTSPG_8 (3357) | L_003358CENTVILL_8-003394JEWETTA_8C1 | 138 | Bus High Volts | 1.05 | 1.0639 | - | - | - | - | - | -
TONCOR | NORTH_CE | PLUTO1_8 (12303) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86813 | 0.83384 | 0.89475 | -
TONCOR | NORTH_CE | PLUTO2_8 (12304) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86813 | 0.83384 | 0.89475 | -
TONCOR | NORTH_CE | POETRY_5 (2485) | L_002478ROYSE_S5-002485POETRY_5C1 | 345 | Bus High Volts | 1.1 | - | 1.1367 | - | - | - | - | -
TONCOR | FAR_WEST | POLECAT1_8 (11337) | L_001335FORSANTA_8-011337POLECAT1_8C1 | 138 | Bus Low Volts | 0.9 | 0.89886 | 0.89905 | - | - | - | - | -
TONCOR | FAR_WEST | POLECAT1_8 (11337) | MCDONALD RD - POLECAT 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | 0.89894 | 0.89905 | - | - | - | - | -
TONCOR | FAR_WEST | POLECAT1_8 (11337) | Pre-contingency | 138 | Bus Low Volts | 0.95 | 0.94891 | - | - | - | - | - | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | E_NEDIN_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | 0.84298 | - | - | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | E5DVA1C1_1_B | 138 | Bus Low Volts | 0.92 | - | - | - | 0.85373 | - | - | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | L_005761PAREDESSW8-005766CNTRLAVESUB8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91856 | 0.9163 | 0.91401 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | L_005766CNTRLAVESUB8-008914COFFPORT4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91976 | 0.9175 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | L_005767HIWAY511SUB8-008735CHALYBE4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91831 | 0.91614 | 0.91391 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | L_005767HIWAY511SUB8-008914COFFPORT4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91631 | 0.91406 | 0.91181 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | L_005963TITAN-005965PALOALTOC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91365 | 0.91069 | 0.90937 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | L_005963TITAN-008735CHALYBE4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91467 | 0.91174 | 0.91522 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | L_005965PALOALTO-008950OLMITO4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.90921 | 0.90595 | 0.9054 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | L_008047OCELOTAP4A-008275MILITARY4DC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.90696 | 0.90349 | 0.90274 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | L_008047OCELOTAP4A-008950OLMITO4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.9069 | 0.90342 | 0.90268 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | L_008266MARCONI4A-008338P_ISABEL4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91279 | 0.91115 | 0.90997 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | L_008318RIOHONDO7A-008573BONILLA7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | - | 0.9165 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | L_008338P_ISABEL4A-008735CHALYBE4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91982 | 0.9184 | 0.91705 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | L_008535POMPANO4A-008735CHALYBE4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.83308 | 0.82964 | 0.82661 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | L_008535POMPANO4A-079601STILLMANC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.88426 | - | - | - | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | L10010434_MODIFIED_BY_MZ | 138 | Bus Low Volts | 0.92 | - | - | - | 0.9178 | 0.91547 | 0.91323 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | L10011660_MODIFIED_BY_MZ | 138 | Bus Low Volts | 0.92 | - | - | - | 0.90995 | 0.90675 | 0.90574 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | M1000031210000064 | 138 | Bus Low Volts | 0.92 | - | - | - | - | - | 0.91627 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | M10000841000093-1A | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91828 | 0.91462 | 0.90852 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | P7/C5-SHRY-1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.8696 | 0.85903 | 0.86434 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | P7/C5-SHRY-3 | 138 | Bus Low Volts | 0.92 | - | - | - | - | - | 0.91808 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93459 | 0.93359 | 0.93232 | -
TAEPTC | SOUTHERN | POMPANO4A (8535) | S_008275MILITARY4D1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | - | 0.91996 | -
QFPLT | WEST | PONY_1_8 (170247) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.1991 | - | - | - | - | -
QFPLT | WEST | PONY_2_8 (170248) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.1997 | - | - | - | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | ARGENTA_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91212 | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | E_B_DAVIS_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91039 | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | E_CCEC_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91503 | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90621 | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | E_NUECES_B_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8915 | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91093 | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90666 | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | L_008027CLLCOTTE4A-008452LON_HILL4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89517 | 0.85233 | 0.90369 | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | L_008027CLLCOTTE4A-008924PORTILLA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.9128 | 0.87418 | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8724 | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | L_008579KATOEN7A-008606GODDARD7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89853 | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | L_008606GODDARD7A-888858ARGENTA_POIC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91811 | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | M10000253106503-1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91229 | - | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | M10000254106503-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87347 | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | MB100002510650-2 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91234 | - | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | MB106501000025-2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87397 | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94394 | - | -
TAEPTC | SOUTHERN | PORTILLA4A (8924) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91152 | - | -
TAEPTC | SOUTHERN | PORTLAND4A (8414) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90169 | - | -
TAEPTC | SOUTHERN | PORTLAND4A (8414) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90301 | - | -
RPRIDD | NORTH_CE | PRIDDY_5 (151856) | BROWN SS - RUSSELL GAP / BUCKHORN_5 (DOUBLE B TO B ) | 345 | Bus High Volts | 1.05 | - | 1.0646 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_5 (151856) | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus High Volts | 1.05 | 1.0539 | - | 1.0541 | - | 1.0522 | 1.0543 | -
RPRIDD | NORTH_CE | PRIDDY_5 (151856) | L_001444BROWN_5-003424BUCK_H_5C1 | 345 | Bus High Volts | 1.05 | - | 1.054 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | BROWN SS - RUSSELL GAP / BUCKHORN_5 (DOUBLE B TO B ) | 230 | Bus High Volts | 1.05 | - | 1.0848 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | BROWN SS_RED CRK (AEP) (SINGLE B TO B ) C | 230 | Bus High Volts | 1.05 | - | 1.0527 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | BROWN SW - BLUFF CREEK SW & BROWN SW - CENTRAL BLUFF 345 KV (DOUBLE B TO B)-1 | 230 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | CHINA GROVE SW - AEP PAINT CREEK 138 KV & GRAHAM SES - TONKAWA/COOKFIELD/LONGCREEK 345 KV (DOUBLE B TO B) 2019 SUM - FUTURE-1 | 230 | Bus High Volts | 1.05 | - | 1.052 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | CHINA GROVE SW - AEP PAINT CREEK 138 KV & GRAHAM SES - TONKAWA/COOKFIELD/LONGCREEK 345 KV (DOUBLE B TO B) 2019 SUM - FUTURE-2 | 230 | Bus High Volts | 1.05 | - | 1.0519 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | HANSON_CON | 230 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | L_001444BROWN_5-003424BUCK_H_5C1 | 230 | Bus High Volts | 1.05 | - | 1.0706 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | L_001444BROWN_5-007077L_AMOSCR5_1YC1 | 230 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | L_001444BROWN_5-076006L_BOWWOO5_1YC1 | 230 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | LCRA TSC_BAKERS_CEDACA_DC | 230 | Bus High Volts | 1.05 | - | 1.0529 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | LCRA TSC_CEDACA_NOELKE_DC_1A-1 | 230 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | LCRA TSC_CEDACA_NOELKE_DC_1B-1 | 230 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | LCRA TSC_T551_T643_1 | 230 | Bus High Volts | 1.05 | - | 1.063 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | LCRA TSC_T558_T559_A | 230 | Bus High Volts | 1.05 | - | 1.0522 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | LCRA TSC_T558_T559_B | 230 | Bus High Volts | 1.05 | - | 1.0522 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | LCRA TSC_T558_T559_C | 230 | Bus High Volts | 1.05 | - | 1.052 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | LCRA TSC_T710_T709 | 230 | Bus High Volts | 1.05 | - | 1.0535 | - | - | - | - | -
RPRIDD | NORTH_CE | PRIDDY_T1 (151855) | STECL_4721-1 | 230 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | NORTH_CE | PROLINA_P8 (12366) | L_000675ROCKHILL-002380WESTRIDGE1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0508 | - | - | - | - | -
TONCOR | NORTH_CE | PROLINA_P8 (12366) | L_002370COLLINSS1_8-002380WESTRIDGE1_8C1 | 138 | Bus Low Volts | 0.9 | 0.88518 | - | 0.87821 | 0.87287 | 0.87295 | 0.87369 | -
TONCOR | NORTH_CE | PROSPER1_8 (12375) | L_000675ROCKHILL-002380WESTRIDGE1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
TONCOR | NORTH_CE | PROSPER1_8 (12375) | L_002370COLLINSS1_8-002380WESTRIDGE1_8C1 | 138 | Bus Low Volts | 0.9 | 0.87693 | - | 0.86985 | 0.86431 | 0.86448 | 0.86522 | -
TGSEC | WEST | PUMPJACK4A (60374) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91941 | - | -
TGSEC | WEST | PUMPJACK4A (60374) | L_006648HARGROVE4A-060374PUMPJACK4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91173 | - | -
TGSEC | WEST | PUMPJACK4A (60374) | L_006648HARGROVE4A-076011L_TWINBU8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91535 | 0.90445 | 0.9162 | -
TGSEC | WEST | PUMPJACK4A (60374) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91783 | 0.90136 | 0.91542 | -
TGSEC | WEST | PUMPJACK4A (60374) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91542 | 0.89832 | 0.91264 | -
TGSEC | WEST | PUMPJACK4A (60374) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91176 | 0.89373 | 0.90839 | -
TGSEC | WEST | PUMPJACK4A (60374) | L2020944-A | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91548 | 0.89843 | 0.9127 | -
TGSEC | WEST | PUMPJACK4A (60374) | LCRA TSC_T429_T9426 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91582 | 0.90487 | 0.91642 | -
TAEPTN | NORTH_CE | PUTN4B (6310) | L_060063CERRORIC4A-060355VINSON4AC1 | 138 | Bus High Volts | 1.05 | 1.0502 | - | 1.0501 | 1.0509 | - | 1.0508 | -
TONCOR | FAR_WEST | QUARRYFLD_5 (11188) | QUARRY FIELD - RIVERTON 345 KV 2021 SUM - FUTURE (DOUBLE B TO B) | 345 | Bus High Volts | 1.05 | - | 1.0582 | - | - | - | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91914 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | ARGENTA_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90011 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | DVCPA1C21B_1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91872 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | DVCPA1C21B_2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91967 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | E_B_DAVIS_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89928 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | E_CCEC_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91102 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86745 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | E_LGE_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90283 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | E_NEDIN_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91191 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | E_NUECES_B_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88578 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | G_080039LUCERO7AUS1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91831 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | G_160153INGLCOSW_STGUPE | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91883 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | G_163641CHARGER_S1US1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91795 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | G_170126CALAVER_JKS2UL2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91757 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89741 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88934 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91336 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_005133ELMCREEK-005380SHAULAC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91142 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91931 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_005380SHAULA-005915SO_TEX__345AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91896 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_005725PAWNEESW5-008164COLETO7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91728 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91286 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_008422I_DUPSW4A-008425INGLESID4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90077 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91685 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86285 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_008458B_DAVIS4A-160106B_DAVIS_2_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91971 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_008579KATOEN7A-008606GODDARD7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88754 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_008606GODDARD7A-888858ARGENTA_POIC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9082 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_008659NAISMITH7A-080039LUCERO7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90497 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_008813QUINTANA4A-080065MELNCRK4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91621 | 0.86358 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91547 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_080071ZORILLO7A-080076AJO7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91538 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | L_084555AMBER7A-085000N_SHARPE7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9189 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | M10000271115801 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91138 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | M100101100271-1A | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91824 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | M100101100271-1B | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91944 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | M105311105321 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90279 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | M115851115803 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91538 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | M128103100534 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91715 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | M128104100523 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91837 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | MB100002711580 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91138 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | MB1002710010-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91816 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | MB1005312810 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91732 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | MB1158011585 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91538 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | MB1281010052 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91853 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | MB1291012930 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.83301 | 0.91271 | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | MB1293012910 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89909 | - | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | MBAM-REFORnew | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91934 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | N5GSU2_B | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91757 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | P7-1_E1>>T1839X1_ERC | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91997 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | P7-1_E1>>T1839X2_ERC | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.919 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | P7-1_E1>>T2764Y_ERCa | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91727 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.93532 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87103 | - | -
TAEPTC | SOUTHERN | QUINTANA4A (8813) | STP - HOUDINI & STP - SHAULA | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91755 | - | -
TAEPTC | COAST | RADIANT7A (8715) | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91447 | - | -
TAEPTC | COAST | RADIANT7A (8715) | DVCPA1C21B_1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9122 | - | -
TAEPTC | COAST | RADIANT7A (8715) | E_B_DAVIS_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91934 | - | -
TAEPTC | COAST | RADIANT7A (8715) | E_NUECES_B_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91515 | - | -
TAEPTC | COAST | RADIANT7A (8715) | G_113111LUNIS_CK_S1US1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91966 | - | -
TAEPTC | COAST | RADIANT7A (8715) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89562 | - | -
TAEPTC | COAST | RADIANT7A (8715) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.88125 | - | -
TAEPTC | COAST | RADIANT7A (8715) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91824 | - | -
TAEPTC | COAST | RADIANT7A (8715) | L_005133ELMCREEK-005380SHAULAC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91348 | - | -
TAEPTC | COAST | RADIANT7A (8715) | L_005915SO_TEX__345A-008715RADIANT7AC1 | 345 | Bus High Volts | 1.05 | - | 1.0599 | - | - | - | - | -
TAEPTC | COAST | RADIANT7A (8715) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.9171 | - | -
TAEPTC | COAST | RADIANT7A (8715) | L_008249ANGSTRM7A-008676STATIC7AC1 | 345 | Bus High Volts | 1.05 | - | 1.0521 | - | - | - | - | -
TAEPTC | COAST | RADIANT7A (8715) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91987 | - | -
TAEPTC | COAST | RADIANT7A (8715) | L_008728COBRA7A-081003HABER7AC1 | 345 | Bus High Volts | 1.05 | - | 1.052 | - | - | - | - | -
TAEPTC | COAST | RADIANT7A (8715) | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90541 | - | -
TAEPTC | COAST | RADIANT7A (8715) | M11227210000105-2 | 345 | Bus High Volts | 1.05 | - | 1.0599 | - | - | - | - | -
TAEPTC | COAST | RADIANT7A (8715) | P7-1_E1>>T1839X2_ERC | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91303 | - | -
TONCOR | WEST | RADIUMMT_8 (1398) | L2021010-1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0519 | - | - | -
TONCOR | WEST | RADIUMMT_8 (1398) | PAINT CREEK (WTU) - CHINA GROVE SW 138 KV & GRAHAM SES - TONKAWA 345 KV SUM 2019 - FUTURE (DOUBLE B TO B)-1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0518 | - | - | -
TONCOR | WEST | RADIUMMT_8 (1398) | PAINT CREEK (WTU) - CHINA GROVE SW 138 KV & GRAHAM SES - TONKAWA 345 KV SUM 2019 - FUTURE (DOUBLE B TO B)-2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0519 | - | - | -
TBREC | NORTH_CE | RAILPORT (442) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.92 | - | 0.90288 | 0.87745 | 0.83545 | 0.80183 | 0.86057 | -
TBREC | NORTH_CE | RAILPORT (442) | BEPC_306 | 138 | Bus Low Volts | 0.92 | 0.78661 | 0.73134 | - | - | - | - | -
TBREC | NORTH_CE | RAILPORT (442) | L_000442RAILPORT-001908VENUSC1 | 138 | Bus Low Volts | 0.92 | 0.82334 | 0.74401 | 0.68369 | - | - | - | -
TBREC | NORTH_CE | RAILPORT (442) | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | Bus Low Volts | 0.92 | 0.78658 | 0.73057 | - | - | - | - | -
TAEN | SOUTH_CE | RAINEYST (9261) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94523 | - | - | -
TAEN | SOUTH_CE | RAINEYST (9261) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85542 | - | -
TAEN | SOUTH_CE | RAINEYST (9261) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94928 | - | -
TONCOR | WEST | RANGER_8 (10050) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.77241 | - | - | - | - | -
TAEPTC | SOUTHERN | RAPTOR7A (8673) | E_INGLCOSW_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91756 | - | -
TAEPTC | SOUTHERN | RAPTOR7A (8673) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91675 | - | -
TAEPTC | SOUTHERN | RAPTOR7A (8673) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89265 | - | -
TAEPTC | SOUTHERN | RAPTOR7A (8673) | L_008579KATOEN7A-008606GODDARD7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91946 | - | -
TONCOR | SOUTH_CE | RATTANCRK_8 (3676) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.84863 | - | -
TONCOR | FAR_WEST | RDRUNNER_8 (11131) | L_011180ARYOBLUFF_T8-011199RDRUNNER_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.83061 | - | -
TONCOR | FAR_WEST | RDRUNNER_T8 (11199) | L_011180ARYOBLUFF_T8-011199RDRUNNER_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.83067 | - | -
TONCOR | NORTH_CE | RED_OAK1_8 (2328) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89415 | - | -
TONCOR | NORTH_CE | RED_OAK1_8 (2328) | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89848 | - | -
TONCOR | NORTH_CE | RED_OAK1_8 (2328) | L_002328RED_OAK1_8-002424DESSW1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89969 | 0.88252 | - | -
TONCOR | NORTH_CE | RED_OAK1_8 (2328) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89936 | - | -
TONCOR | NORTH_CE | RED_OAK1_8 (2328) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94961 | 0.93225 | - | -
TONCOR | NORTH_CE | RED_OAK1_8 (2328) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89125 | - | -
TONCOR | NORTH_CE | RED_OAK1_8 (2328) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | Bus Low Volts | 0.9 | - | - | - | 0.8895 | - | - | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | EINSTEIN - CARTERVILLE 138 KV LINE 2025 SUM - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | 0.89467 | - | - | - | - | - | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | L_001328QUARTZSAND_8-010029LILDEWEY_8C1 | 138 | Bus Low Volts | 0.9 | 0.89215 | - | - | - | - | - | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | L_001333MCDONALD_8-001334GLASSCNTYN_8C1 | 138 | Bus Low Volts | 0.9 | 0.89113 | 0.89768 | - | - | - | - | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | L_001334GLASSCNTYN_8-001335FORSANTA_8C1 | 138 | Bus Low Volts | 0.9 | 0.89542 | 0.89992 | - | - | - | - | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | L_001335FORSANTA_8-011337POLECAT1_8C1 | 138 | Bus Low Volts | 0.9 | 0.8915 | 0.89299 | - | - | - | - | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | L_010018CARTVLRNCH_8-023851CARTRVL_8C1 | 138 | Bus Low Volts | 0.9 | 0.89467 | - | - | - | - | - | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | L_010018CARTVLRNCH_8-023852EINSTN_8C1 | 138 | Bus Low Volts | 0.9 | 0.89468 | - | - | - | - | - | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | L_010029LILDEWEY_8-011350WRGRN_P8C1 | 138 | Bus Low Volts | 0.9 | 0.8922 | - | - | - | - | - | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | L_010080REDBERRY_8-023833BULLDOG_8C1 | 138 | Bus Low Volts | 0.9 | 0.84994 | 0.85227 | - | - | 0.89398 | 0.89533 | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | L_011337POLECAT1_8-011350WRGRN_P8C1 | 138 | Bus Low Volts | 0.9 | 0.8946 | - | - | - | - | - | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | L_023851CARTRVL_8-023853EILAND_8C1 | 138 | Bus Low Volts | 0.9 | 0.89731 | - | - | - | - | - | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | MCDONALD RD - POLECAT 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | 0.89162 | 0.89299 | - | - | - | - | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | Pre-contingency | 138 | Bus Low Volts | 0.95 | 0.9251 | 0.93833 | - | - | 0.94322 | 0.94149 | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | QUARTZ SAND - POLECAT CREEK 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | 0.89468 | - | - | - | - | - | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | 0.88279 | 0.89941 | - | - | 0.8956 | - | -
TONCOR | FAR_WEST | REDBERRY_8 (10080) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.8596 | - | - | - | - | -
TBREC | NORTH_CE | REDBUD (643) | L_000675ROCKHILL-002380WESTRIDGE1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0508 | - | - | - | - | -
TBREC | NORTH_CE | REDBUD (643) | L_002370COLLINSS1_8-002380WESTRIDGE1_8C1 | 138 | Bus Low Volts | 0.92 | 0.88517 | - | 0.8782 | 0.87285 | 0.87294 | 0.87367 | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | AEN_LY-FPP¦CIS | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91936 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91566 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | ARGENTA_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89632 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | BAS_RANCH_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91884 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91752 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91924 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | DVCPA1C21B_1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9152 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | DVCPA1C21B_2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91616 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | E_B_DAVIS_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89551 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | E_CCEC_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90733 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | E_DUKE_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91745 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86343 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | E_LGE_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89915 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | E_NEDIN_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90831 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | E_NUECES_B_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88183 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | G_080039LUCERO7AUS1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91476 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | G_080039LUCERO7AUS2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9181 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | G_160101B_D_B_DAVIG1UN1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91767 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | G_160151INGLCOS_CTG1UPE | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91751 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | G_160152INGLCOS_CTG2UPE | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91751 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | G_160153INGLCOSW_STGUPE | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9153 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | G_160201LGE_LGE_GT1UPE | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91919 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | G_163521PEREGRN_S1US1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91975 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | G_163641CHARGER_S1US1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91439 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | G_170126CALAVER_JKS2UL2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91405 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | G_888839BAS_RANCH_POIUC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91886 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89371 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88562 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90982 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_005133ELMCREEK-005380SHAULAC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90787 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9158 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_005380SHAULA-005915SO_TEX__345AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91545 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_005725PAWNEESW5-008164COLETO7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91366 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9093 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_008162COLETO4A-008172VICTORIA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91861 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_008162COLETO4A-008172VICTORIA4AC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9175 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_008249ANGSTRM7A-008956WHITEPT7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91793 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_008412REFUGIO4A-008813QUINTANA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87013 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_008422I_DUPSW4A-008425INGLESID4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89618 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91324 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.85854 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_008458B_DAVIS4A-160105B_DAVIS_1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91767 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_008458B_DAVIS4A-160106B_DAVIS_2_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91614 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_008579KATOEN7A-008606GODDARD7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88355 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_008606GODDARD7A-888858ARGENTA_POIC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90446 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_008659NAISMITH7A-080039LUCERO7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90133 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_008813QUINTANA4A-080065MELNCRK4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91646 | 0.86387 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91197 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_080071ZORILLO7A-080076AJO7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9118 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_080071ZORILLO7A-080171SARITA7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91958 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_080076AJO7A-085000N_SHARPE7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91976 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_080078REFORZAR7A-084555AMBER7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91972 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_080171SARITA7A-160299BAFFIN_2_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91961 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_084555AMBER7A-085000N_SHARPE7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91531 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L_888858ARGENTA_POI-008689TANGO7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9167 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L10011206 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87011 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | L10011585 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91958 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | LCRA TSC_T255_TAE3121_1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91798 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | M10000254106503-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91792 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | M10000271115801 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90777 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | M100101100271-1A | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91531 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | M100101100271-1B | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91649 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | M105311105321 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89911 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | M115851115803 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9118 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | M128103100534 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91341 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | M128104100523 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91465 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | MB100002711580 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90777 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | MB1002710010-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91523 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | MB1005312810 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91358 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | MB106501000025-2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91848 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | MB1158011585 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9118 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | MB1281010052 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91482 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | MB1291012930 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.83359 | 0.91316 | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | MB1293012910 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89954 | - | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | MBAM-REFORnew | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91575 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | N5GSU2_B | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91405 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | P7-1_E1>>T1839X1_ERC | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91647 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | P7-1_E1>>T1839X2_ERC | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91549 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | P7-1_E1>>T2764Y_ERCa | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91375 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.93202 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86709 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | STP - HOUDINI & STP - SHAULA | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91403 | - | -
TAEPTC | SOUTHERN | REFUGIO4A (8412) | WAP - HOUDINI & STP - SHAULA | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91692 | - | -
TONCOR | NORTH_CE | REINDEER_8 (3065) | L_002429WATMLL_8-003065REINDEER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89544 | 0.86921 | - | -
RREROS | FAR_WEST | REROCK_8 (132331) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.0574 | - | - | - | - | - | -
TAEPTC | SOUTHERN | RESNIK4A (8580) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87853 | - | -
TAEPTC | SOUTHERN | RESNIK4A (8580) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89119 | - | -
TAEPTC | SOUTHERN | RESNIK4A (8580) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90437 | - | -
TAEPTC | SOUTHERN | RESNIK4B (8727) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87932 | - | -
TAEPTC | SOUTHERN | RESNIK4B (8727) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89309 | - | -
TAEPTC | SOUTHERN | RESNIK4B (8727) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90666 | - | -
TBREC | NORTH_CE | RETTA (429) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91213 | - | -
TAEPTC | SOUTHERN | RINCON4A (8418) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88378 | - | -
TAEPTC | SOUTHERN | RINCON4A (8418) | E_NUECES_B_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9182 | - | -
TAEPTC | SOUTHERN | RINCON4A (8418) | L_008422I_DUPSW4A-008425INGLESID4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91568 | - | -
TAEPTC | SOUTHERN | RINCON4A (8418) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8894 | - | -
TAEPTC | SOUTHERN | RINCON4A (8418) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90463 | - | -
TAEPTC | SOUTHERN | RINCON4B (8437) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.88366 | - | -
TAEPTC | SOUTHERN | RINCON4B (8437) | E_NUECES_B_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9181 | - | -
TAEPTC | SOUTHERN | RINCON4B (8437) | L_008422I_DUPSW4A-008425INGLESID4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91548 | - | -
TAEPTC | SOUTHERN | RINCON4B (8437) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8893 | - | -
TAEPTC | SOUTHERN | RINCON4B (8437) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90453 | - | -
TAEPTC | SOUTHERN | RIOHNDO7B (8582) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | 0.89003 | - | - | -
TAEPTC | SOUTHERN | RIOHNDO7B (8582) | E5DVA1C1_1_B | 345 | Bus Low Volts | 0.92 | - | - | - | 0.89572 | - | - | -
TAEPTC | SOUTHERN | RIOHNDO7B (8582) | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91071 | - | -
TAEPTC | SOUTHERN | RIOHONDO7A (8318) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | 0.88915 | - | - | -
TAEPTC | SOUTHERN | RIOHONDO7A (8318) | E5DVA1C1_1_B | 345 | Bus Low Volts | 0.92 | - | - | - | 0.89484 | - | - | -
TAEPTC | SOUTHERN | RIOHONDO7A (8318) | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90994 | - | -
TAEPTC | SOUTHERN | RIOHONDO7C (8902) | E_NEDIN_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | 0.7531 | - | - | -
TAEPTC | SOUTHERN | RIOHONDO7C (8902) | E5DVA1C1_1_B | 345 | Bus Low Volts | 0.92 | - | - | - | 0.75236 | - | - | -
TAEPTC | SOUTHERN | RIOHONDO7C (8902) | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | Bus Low Volts | 0.92 | - | - | - | 0.77038 | 0.77335 | - | -
TCPSE | SOUTH_CE | RIONOG_1_5 (5362) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88958 | - | -
TAEN | SOUTH_CE | RIVERPLACE (9260) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94098 | - | - | -
TAEN | SOUTH_CE | RIVERPLACE (9260) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85846 | - | -
TONCOR | FAR_WEST | RIVERVIEW_8 (11245) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0524 | - | - | - | - | -
TONCOR | SOUTH_CE | RNDRCK_S1_8 (3672) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.84861 | - | -
TONCOR | SOUTH_CE | RNDRCKNE1_8 (3670) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85819 | - | -
TONCOR | SOUTH_CE | RNDRCKNE2_8 (3667) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89407 | - | - | -
TONCOR | SOUTH_CE | RNDRCKNE2_8 (3667) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85342 | - | -
TONCOR | SOUTH_CE | RNDRCKNE2_8 (3667) | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | Bus Low Volts | 0.9 | 0.89479 | - | 0.89904 | 0.88112 | 0.87697 | 0.88186 | -
TONCOR | SOUTH_CE | RNDRCKSE1_8 (3654) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89394 | - | - | -
TONCOR | SOUTH_CE | RNDRCKSE1_8 (3654) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85098 | - | -
TONCOR | SOUTH_CE | RNDRCKWH_T_8 (3664) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88653 | - | - | -
TONCOR | SOUTH_CE | RNDRCKWH_T_8 (3664) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.84107 | - | -
TONCOR | SOUTH_CE | RNDRCKWH_T_8 (3664) | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | Bus Low Volts | 0.9 | 0.89748 | - | - | 0.88384 | 0.87969 | 0.88457 | -
TONCOR | SOUTH_CE | RNDRCKWH1_8 (3669) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87965 | - | - | -
TONCOR | SOUTH_CE | RNDRCKWH1_8 (3669) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.82998 | - | -
TONCOR | SOUTH_CE | RNDRCKWH1_8 (3669) | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | Bus Low Volts | 0.9 | 0.89999 | - | - | 0.88638 | 0.88224 | 0.8871 | -
TONCOR | SOUTH_CE | RNDROCK1_8 (3668) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.84978 | - | -
TONCOR | NORTH_CE | RNRDPL1_5 (2359) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | 0.93693 | 0.9343 | - | -
TONCOR | NORTH_CE | RNRDPL1_5 (2359) | RENNER - NORTHWEST CARROLLTON 345 KV & RENNER - ALLEN SW 345 KV (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | 0.88024 | 0.87727 | 0.87861 | 0.88117 | -
TONCOR | NORTH_CE | RNRTPL1_5 (2355) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | 0.93684 | 0.93415 | - | -
TONCOR | NORTH_CE | RNRTPL1_5 (2355) | RENNER - NORTHWEST CARROLLTON 345 KV & RENNER - ALLEN SW 345 KV (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | 0.88026 | 0.87729 | 0.87862 | 0.88119 | -
TGSEC | WEST | ROCK_HOLLOW (60352) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91206 | 0.89039 | 0.89722 | -
TGSEC | WEST | ROCK_HOLLOW (60352) | L_006536BIGLAKE4B-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90539 | - | -
TGSEC | WEST | ROCK_HOLLOW (60352) | L_006648HARGROVE4A-060374PUMPJACK4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91369 | - | -
TGSEC | WEST | ROCK_HOLLOW (60352) | L_006648HARGROVE4A-076011L_TWINBU8_1YC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91858 | 0.90803 | 0.91964 | -
TGSEC | WEST | ROCK_HOLLOW (60352) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88346 | 0.86483 | 0.88092 | -
TGSEC | WEST | ROCK_HOLLOW (60352) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88049 | 0.8611 | 0.87747 | -
TGSEC | WEST | ROCK_HOLLOW (60352) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91994 | 0.87576 | 0.85519 | 0.87195 | -
TGSEC | WEST | ROCK_HOLLOW (60352) | L2020944-A | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88057 | 0.86123 | 0.87754 | -
TGSEC | WEST | ROCK_HOLLOW (60352) | LCRA TSC_T429_T9426 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91905 | 0.90844 | 0.91986 | -
TGSEC | WEST | ROCK_HOLLOW (60352) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94825 | - | -
TGSEC | WEST | ROCK_HOLLOW (60352) | T_006535BIGLAKE4A-006536BIGLAKE4BC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90997 | - | -
TONCOR | SOUTH_CE | ROCKDALE1_8 (3678) | L_003740SLRPRTY_8-003750VOSSLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88824 | - | - | - | - | -
TBREC | NORTH_CE | ROCKHILL (675) | L_000675ROCKHILL-002380WESTRIDGE1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
TBREC | NORTH_CE | ROCKHILL (675) | L_002370COLLINSS1_8-002380WESTRIDGE1_8C1 | 138 | Bus Low Volts | 0.92 | 0.87371 | - | 0.86659 | 0.86097 | 0.86117 | 0.86191 | -
TAEPTC | SOUTHERN | ROCKPORT4A (8434) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.86799 | - | -
TAEPTC | SOUTHERN | ROCKPORT4A (8434) | E_NUECES_B_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90836 | - | -
TAEPTC | SOUTHERN | ROCKPORT4A (8434) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91993 | - | -
TAEPTC | SOUTHERN | ROCKPORT4A (8434) | L_008422I_DUPSW4A-008425INGLESID4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.88842 | 0.87221 | 0.78716 | 0.88067 | -
TAEPTC | SOUTHERN | ROCKPORT4A (8434) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87842 | - | -
TAEPTC | SOUTHERN | ROCKPORT4A (8434) | L_008579KATOEN7A-008606GODDARD7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91039 | - | -
TAEPTC | SOUTHERN | ROCKPORT4A (8434) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89299 | - | -
TONCOR | SOUTH_CE | ROGERS1A_8 (3675) | L_003415TEMP_SS__8-003485TINROOF_8C1 | 138 | Bus High Volts | 1.05 | 1.0811 | - | 1.0746 | 1.0575 | 1.0565 | - | -
TLCRA | SOUTHERN | ROSATA4A (8153) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90811 | - | -
TLCRA | SOUTHERN | ROSATA4A (8153) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91014 | - | -
TLCRA | SOUTHERN | ROSATA4A (8153) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9195 | - | -
TSTEC | SOUTHERN | ROSSVILLESB8 (5718) | L_005390SOMERSET-005718ROSSVILLESB8C1 | 138 | Bus Low Volts | 0.9 | 0.87606 | - | - | - | - | - | -
TONCOR | NORTH_CE | ROYSE_N5 (2461) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94842 | - | -
TONCOR | NORTH_CE | ROYSE_S5 (2478) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94841 | - | -
TONCOR | NORTH_CE | ROYSE1_T5 (2474) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94834 | - | -
TONCOR | NORTH_CE | ROYSE3_5 (2483) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94839 | - | -
TAEPTN | WEST | RUSSEKST4A (6517) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91303 | 0.89116 | 0.89667 | -
TAEPTN | WEST | RUSSEKST4A (6517) | L_006536BIGLAKE4B-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90821 | - | -
TAEPTN | WEST | RUSSEKST4A (6517) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.8796 | 0.86206 | 0.87794 | -
TAEPTN | WEST | RUSSEKST4A (6517) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.87652 | 0.85821 | 0.87435 | -
TAEPTN | WEST | RUSSEKST4A (6517) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91983 | 0.87142 | 0.85189 | 0.8684 | -
TAEPTN | WEST | RUSSEKST4A (6517) | L2020944-A | 138 | Bus Low Volts | 0.92 | - | - | - | 0.87659 | 0.85834 | 0.87442 | -
TAEPTN | WEST | RUSSEKST4A (6517) | T_006535BIGLAKE4A-006536BIGLAKE4BC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.913 | - | -
TONCOR | NORTH_CE | RUSSELLGAP_5 (3348) | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus High Volts | 1.05 | 1.0721 | - | 1.0729 | 1.0659 | 1.0708 | 1.0726 | -
TONCOR | FAR_WEST | RUSTHLLS_8 (11103) | L_001084ORLA_SW1_8-011132LONGPAST_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0518 | - | - | - | - | -
TONCOR | FAR_WEST | RUSTHLLS_8 (11103) | L_001095SCRWBEAN_T8-011132LONGPAST_8C1 | 138 | Bus High Volts | 1.05 | 1.0509 | 1.0529 | - | - | - | - | -
RKEYCA | SOUTH_CE | RVRVLY2_8 (170664) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88586 | - | -
RKEYCA | SOUTH_CE | RVRVLYS_8 (170663) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88584 | - | -
RKEYCA | SOUTH_CE | RVRVLYS3_8 (170665) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88573 | - | -
TONCOR | FAR_WEST | S_CURTIS_8 (11179) | L_001023MIDLNDE_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0561 | - | - | - | - | -
TONCOR | FAR_WEST | S_CURTIS_8 (11179) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | 1.0509 | 1.0642 | - | - | - | - | -
TONCOR | FAR_WEST | S_CURTIS_8 (11179) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0628 | - | - | - | - | -
TONCOR | FAR_WEST | S_CURTIS_8 (11179) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0511 | 1.0638 | - | - | - | - | -
TBREC | NORTH_CE | SAINTPAUL (223) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89515 | 0.86245 | - | -
TBREC | NORTH_CE | SAINTPAUL (223) | KEMP RANCH - SARDIS 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91171 | - | -
TBREC | NORTH_CE | SAINTPAUL (223) | KEMP RANCH - SARDIS 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91171 | - | -
TBREC | NORTH_CE | SAINTPAUL (223) | KEMP RANCH - SOAP CREEK / SARDIS 138 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90645 | - | -
TBREC | NORTH_CE | SAINTPAUL (223) | L_000203SARDIS8-002309WAX_NW_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91072 | - | -
TBREC | NORTH_CE | SAINTPAUL (223) | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89982 | - | -
TBREC | NORTH_CE | SAINTPAUL (223) | L_002305AIRPRD_T8-002307MDLTHTXI1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90284 | - | -
TBREC | NORTH_CE | SAINTPAUL (223) | L_002307MDLTHTXI1_8-012307NEWBRCH_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91291 | - | -
TBREC | NORTH_CE | SAINTPAUL (223) | L_002308MDLTH_S_8-002309WAX_NW_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90532 | - | -
TBREC | NORTH_CE | SAINTPAUL (223) | L_002308MDLTH_S_8-012307NEWBRCH_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91581 | - | -
TBREC | NORTH_CE | SAINTPAUL (223) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91974 | - | -
TBREC | NORTH_CE | SAINTPAUL (223) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.9466 | - | -
TBREC | NORTH_CE | SAINTPAUL (223) | SOAP CREEK - CEDAR HILL / SARDIS 138 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90953 | - | -
TONCOR | NORTH_CE | SALADO_S1_8 (13640) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89904 | - | - | -
TONCOR | NORTH_CE | SALADO_S1_8 (13640) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.84831 | - | -
TONCOR | NORTH_CE | SALADO1_8 (3640) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85789 | - | -
TONCOR | NORTH_CE | SALADOSS_5 (3699) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.86575 | - | -
TONCOR | FAR_WEST | SALEM_8 (10041) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | 0.89342 | - | - | - | 0.89673 | - | -
TONCOR | FAR_WEST | SALEM_8 (10041) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.86695 | - | - | - | - | -
TAEN | SOUTH_CE | SALEMWLK (9263) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86173 | - | -
TONCOR | FAR_WEST | SALTCRKW_8 (1079) | L_001084ORLA_SW1_8-011080THRMIDRW_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0537 | - | - | - | - | -
TONCOR | FAR_WEST | SALTCRKW_8 (1079) | L_001084ORLA_SW1_8-011132LONGPAST_8C1 | 138 | Bus High Volts | 1.05 | 1.0542 | 1.0575 | - | - | - | - | -
TONCOR | FAR_WEST | SALTCRKW_8 (1079) | L_001095SCRWBEAN_T8-011132LONGPAST_8C1 | 138 | Bus High Volts | 1.05 | 1.0567 | 1.0589 | 1.052 | - | - | - | -
TONCOR | WEST | SALTMN_8 (23846) | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus Low Volts | 0.9 | 0.83331 | 0.85163 | 0.84715 | 0.84877 | 0.83144 | 0.84423 | -
TONCOR | WEST | SALTMN_8 (23846) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.75656 | - | - | - | - | -
TONCOR | SOUTH_CE | SAND_TXU_5 (13429) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88168 | - | -
TONCOR | FAR_WEST | SANDHILL_8 (1104) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.0586 | - | - | - | - | -
TONCOR | FAR_WEST | SANDHLTA_8 (1103) | L_001013WOLFSS_8-001103SANDHLTA_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0792 | - | - | - | - | -
TAEN | SOUTH_CE | SANDHSYD (9216) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.88217 | - | -
TONCOR | SOUTH_CE | SANDOW_SR1_8 (13441) | L_013430SAND_TXU_8-013441SANDOW_SR1_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | - | 1.0534 | - | -
TONCOR | SOUTH_CE | SANDOW_SR2_8 (13442) | L_013430SAND_TXU_8-013442SANDOW_SR2_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | - | 1.0534 | - | -
TAEPTN | FAR_WEST | SANTARIT4A (60361) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91625 | 0.85644 | 0.83906 | 0.85469 | -
TAEPTN | FAR_WEST | SANTARIT4A (60361) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91144 | 0.85078 | 0.83074 | 0.84696 | -
TAEPTN | FAR_WEST | SANTARIT4A (60361) | L2020944-A | 138 | Bus Low Volts | 0.92 | - | - | 0.91634 | 0.85651 | 0.83918 | 0.85475 | -
TBREC | NORTH_CE | SARDIS8 (203) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88952 | 0.85336 | 0.91789 | -
TBREC | NORTH_CE | SARDIS8 (203) | KEMP RANCH - SARDIS 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90617 | - | -
TBREC | NORTH_CE | SARDIS8 (203) | KEMP RANCH - SARDIS 138 KV (SINGLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90617 | - | -
TBREC | NORTH_CE | SARDIS8 (203) | KEMP RANCH - SOAP CREEK / SARDIS 138 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89994 | - | -
TBREC | NORTH_CE | SARDIS8 (203) | L_000203SARDIS8-002309WAX_NW_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90502 | - | -
TBREC | NORTH_CE | SARDIS8 (203) | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89612 | - | -
TBREC | NORTH_CE | SARDIS8 (203) | L_002305AIRPRD_T8-002307MDLTHTXI1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89955 | - | -
TBREC | NORTH_CE | SARDIS8 (203) | L_002307MDLTHTXI1_8-012307NEWBRCH_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91138 | - | -
TBREC | NORTH_CE | SARDIS8 (203) | L_002308MDLTH_S_8-002309WAX_NW_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89883 | - | -
TBREC | NORTH_CE | SARDIS8 (203) | L_002308MDLTH_S_8-012307NEWBRCH_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91486 | - | -
TBREC | NORTH_CE | SARDIS8 (203) | SOAP CREEK - CEDAR HILL / SARDIS 138 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90359 | - | -
TONCOR | NORTH_CE | SARGT1_5 (2946) | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | 0.8985 | - | - | -
TONCOR | NORTH_CE | SARGT1_5 (2946) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89413 | - | -
TONCOR | NORTH_CE | SARGT1_5 (2946) | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89759 | - | -
TONCOR | NORTH_CE | SARGT1_5 (2946) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89761 | - | -
TONCOR | NORTH_CE | SARGT1_5 (2946) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89654 | - | -
TONCOR | NORTH_CE | SARGT1_5 (2946) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | 0.94019 | 0.94329 | 0.93142 | - | -
TONCOR | NORTH_CE | SARGT1_5 (2946) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88997 | - | -
TONCOR | NORTH_CE | SARGT1_5 (2946) | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89906 | - | -
TONCOR | NORTH_CE | SARGT1_5 (2946) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89875 | - | -
TONCOR | NORTH_CE | SARGT1_5 (2946) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | Bus Low Volts | 0.9 | - | - | - | 0.88698 | - | - | -
TONCOR | NORTH_CE | SARGT1_5 (2946) | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 345 | Bus Low Volts | 0.9 | - | - | 0.89035 | - | - | - | -
TONCOR | FAR_WEST | SCHUMM_P8 (11379) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.0581 | - | - | - | - | -
TBREC | SOUTH_CE | SCHWERTNER (122) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88919 | - | 0.91406 | -
TBREC | SOUTH_CE | SCHWERTNER (122) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8322 | - | -
TONCOR | FAR_WEST | SCRWBEAN_8 (1090) | L_001084ORLA_SW1_8-011080THRMIDRW_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0543 | - | - | - | - | -
TONCOR | FAR_WEST | SCRWBEAN_8 (1090) | L_001084ORLA_SW1_8-011132LONGPAST_8C1 | 138 | Bus High Volts | 1.05 | 1.0548 | 1.0581 | 1.0504 | - | - | - | -
TONCOR | FAR_WEST | SCRWBEAN_8 (1090) | L_001095SCRWBEAN_T8-011132LONGPAST_8C1 | 138 | Bus High Volts | 1.05 | 1.0573 | 1.0596 | 1.0526 | - | - | - | -
TONCOR | FAR_WEST | SCRWBEAN_T8 (1095) | L_001084ORLA_SW1_8-011080THRMIDRW_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0525 | - | - | - | - | -
TONCOR | FAR_WEST | SCRWBEAN_T8 (1095) | L_001084ORLA_SW1_8-011132LONGPAST_8C1 | 138 | Bus High Volts | 1.05 | 1.053 | 1.0563 | - | - | - | - | -
TONCOR | FAR_WEST | SCRWBEAN_T8 (1095) | L_001095SCRWBEAN_T8-011132LONGPAST_8C1 | 138 | Bus High Volts | 1.05 | 1.0555 | 1.0577 | 1.0508 | - | - | - | -
TAEPTC | SOUTHERN | SDI7A (88249) | E_INGLCOSW_CC1_TRAIN | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91073 | - | -
TAEPTC | SOUTHERN | SDI7A (88249) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.89218 | - | -
TAEPTC | SOUTHERN | SDI7A (88249) | SAN_PAT_CON | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.91768 | - | -
RLUMN | SOUTH_CE | SDSES_1_8 (170093) | 3WT_013429SAND_TXU_5_013441SANDOW_SR1_8_013440SAND3_ONC_3 C 2 | 138 | Bus High Volts | 1.036 | 1.0407 | - | - | - | - | - | -
RLUMN | SOUTH_CE | SDSES_1_8 (170093) | 3WT_013429SAND_TXU_5_013442SANDOW_SR2_8_013439SAND2_ONC_3 C 3 | 138 | Bus High Volts | 1.036 | 1.0404 | - | - | - | - | - | -
RLUMN | SOUTH_CE | SDSES_1_8 (170093) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.971 | - | - | - | - | 0.95827 | - | -
RLUMN | SOUTH_CE | SDSES_1_8 (170093) | L_013430SAND_TXU_8-013441SANDOW_SR1_8C1 | 138 | Bus High Volts | 1.036 | 1.0407 | - | - | - | - | - | -
RLUMN | SOUTH_CE | SDSES_1_8 (170093) | L_013430SAND_TXU_8-013442SANDOW_SR2_8C1 | 138 | Bus High Volts | 1.036 | 1.0404 | - | - | - | - | - | -
TAEPTC | SOUTHERN | SEABIRD (84250) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.86144 | - | -
TAEPTC | SOUTHERN | SEABIRD (84250) | L_008422I_DUPSW4A-008425INGLESID4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.84615 | 0.82751 | 0.73008 | 0.83813 | -
TAEPTC | SOUTHERN | SEABIRD (84250) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87557 | - | -
TAEPTC | SOUTHERN | SEABIRD (84250) | SAN_PAT_CON | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89003 | - | -
TAEN | SOUTH_CE | SEAHOLM (9132) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94525 | - | - | -
TAEN | SOUTH_CE | SEAHOLM (9132) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85518 | - | -
TAEN | SOUTH_CE | SEAHOLM (9132) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94951 | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | G_134241TAYGETE_S1US1 | 138 | Bus Low Volts | 0.92 | - | - | 0.9199 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | G_134243TAYGETE_S2US2 | 138 | Bus Low Volts | 0.92 | - | - | 0.91982 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_001009YUCCADR_8-011245RIVERVIEW_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91516 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_006630FTST4A-038355TNLEONCRK_1C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91912 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_006630FTST4A-060384SOLSTICE4BC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91977 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_006630FTST4A-132482RIGGINS_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91863 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_006673MUSQUIZ4A-060377CREOSOTE4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.9188 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_011245RIVERVIEW_8-900064Other_134C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91583 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_038069TNFLATTOP_1-038294TNFOXTAIL_1C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91862 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_060207VERH4A-060808HOEFSROA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.89684 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91359 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_060383LINTERNA4A-060385SOLSTICE4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91574 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_060383LINTERNA4A-132331REROCK_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91465 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_060385SOLSTICE4A-060393PIGCREEK4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91201 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_060385SOLSTICE4A-060716SGSA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.86745 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_060385SOLSTICE4A-060717FTSW4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91896 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_060385SOLSTICE4A-060808HOEFSROA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.84878 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_060392LOTEBUSH4A-060415BASIN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91798 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_060393PIGCREEK4A-134245TAYGETE_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91343 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_060393PIGCREEK4A-134705TYGTEII_8C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.9164 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_060397GASPADTA4A-060415BASIN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91772 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_060397GASPADTA4A-900064Other_134C1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91625 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L_060716SGSA4A-060721CRYO4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91523 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | L2020971-B2 | 138 | Bus Low Volts | 0.92 | - | - | 0.91798 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.0552 | - | - | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.9233 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | S_038340TNAIRPORT411 | 138 | Bus Low Volts | 0.92 | - | - | 0.91692 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | S_038380TNCOYANOSA11 | 138 | Bus Low Volts | 0.92 | - | - | 0.91821 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | S_060721CRYO4A1 | 138 | Bus Low Volts | 0.92 | - | - | 0.90949 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | SAND LAKE - SOLSTICE 345 KV DCKT LINE (DOUBLE B TO B) WIN 2027 - FUTURE | 138 | Bus Low Volts | 0.92 | - | - | 0.90866 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | T_060385SOLSTICE4A-060384SOLSTICE4BCP1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91996 | - | - | - | -
TAEPTN | FAR_WEST | SGSA4A (60716) | YUCCA DRIVE - LOTEBUSH (AEP) 138 KV 2021 SUM - FUTURE (SINGLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | 0.91798 | - | - | - | -
TONCOR | NORTH_CE | SGVL1_8 (3076) | L_002434SGVLSW1_8-003076SGVL1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89384 | - | -
TONCOR | NORTH_CE | SGVLSW1_5 (2433) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | 0.94916 | 0.93978 | - | -
TONCOR | NORTH_CE | SGVLSW1_5 (2433) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89276 | - | -
TCPSE | SOUTH_CE | SHAULA (5380) | E5DVA1C1_1_B | 345 | Bus High Volts | 1.05 | - | 1.0556 | - | - | - | - | -
TCPSE | SOUTH_CE | SHAULA (5380) | E5DVA1C1_1_B_1 | 345 | Bus High Volts | 1.05 | - | 1.0548 | - | - | - | - | -
TCPSE | SOUTH_CE | SHAULA (5380) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89389 | - | -
TCPSE | SOUTH_CE | SHAULA (5380) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88382 | - | -
TCPSE | SOUTH_CE | SHAULA (5380) | L_005133ELMCREEK-005380SHAULAC1 | 345 | Bus High Volts | 1.05 | - | 1.0545 | - | - | - | - | -
ERCOT | SOUTH_CE | SHLA_S1 (170901) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89396 | - | -
ERCOT | SOUTH_CE | SHLA_S1 (170901) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8839 | - | -
ERCOT | SOUTH_CE | SHLA_S1 (170951) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89396 | - | -
ERCOT | SOUTH_CE | SHLA_S1 (170951) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8839 | - | -
TONCOR | NORTH_CE | SHRYAUTO1_5 (1918) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89906 | - | -
TONCOR | NORTH_CE | SHRYAUTO1_5 (1918) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94266 | - | -
TONCOR | NORTH_CE | SHRYAUTO2_5 (1934) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89914 | - | -
TONCOR | NORTH_CE | SHRYAUTO2_5 (1934) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94279 | - | -
TONCOR | SOUTH_CE | SKYBOX_8 (3371) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88295 | - | -
TAEN | SOUTH_CE | SLAUGHTR (9267) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86068 | - | -
RKEYCA | SOUTH_CE | SLCNHLS_8 (170582) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87236 | - | -
TONCOR | SOUTH_CE | SLRPRTY_8 (3740) | L_003740SLRPRTY_8-003750VOSSLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | 0.88109 | - | - | - | - | -
TONCOR | SOUTH_CE | SLRPRTY_8 (3740) | Voss Lake - Sandow 138 kV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.054 | - | - | - | - | - | -
TONCOR | WEST | SNYDER_8 (1305) | XFMR-RANGER_5 | 138 | Bus Low Volts | 0.9 | - | 0.88827 | - | - | - | - | -
TONCOR | NORTH_CE | SOAPCRK_8 (2289) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87766 | 0.84435 | - | -
ERCOT | NORTH_CE | SODG_2320 (702320) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88976 | - | -
ERCOT | NORTH_CE | SODG_2704 (702704) | L_002340MELSSA_P8-002374ANNASW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89735 | - | - | -
ERCOT | EAST | SODG_32853 (732853) | BRYN_9995DC | 138 | Bus Low Volts | 0.9 | - | - | 0.84103 | 0.83716 | - | - | -
ERCOT | EAST | SODG_32853 (732853) | L_032780BRYN_RELLIS-032852BRYN_STEELE_C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.83256 | 0.83841 | -
ERCOT | EAST | SODG_32853 (732853) | L_032851BRYN_LENRDRD-032853BRYN_SMETANAC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.86982 | 0.86652 | 0.69896 | 0.71438 | -
ERCOT | EAST | SODG_32853 (732853) | L_032851BRYN_LENRDRD-032862BRYN_ATK138C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.84668 | 0.84326 | - | - | -
ERCOT | EAST | SODG_32853 (732853) | L_032852BRYN_STEELE_-032857BRYN_SNOO138C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.81959 | 0.82639 | -
ERCOT | SOUTH_CE | SODG_3654 (703654) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89394 | - | - | -
ERCOT | SOUTH_CE | SODG_3654 (703654) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85098 | - | -
ERCOT | SOUTH_CE | SODG_3661 (703661) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.86981 | - | -
ERCOT | SOUTH_CE | SODG_3665 (703665) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.86772 | - | -
ERCOT | SOUTH_CE | SODG_3666 (703666) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87632 | - | -
ERCOT | SOUTH_CE | SODG_3667 (703667) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89407 | - | - | -
ERCOT | SOUTH_CE | SODG_3667 (703667) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85342 | - | -
ERCOT | SOUTH_CE | SODG_3667 (703667) | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | Bus Low Volts | 0.9 | 0.89479 | - | 0.89904 | 0.88112 | 0.87697 | 0.88186 | -
ERCOT | SOUTH_CE | SODG_3668 (703668) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.84978 | - | -
ERCOT | SOUTH_CE | SODG_3673 (703673) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87659 | - | -
ERCOT | NORTH_CE | SODG_441 (700441) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86689 | 0.83264 | 0.89345 | -
ERCOT | NORTH_CE | SODG_441 (700441) | BEPC_306 | 138 | Bus Low Volts | 0.9 | 0.78305 | 0.73045 | - | - | - | - | -
ERCOT | NORTH_CE | SODG_441 (700441) | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | Bus Low Volts | 0.9 | 0.78302 | 0.72967 | - | - | - | - | -
ERCOT | NORTH_CE | SODG_675 (700675) | L_002370COLLINSS1_8-002380WESTRIDGE1_8C1 | 138 | Bus Low Volts | 0.9 | 0.87371 | - | 0.86659 | 0.86097 | 0.86117 | 0.86191 | -
ERCOT | SOUTH_CE | SODG_7208 (707208) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85283 | - | -
ERCOT | SOUTH_CE | SODG_9121 (709121) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8589 | - | -
ERCOT | SOUTH_CE | SODG_9123 (709123) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.86024 | - | -
ERCOT | SOUTH_CE | SODG_9271 (709271) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85237 | - | -
ERCOT | SOUTH_CE | SODG_9342 (709342) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85778 | - | -
TAEPTN | FAR_WEST | SOLSTICE4A (60385) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.0731 | - | - | - | - | - | -
TAEPTN | FAR_WEST | SOLSTICE4A (60385) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.94432 | - | - | - | -
TAEPTN | FAR_WEST | SOLSTICE4B (60384) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.0629 | - | - | - | - | - | -
TBREC | NORTH_CE | SONTERRA (121) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88305 | - | 0.90846 | -
TBREC | NORTH_CE | SONTERRA (121) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.82501 | - | -
TBREC | NORTH_CE | SONTERRA (121) | LCRATSC_6_EUCLID_JOHNDU | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91932 | - | -
TAEN | SOUTH_CE | SOUTHEAST (9240) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.88128 | - | -
TAEN | SOUTH_CE | SPRNKL_MB1 (9272) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93601 | - | 0.94959 | -
TAEN | SOUTH_CE | SPRNKL_MB1 (9272) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85241 | - | -
TAEN | SOUTH_CE | SPRNKL_MB1 (9272) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.93956 | - | -
TAEN | SOUTH_CE | SPRNKL_MB2 (9271) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93598 | - | 0.94954 | -
TAEN | SOUTH_CE | SPRNKL_MB2 (9271) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85237 | - | -
TAEN | SOUTH_CE | SPRNKL_MB2 (9271) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.93945 | - | -
TONCOR | NORTH_CE | SSWWT2_8 (3080) | L_002429WATMLL_8-003083WILMER1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.82085 | 0.80782 | 0.86188 | -
TONCOR | NORTH_CE | SSWWT2_8 (3080) | L_002434SGVLSW1_8-003076SGVL1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89626 | - | -
TONCOR | NORTH_CE | SSWWT2T_8 (3079) | L_002429WATMLL_8-003083WILMER1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.82104 | 0.80801 | 0.86206 | -
TONCOR | NORTH_CE | SSWWT2T_8 (3079) | L_002434SGVLSW1_8-003076SGVL1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89643 | - | -
TONCOR | SOUTH_CE | STARRANCH_8 (3653) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.86668 | - | -
TONCOR | SOUTH_CE | STARRANCH1_8 (13656) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87321 | - | -
TONCOR | SOUTH_CE | STARRANCH2_8 (13657) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8667 | - | -
TAEPTC | SOUTHERN | STATIC7A (8676) | Haber - Coleto Creek | 345 | Bus Low Volts | 0.92 | - | - | - | - | - | 0.82954 | -
TAEPTC | SOUTHERN | STATIC7A (8676) | L_008249ANGSTRM7A-008676STATIC7AC1 | 345 | Bus High Volts | 1.05 | - | 1.0592 | - | - | - | - | -
TAEPTC | SOUTHERN | STATIC7A (8676) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.91865 | - | -
TAEN | SOUTH_CE | STECK (9275) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93856 | - | - | -
TAEN | SOUTH_CE | STECK (9275) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85457 | - | -
TAEN | SOUTH_CE | STECK (9275) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94858 | - | -
TONCOR | FAR_WEST | STEER_8 (10044) | L_001322BIGSPRIG_8-010044STEER_8C1 | 138 | Bus Low Volts | 0.9 | 0.85453 | 0.88888 | - | - | 0.8845 | - | -
TONCOR | NORTH_CE | STERRETT1_8 (2317) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8781 | - | -
TONCOR | NORTH_CE | STERRETT1_8 (2317) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94643 | - | -
TONCOR | NORTH_CE | STERRETT1_8 (2317) | STERRETT-SARDIS/DESOTO 138KV DCKT (DOULBE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89911 | - | - | -
TONCOR | NORTH_CE | STERRETTL_8 (12317) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89682 | 0.86 | - | -
TONCOR | NORTH_CE | STERRETTL_8 (12317) | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89978 | - | -
TONCOR | NORTH_CE | STERRETTL_8 (12317) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94688 | - | -
TONCOR | NORTH_CE | STERTRD_8 (2237) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88454 | - | -
TONCOR | NORTH_CE | STERTRD_8 (2237) | L_000217GLNHEIGHTS-002424DESSW1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89879 | - | -
TONCOR | NORTH_CE | STERTRD_8 (2237) | STERRETT-SARDIS/DESOTO 138KV DCKT (DOULBE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89342 | - | - | -
TSHARL | SOUTHERN | STILLMAN (79601) | E_NEDIN_CC1_TRAIN | 138 | Bus Low Volts | 0.9 | - | - | - | 0.8977 | - | - | -
TBREC | NORTH_CE | STLHOSHOLW (125) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.85789 | - | -
TAEN | SOUTH_CE | STONEY (9237) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.88169 | - | -
RELMBR | NORTH_CE | STRATEGC_5 (151423) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89788 | - | -
RELMBR | NORTH_CE | STRATEGC_5 (151423) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89759 | - | -
RELMBR | NORTH_CE | STRATEGC_5 (151423) | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89979 | - | -
RELMBR | NORTH_CE | STRATEGC_5 (151423) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93431 | - | -
RELMBR | NORTH_CE | STRATEGC_5 (151423) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89337 | - | -
RELMBR | NORTH_CE | STRATEGC_5 (151423) | TRIN-RICH (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89215 | - | -
RELMBR | NORTH_CE | STRATEGC_5 (151423) | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89853 | - | -
RELMBR | NORTH_CE | STRATEGC_5 (151423) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89909 | - | -
RELMBR | NORTH_CE | STRATEGC_5 (151423) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | Bus Low Volts | 0.9 | - | - | - | 0.8877 | - | - | -
TAEN | SOUTH_CE | SUMMIT_MB1 (9279) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93537 | - | - | -
TAEN | SOUTH_CE | SUMMIT_MB1 (9279) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85413 | - | -
TAEN | SOUTH_CE | SUMMIT_MB1 (9279) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94749 | - | -
TAEN | SOUTH_CE | SUMMIT_MB2 (9280) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93543 | - | - | -
TAEN | SOUTH_CE | SUMMIT_MB2 (9280) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85417 | - | -
TAEN | SOUTH_CE | SUMMIT_MB2 (9280) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94753 | - | -
TAEN | SOUTH_CE | SW138_CAP (9016) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86176 | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | 3WT_010049RANGER_5_010050RANGER_8_010051RANGER1_3 C 1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | 3WT_010049RANGER_5_010050RANGER_8_010052RANGER2_3 C 2 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | ASP_WRG_P7F2 | 138 | Bus High Volts | 1.05 | - | 1.051 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | BAS_RANCH_CON | 138 | Bus High Volts | 1.05 | - | - | - | 1.0508 | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | BIGSAMPSON_CON | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | BROWN SS_RED CRK (AEP) (SINGLE B TO B ) C | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | BROWN SW - BLUFF CREEK SW & BROWN SW - CENTRAL BLUFF 345 KV (DOUBLE B TO B)-2 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | C5-WETT-2_A | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | CATTLEMAN - PRAIRIE LAND 345 KV 2026 SUM - 2027 SUM (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | CATTLMAN - LONGSHORE/PRAIRIE LAND 345 KV WIN 2027 - SUM 2027 (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0522 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | CLEAR CROSSING - COODY CROSSING/THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | CLY_PHNT1P7F1-1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | CLY_PHNT1P7F1-2 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | CLY_PHNT2P7F1-1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | CLY_PHNT2P7F1-2 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | COODY CROSSING - TECUMSEH AND CLEAR CROSSING - THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | DERMOTT - BLUFF CREEK SW & DERMOTT - ENNIS CREEK 138 KV (DOUBLE B TO B) 2023 WIN - FUTURE | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | DERMOTT - BLUFF CREEK SW & ENNIS CREEK - GOLDEN SW 138 KV (DOUBLE B TO B) 2023 WIN - FUTURE | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | DERMOTT - KIRCHHOF CKT 1 & DERMOTT - KIRCHHOF CKT 2 345 KV (DOUBLE B TO B) C | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | E_OECCS_CC1_TRAIN | 138 | Bus High Volts | 1.05 | - | 1.0527 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | E_OECCS_CC2_TRAIN | 138 | Bus High Volts | 1.05 | - | 1.0528 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | E_QALSW_CC1_TRAIN | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | E_QALSW_CC2_TRAIN | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | G_180151SWEETWN_WND1UW1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | G_180156SWEETWN_WND3UW2 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | G_180160SWEETW_WND4BUW1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | G_180162SWEETWN_WND5UW1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | G_182971MARYNEAL_W1UW1 | 138 | Bus High Volts | 1.05 | - | 1.0528 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | G_888839BAS_RANCH_POIUC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0509 | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | HLX_NAV_P7F2 | 138 | Bus High Volts | 1.05 | - | 1.051 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | HOLLY_CON | 138 | Bus High Volts | 1.05 | - | 1.0517 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | IRON_BELT_CON | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_000844GPL_NEVILLSW-076000L_NORTMC5_1YC1 | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_000844GPL_NEVILLSW-076002L_BAKERS5_1YC1 | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_001048TONKAWA_5-888881SOLAC_POIC1 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_001058LONGSHORE_5-010053CATTLEMEN_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0509 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_001058LONGSHORE_5-059903BEARKATC1 | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_001064SUN_8-001311SACROC_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0508 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_001190BARBER_LK2_8-011393FRONTIER_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_001298ONC900014_TAP-001305SNYDER_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_001304DEEPCRK_8-001305SNYDER_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_001304DEEPCRK_8-001311SACROC_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_001309BLUFCKTA_8-001318CHINAGRV_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_001333MCDONALD_8-131143MCDLD_1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_001339ESKOTA_8-011341NLAMARTA_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_001341SWTRDTAP_8-011341NLAMARTA_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0512 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_001414CHAMPNCRK_5-181153LONEWOLF_1_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0514 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_001435LONGCREK_5-006235ABMULCW7AC1 | 138 | Bus High Volts | 1.05 | - | 1.0523 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_001435LONGCREK_5-011420SWEETEAST_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_006235ABMULCW7A-060040BLF_CRK7AC1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_006235ABMULCW7A-060791PERIGEE7AC1 | 138 | Bus High Volts | 1.05 | - | 1.0512 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_007046L_KENDAL5_1Y-060618EDISON7BC1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_007046L_KENDAL5_1Y-060621EDISON7DC1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_010032LILLUTHER_8-023831LUTHER_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_010032LILLUTHER_8-023835VLMOOR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_010041SALEM_8-023832COYOTE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_010041SALEM_8-023833BULLDOG_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_010049RANGER_5-010057FLCNSEABD_SC1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_010049RANGER_5-010057PRNGMOSS_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_010049RANGER_5-011048TONKAWAW_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0539 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_010053CATTLEMEN_5-019000LONGSHRFLY_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_010053CATTLEMEN_5-076030L_GASCCR5_1YC1 | 138 | Bus High Volts | 1.05 | - | 1.0552 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_011048TONKAWAW_5-011318SCURCNTYS_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_011048TONKAWAW_5-011318SCURCNTYS_5C2 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_011048TONKAWAW_5-011420SWEETEAST_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0517 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_011048TONKAWAW_5-011420SWEETEAST_5C2 | 138 | Bus High Volts | 1.05 | - | 1.0517 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_011406CENTBLUF_5-011420SWEETEAST_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_011406CENTBLUF_5-011420SWEETEAST_5C2 | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_011406CENTBLUF_5-182255HOLSTN_5C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_011420SWEETEAST_5-071050L_BITTCR5_1YC1 | 138 | Bus High Volts | 1.05 | - | 1.052 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_023831LUTHER_8-023832COYOTE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_023849VLMOOR_5-059900LONG_DRAWC1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_023920ABERNATH_5-023928DBLMTN_5C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_023920ABERNATH_5-141607AEEC_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_023924FARMLAND_5-023930FIDLWD_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_023924FARMLAND_5-888856HOLLY_POIC1 | 138 | Bus High Volts | 1.05 | - | 1.0517 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_059900LONG_DRAW-888842IRON_BELT_POIC1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_059902SAND_BLUFF-059907BERNOULLIC1 | 138 | Bus High Volts | 1.05 | - | 1.051 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_059902SAND_BLUFF-076090L_DIVIDE5_1YC1 | 138 | Bus High Volts | 1.05 | - | 1.0508 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_059903BEARKAT-059907BERNOULLIC1 | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_059903BEARKAT-132993BEARKAT_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_060616EDISON7A-060709OERSTED7BC1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_060619EDISON7C-060711OERSTED7DC1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_060708OERSTED7A-076003L_BIGHIL5_1YC1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_060710OERSTED7C-076003L_BIGHIL5_1YC1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_071050L_BITTCR5_1Y-180161SWEETWN4_1_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0567 | - | 1.051 | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_076003L_BIGHIL5_1Y-076005L_SCHNDR5_1YC1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_076003L_BIGHIL5_1Y-076005L_SCHNDR5_1YC2 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_076015L_CEDACA5_1Y-134512HILO_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_076030L_GASCCR5_1Y-076090L_DIVIDE5_1YC1 | 138 | Bus High Volts | 1.05 | - | 1.0523 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_076030L_GASCCR5_1Y-181352GOAT_1_5C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_131753PC_SOUTH_1_5-131754PC_SOUTH_2_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_131753PC_SOUTH_1_5-131755PC2_SWYD_1_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0514 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_150313LNCRK2_1_8-150314LNCRK2_2_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0518 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_180157SWEETWN3_1_8-180158SWEETWN3_2_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_180161SWEETWN4_1_5-180163SWEETWN5_5C1 | 138 | Bus High Volts | 1.05 | - | 1.0545 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_180955TKWSW_1_5-180956KIO_SWYD_2_5C1 | 138 | Bus High Volts | 1.05 | - | 1.051 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_180961IND_1_5-180962KIO_SWYD_4_5C1 | 138 | Bus High Volts | 1.05 | - | 1.051 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_888842IRON_BELT_POI-059910VOLTAC1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L_888856HOLLY_POI-059900LONG_DRAWC1 | 138 | Bus High Volts | 1.05 | - | 1.0517 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L2025540 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | L2025541 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LATIMER_REATA_P7F1 | 138 | Bus High Volts | 1.05 | - | 1.051 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_BAKERS_CEDACA_DC | 138 | Bus High Volts | 1.05 | - | 1.0604 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_CEDACA_NOELKE_DC_1A-1 | 138 | Bus High Volts | 1.05 | - | 1.0581 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_CEDACA_NOELKE_DC_1A-2 | 138 | Bus High Volts | 1.05 | - | 1.0571 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_CEDACA_NOELKE_DC_1B-1 | 138 | Bus High Volts | 1.05 | - | 1.0581 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_CEDACA_NOELKE_DC_1B-2 | 138 | Bus High Volts | 1.05 | - | 1.0571 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_NOELK_SNGTR_NOELK_SNGTR2 | 138 | Bus High Volts | 1.05 | - | 1.0563 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_SCHNDR_BIGHIL_DC | 138 | Bus High Volts | 1.05 | - | 1.053 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_SNGTR_SCHDR_SNGTR_SCHDR2 | 138 | Bus High Volts | 1.05 | - | 1.0556 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_T21457 | 138 | Bus High Volts | 1.05 | - | 1.0603 | - | 1.054 | - | 1.0511 | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_T422_T550 | 138 | Bus High Volts | 1.05 | - | 1.053 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_T423_T551_A | 138 | Bus High Volts | 1.05 | - | 1.0514 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_T424_T551_A_1 | 138 | Bus High Volts | 1.05 | - | 1.0521 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_T551_T643_1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_T558 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_T558_T559_A | 138 | Bus High Volts | 1.05 | - | 1.0525 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_T558_T559_B | 138 | Bus High Volts | 1.05 | - | 1.0525 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_T558_T559_C | 138 | Bus High Volts | 1.05 | - | 1.0525 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_T559 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LCRA TSC_T710_T709 | 138 | Bus High Volts | 1.05 | - | 1.0509 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LONGCREEK SW - SWEETWATER EAST & MULBERRY CREEK 345 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0539 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | LUTHER - VEALMOOR 138 KV LINE 2026 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | MB210150210155-2 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | MB210150210155-3 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | New Champion - Meinan 138kV | 138 | Bus High Volts | 1.05 | - | 1.0526 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | New SweetEAST - Meinan 138kV | 138 | Bus High Volts | 1.05 | - | 1.0529 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | New Sweeteast - Meinan and BitterCreek 345kV Double | 138 | Bus High Volts | 1.05 | - | 1.061 | 1.0529 | 1.0547 | - | 1.0509 | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | PAINT CREEK (WTU) - CHINA GROVE SW 138 KV & GRAHAM SES - TONKAWA 345 KV SUM 2019 - FUTURE (DOUBLE B TO B)-1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | PHNT_WSHACK_P7-1 | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | PHNT_WSHACK_P7-2 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | - | - | - | 1.0616 | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | RANGER CAMP - ESKOTA SW 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0518 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | RANGER CAMP - FALCON SEABOARD 345 KV (SINGLE B TO B) SUM 2026 - WIN 2027_MODIFIED_BY_MZ | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | Ranger Camp-Eskota 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | - | - | 1.0552 | - | 1.0523 | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | REAT_SKYD_P7F2 | 138 | Bus High Volts | 1.05 | - | 1.051 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | S_011318SCURCNTYS_51 | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | S_150315LNCRK2_1_51 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | SAND LAKE - SOLSTICE 345 KV DCKT LINE (DOUBLE B TO B) WIN 2027 - FUTURE | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 1 & SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 2 345 KV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0504 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | SKYD_SAMS_P7F1 | 138 | Bus High Volts | 1.05 | - | 1.051 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | SNYDER - SUN SW 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | SOLACE_CON | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | STECL_4720 | 138 | Bus High Volts | 1.05 | - | 1.0563 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | STECL_4721-1 | 138 | Bus High Volts | 1.05 | - | 1.0581 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | STECL_4721-2 | 138 | Bus High Volts | 1.05 | - | 1.0571 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | SWEETWATER EAST - CENTRAL BLUFF CKT 1 & SWEETWATER EAST - CENTRAL BLUFF CKT 2 345 KV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0532 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | SWEETWATER EAST - TONKAWA SW CKT 1 & SWEETWATER EAST - TONKAWA SW CKT 2 345 KV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0551 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | T_150315LNCRK2_1_5-150314LNCRK2_2_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0518 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | T_180165SWEETWN3_1_5-180158SWEETWN3_2_8C2 | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.053 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | WETT LONG DRAW - WETT VOLTA 345 KV LINE (SINGLE B TO B)-1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | WETT LONG DRAW - WETT VOLTA 345 KV LINE (SINGLE B TO B)-2 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | WILLOW CREEK - CLEAR CROSSING (THOMAS PRICE) & COODY CROSSING - TECUMSEH 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV SUM 2026 - FUTURE (TRIPLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | WILLOW CREEK - CLEAR CROSSING\TECUMSEH 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV (TRIPLE B TO B) A | 138 | Bus High Volts | 1.05 | - | 1.0503 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | WILLOW CREEK - TECUMSEH/THOMAS PRICE 345 KV DCKT WIN 2023 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | WILLOW CREEK - THOMAS PRICE\TECUMSEH CREEK 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV WIN 2023 - FUTURE (TRIPLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | WRG_HLX_P7F2 | 138 | Bus High Volts | 1.05 | - | 1.051 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | WSHACK_LATIMER_P7 | 138 | Bus High Volts | 1.05 | - | 1.0508 | - | - | - | - | -
ERCOT | WEST | SWEETWN2_1_8 (180154) | XFMR-RANGER_5 | 138 | Bus High Volts | 1.05 | - | 1.0508 | - | - | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | ALLEN SW - ANNA SW 138 KV (DOUBLE B TO B) A 23 RIDGEVIEW | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | ALLEN SW - ANNA SW/BLOOMDALE SW 138 KV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | BAS_RANCH_CON | 138 | Bus High Volts | 1.05 | - | - | - | 1.0569 | - | 1.0506 | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | BROWN SW - BLUFF CREEK SW & BROWN SW - CENTRAL BLUFF 345 KV (DOUBLE B TO B)-1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | BROWN SW - BLUFF CREEK SW & BROWN SW - CENTRAL BLUFF 345 KV (DOUBLE B TO B)-2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | C5-WETT-2_A-1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | C5-WETT-2_A-2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.051 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | Cattleman-Morgan Creek CT Yard Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | CENTRAL BLUFF - BROWN SW & CENTRAL BLUFF - BLUFF CREEK SW 345 KV (DOUBLE B TO B)-2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | CONSAVVY - MIDESSA SOUTH & CONSAVVY - TESORO 345 KV 2024 WIN - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0511 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | DERMOTT - BLUFF CREEK SW & DERMOTT - ENNIS CREEK 138 KV (DOUBLE B TO B) 2023 WIN - FUTURE | 138 | Bus High Volts | 1.05 | - | - | - | 1.0513 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | DERMOTT - BLUFF CREEK SW & ENNIS CREEK - GOLDEN SW 138 KV (DOUBLE B TO B) 2023 WIN - FUTURE | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | DUNE - WINK/YUKON 138 KV 2019 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | E_FLCNS_CC1_TRAIN | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | E_OECCS_CC1_TRAIN | 138 | Bus High Volts | 1.05 | - | - | - | 1.0521 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | E_OECCS_CC2_TRAIN | 138 | Bus High Volts | 1.05 | - | - | - | 1.0523 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | E_QALSW_CC1_TRAIN | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | E_QALSW_CC2_TRAIN | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | E5DVA1C1_1_B | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | E5DVA1C1_1_B_1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | EXPANSE - GRADY 138 KV LINE SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | FALCON SOUTH - RANGER CAMP 345 KV SUM 2027 - FUTURE(DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0534 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | G_010012METEOR_5US1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0516 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | G_060716SGSA4AUS1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | G_131751PC__PANTHER2UW3 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | G_134953EUNICE_S2US2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | G_135501RDOSLR_S1US1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | G_136341TRBNT_PV_S1US1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | G_180151SWEETWN_WND1UW1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | G_180153SWEETWN_WND2UW2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.051 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | G_180160SWEETW_WND4BUW1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0509 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | G_180162SWEETWN_WND5UW1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | G_181151LONEWOLF_G1UW1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | G_181152LONEWOLF_G2UW2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | G_182971MARYNEAL_W1UW1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0534 | - | 1.0507 | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | G_888839BAS_RANCH_POIUC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0569 | - | 1.0505 | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | G_888851TRIFECTA_POIUN1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0519 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | GRAHAM PLANT SWITCH-TONKAWA SWITCH/COOK FIELD ROAD SWITCH 345 KV (DOUBLE B TO B)-1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | HANSON_CON | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | HLX_NAV_P7F2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | HOLLY_CON | 138 | Bus High Volts | 1.05 | - | - | - | 1.0517 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | IRON_BELT_CON | 138 | Bus High Volts | 1.05 | - | - | - | 1.0521 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_000842GPL_KINGMTSW-000843GPL_KINGMTTPC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.051 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_000844GPL_NEVILLSW-076000L_NORTMC5_1YC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0514 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_000844GPL_NEVILLSW-076002L_BAKERS5_1YC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_000860GPL_GIRVINSW-136341TRBNT_PV_S1C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001048TONKAWA_5-888881SOLAC_POIC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001058LONGSHORE_5-059903BEARKATC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0534 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001064SUN_8-001311SACROC_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.051 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0509 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001141HOLTSS_8-132313ECEC_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001298ONC900014_TAP-001305SNYDER_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001304DEEPCRK_8-001305SNYDER_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0508 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001304DEEPCRK_8-001311SACROC_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0509 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001309BLUFCKTA_8-001318CHINAGRV_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001312SCURYCHV_8-011130KNDRSACRC_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001312SCURYCHV_8-011306DERMOTT_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001314ENNISCK_8-011306DERMOTT_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001333MCDONALD_8-001334GLASSCNTYN_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001333MCDONALD_8-131143MCDLD_1_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001335FORSANTA_8-011337POLECAT1_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001339ESKOTA_8-011341NLAMARTA_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0511 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001341SWTRDTAP_8-011341NLAMARTA_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0511 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001341SWTRDTAP_8-011342LORAINES_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001414CHAMPNCRK_5-181153LONEWOLF_1_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0529 | - | 1.0501 | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001435LONGCREK_5-006235ABMULCW7AC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0521 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001435LONGCREK_5-011420SWEETEAST_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0514 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_001444BROWN_5-060040BLF_CRK7AC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_006216BLF_CRK4A-006260SOUTHABI4AC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_006235ABMULCW7A-060040BLF_CRK7AC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0509 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_006235ABMULCW7A-888860RUBICONALPHA_POIC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0522 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_007389L_PINNAC8_1Y-135019TI_SOLAR_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_010031LILGRADY_8-011368EXPANSE_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_010031LILGRADY_8-023842GRADY_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_010032LILLUTHER_8-010034LILVLMOOR_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_010032LILLUTHER_8-023831LUTHER_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_010034LILVLMOOR_8-023835VLMOOR_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_010041SALEM_8-023832COYOTE_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_010041SALEM_8-023833BULLDOG_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_010049RANGER_5-010057PRNGMOSS_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_010049RANGER_5-010057PRNGMOSS_5C2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0507 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_010049RANGER_5-011048TONKAWAW_5C1 | 138 | Bus High Volts | 1.05 | - | - | 1.0517 | 1.0528 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_010049RANGER_5-011048TONKAWAW_5C2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0528 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_010050RANGER_8-011342LORAINES_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_010053CATTLEMEN_5-076030L_GASCCR5_1YC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.053 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_011028ODESEHV2_5-059901GRELTONC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_011048TONKAWAW_5-011318SCURCNTYS_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_011048TONKAWAW_5-011318SCURCNTYS_5C2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_011048TONKAWAW_5-011420SWEETEAST_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0509 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_011048TONKAWAW_5-011420SWEETEAST_5C2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0509 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_011270DOGHOUSE_5-023876CLEARFRK_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0513 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_011270DOGHOUSE_5-134805PROSPERO_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0504 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_011270DOGHOUSE_5-135183PRSPERO2_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_011273NELSON_8-135503RDOSLR_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_011318SCURCNTYS_5-059905FARADAYC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_011406CENTBLUF_5-011420SWEETEAST_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0516 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_011406CENTBLUF_5-011420SWEETEAST_5C2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0516 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_011420SWEETEAST_5-071050L_BITTCR5_1YC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0517 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_023831LUTHER_8-023832COYOTE_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_023849VLMOOR_5-059900LONG_DRAWC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0509 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_023920ABERNATH_5-023928DBLMTN_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_023924FARMLAND_5-023930FIDLWD_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_023924FARMLAND_5-888856HOLLY_POIC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_059900LONG_DRAW-059902SAND_BLUFFC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_059900LONG_DRAW-888842IRON_BELT_POIC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0516 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_059901GRELTON-059910VOLTAC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_059902SAND_BLUFF-059907BERNOULLIC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0523 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_059902SAND_BLUFF-076090L_DIVIDE5_1YC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_059903BEARKAT-059907BERNOULLIC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0528 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_059903BEARKAT-132993BEARKAT_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_059904COTTONWOOD-060006HYPERION7AC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_060017HODLRAN27A-060515CLEARCRO7AC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_060393PIGCREEK4A-134245TAYGETE_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_060393PIGCREEK4A-134705TYGTEII_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_071050L_BITTCR5_1Y-180161SWEETWN4_1_5C1 | 138 | Bus High Volts | 1.05 | - | - | 1.0514 | 1.0571 | - | 1.0537 | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_076002L_BAKERS5_1Y-135327REDBARN_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_076030L_GASCCR5_1Y-076090L_DIVIDE5_1YC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_131753PC_SOUTH_1_5-131754PC_SOUTH_2_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0509 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_131753PC_SOUTH_1_5-131755PC2_SWYD_1_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0516 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_150313LNCRK2_1_8-150314LNCRK2_2_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0527 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_180154SWEETWN2_1_8-180155SWEETWN2_2_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0511 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_180161SWEETWN4_1_5-180163SWEETWN5_5C1 | 138 | Bus High Volts | 1.05 | - | - | 1.0502 | 1.0552 | - | 1.0523 | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_180955TKWSW_1_5-180956KIO_SWYD_2_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0515 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_180961IND_1_5-180962KIO_SWYD_4_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0515 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_888842IRON_BELT_POI-059910VOLTAC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.052 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_888856HOLLY_POI-059900LONG_DRAWC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0523 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_888860RUBICONALPHA_POI-060791PERIGEE7AC1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L_888866HANSON_POI-011406CENTBLUF_5C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | L2920902 | 138 | Bus High Volts | 1.05 | - | - | - | 1.05 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | LCRA TSC_BAKERS_CEDACA_DC | 138 | Bus High Volts | 1.05 | - | - | - | 1.0522 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | LCRA TSC_CEDACA_NOELKE_DC_1A-1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0514 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | LCRA TSC_CEDACA_NOELKE_DC_1A-2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0511 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | LCRA TSC_CEDACA_NOELKE_DC_1B-1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0514 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | LCRA TSC_CEDACA_NOELKE_DC_1B-2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0511 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | LCRA TSC_NOELK_SNGTR_NOELK_SNGTR2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.051 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | LCRA TSC_SNGTR_SCHDR_SNGTR_SCHDR2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | LCRA TSC_T21456 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0521 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | LCRA TSC_T422_T550 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | LCRA TSC_T423_T551_A | 138 | Bus High Volts | 1.05 | - | - | - | 1.051 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | LCRA TSC_T424_T551_A_1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0511 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | LONGCREEK SW - SWEETWATER EAST & MULBERRY CREEK 345 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | 1.0512 | 1.0549 | - | 1.0512 | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | LUTHER - VEALMOOR 138 KV LINE 2027 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0505 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | MB2089320892 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | MB2552825529 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0509 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | MB2726627277 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | New Champion - Meinan 138kV | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | New SweetEAST - Meinan 138kV | 138 | Bus High Volts | 1.05 | - | - | 1.0502 | 1.054 | - | 1.0513 | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | New Sweeteast - Meinan and BitterCreek 345kV Double | 138 | Bus High Volts | 1.05 | 1.0535 | - | 1.0597 | 1.0622 | - | 1.0571 | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | ODESSA EHV - NORTH MCCAMEY 345 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0508 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | PAINT CREEK (WTU) - CHINA GROVE SW 138 KV & GRAHAM SES - TONKAWA 345 KV SUM 2019 - FUTURE (DOUBLE B TO B)-1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | PRAIRIELAND – CONSAVVY SUM 2027 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0502 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.0519 | - | - | 1.0717 | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | RANGER CAMP - ESKOTA SW 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0524 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | Ranger Camp-Eskota 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | - | - | 1.0522 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | Ranger Camp-Morgan Creek CT Yard Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | - | 1.0513 | 1.0502 | - | 1.0503 | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | - | - | 1.0629 | - | 1.059 | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | Rockhound-Prong Moss Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | RUBICONALPHA_CON | 138 | Bus High Volts | 1.05 | - | - | - | 1.0522 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | S_011318SCURCNTYS_51 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | SAND LAKE - SOLSTICE 345 KV DCKT LINE (DOUBLE B TO B) WIN 2027 - FUTURE | 138 | Bus High Volts | 1.05 | - | - | - | 1.0503 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | SEAGOVILLE SW-WATERMILL 138 KV (SINGLE B TO B) WILMER 138/69 TRANSFORMER A GELLER | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | SEAGOVILLE SW-WATERMILL/WILMER-FERRIS DCKT (DOUBLE B TO B) A | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | SKYD_SAMS_P7F1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | SOLACE_CON | 138 | Bus High Volts | 1.05 | - | - | - | 1.0501 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | STECL_10592 | 138 | Bus High Volts | 1.05 | - | - | 1.0503 | - | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | STECL_4720 | 138 | Bus High Volts | 1.05 | - | - | - | 1.051 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | STECL_4721-1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0514 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | STECL_4721-2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0511 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | SWEETWATER EAST - CENTRAL BLUFF CKT 1 & SWEETWATER EAST - CENTRAL BLUFF CKT 2 345 KV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0543 | - | 1.0517 | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | SWEETWATER EAST - TONKAWA SW CKT 1 & SWEETWATER EAST - TONKAWA SW CKT 2 345 KV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | 1.0508 | 1.0525 | - | 1.0504 | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | T_150315LNCRK2_1_5-150314LNCRK2_2_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0527 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | T_180164SWEETWN2_1_5-180155SWEETWN2_2_8C2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0511 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | TESORO - MIDESSA SOUTH/CONSAVVY 345 KV WIN 2024 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0513 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | 1.0513 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | TRIFECTA_CON | 138 | Bus High Volts | 1.05 | - | - | - | 1.052 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | WETT LONG DRAW - WETT VOLTA 345 KV LINE (SINGLE B TO B)-1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0516 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | WETT LONG DRAW - WETT VOLTA 345 KV LINE (SINGLE B TO B)-2 | 138 | Bus High Volts | 1.05 | - | - | - | 1.052 | - | - | -
RSWTW3 | WEST | SWEETWN3_1_8 (180157) | XFMR-CATTLEMAN_5 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0506 | - | - | -
RSWTW3 | WEST | SWEETWN3_2_8 (180158) | LCRA TSC_BAKERS_CEDACA_DC | 138 | Bus High Volts | 1.05 | - | 1.0508 | - | - | - | - | -
RSWTW3 | WEST | SWEETWN3_2_8 (180158) | New Sweeteast - Meinan and BitterCreek 345kV Double | 138 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
RSWTW3 | WEST | SWEETWN3_2_8 (180158) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | - | - | - | 1.0554 | - | -
TONCOR | FAR_WEST | SWPORTAP_8 (1099) | L_001013WOLFSS_8-001103SANDHLTA_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0515 | - | - | - | - | -
TONCOR | FAR_WEST | SWPORTLA_8 (1100) | L_001013WOLFSS_8-001103SANDHLTA_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0515 | - | - | - | - | -
ERCOT | SOUTH_CE | SYPBRNCH_S1 (171161) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88178 | - | -
TBREC | SOUTH_CE | TALBRTRIDG (120) | L_003740SLRPRTY_8-003750VOSSLAKE_8C1 | 138 | Bus Low Volts | 0.92 | - | 0.89434 | - | - | - | - | -
TONCOR | FAR_WEST | TARZANSW_8 (1175) | L_001023MIDLNDE_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0571 | - | - | - | - | -
TONCOR | FAR_WEST | TARZANSW_8 (1175) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | 1.0514 | 1.0644 | - | - | - | - | -
TONCOR | FAR_WEST | TARZANSW_8 (1175) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0632 | - | - | - | - | -
TONCOR | FAR_WEST | TARZANSW_8 (1175) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0517 | 1.0642 | - | - | - | - | -
TONCOR | FAR_WEST | TARZANSW_8 (1175) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0607 | 1.0699 | 1.0567 | 1.0601 | 1.0562 | 1.0586 | -
TONCOR | FAR_WEST | TARZANSW_8 (1175) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | 1.0559 | 1.0667 | 1.0511 | 1.0542 | - | 1.0523 | -
TONCOR | FAR_WEST | TARZANSW_8 (1175) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | 1.0539 | 1.0655 | - | 1.0517 | - | - | -
TONCOR | FAR_WEST | TARZANSW_8 (1175) | NORTH ANDREWS - LAMESA - MCKENZIE 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | ARGENTA_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90531 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | E_B_DAVIS_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90445 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | E_CCEC_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91606 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87298 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | E_LGE_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90785 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | E_NEDIN_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91682 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | E_NUECES_B_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89122 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90247 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89444 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9182 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | L_005133ELMCREEK-005380SHAULAC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91625 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9177 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | L_008422I_DUPSW4A-008425INGLESID4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90711 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8688 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | L_008579KATOEN7A-008606GODDARD7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89304 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | L_008606GODDARD7A-888858ARGENTA_POIC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91332 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | L_008659NAISMITH7A-080039LUCERO7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90992 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | M10000271115801 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91631 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | M105311105321 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90781 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | MB100002711580 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91631 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | MB1291012930 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8316 | 0.91152 | -
TAEPTC | SOUTHERN | TATTON4A (8811) | MB1293012910 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89788 | - | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.93977 | - | -
TAEPTC | SOUTHERN | TATTON4A (8811) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.87643 | - | -
RTAYGE | FAR_WEST | TAYGETE_8 (134245) | L_001009YUCCADR_8-011245RIVERVIEW_8C1 | 138 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0506 | -
RTAYGE | FAR_WEST | TAYGETE_8 (134245) | L_011245RIVERVIEW_8-900064Other_134C1 | 138 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0503 | -
RTAYGE | FAR_WEST | TAYGETE_8 (134245) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | - | - | - | - | 1.051 | -
RTAYGE | FAR_WEST | TAYGETE_8 (134245) | L_060385SOLSTICE4A-060393PIGCREEK4AC1 | 138 | Bus High Volts | 1.05 | - | - | 1.0511 | - | - | - | -
RTAYGE | FAR_WEST | TAYGETE_8 (134245) | L_060397GASPADTA4A-900064Other_134C1 | 138 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0502 | -
RTAYGE | FAR_WEST | TAYGETE_8 (134245) | SAND LAKE - SOLSTICE 345 KV DCKT LINE (DOUBLE B TO B) WIN 2027 - FUTURE | 138 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0504 | -
TONCOR | SOUTH_CE | TAYLOR_W1_8 (3673) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87659 | - | -
TONCOR | SOUTH_CE | TAYLOR_W2_8 (3376) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8761 | - | -
TONCOR | SOUTH_CE | TAYLOR1_8 (3658) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88162 | - | -
TONCOR | SOUTH_CE | TAYLORW_T1_8 (13673) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8766 | - | -
TONCOR | SOUTH_CE | TAYLORW_T2_8 (13376) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87613 | - | -
TONCOR | SOUTH_CE | TEAL_5 (3363) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | 0.8896 | - | 0.87595 | 0.83101 | - | 0.8628 | -
TONCOR | SOUTH_CE | TEAL_5 (3363) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.81154 | - | -
TONCOR | SOUTH_CE | TEAL_5 (3363) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89105 | - | -
TONCOR | SOUTH_CE | TEAL_5 (3363) | LCRA TSC_T510_1 | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89574 | - | - | -
TONCOR | SOUTH_CE | TEAL_5 (3363) | LCRA TSC_T510_T512_1 | 345 | Bus Low Volts | 0.9 | - | - | 0.88209 | 0.86944 | 0.88078 | - | -
TONCOR | SOUTH_CE | TEAL_5 (3363) | LCRA TSC_T510_T775 | 345 | Bus Low Volts | 0.9 | - | - | - | 0.88924 | 0.88875 | - | -
TONCOR | SOUTH_CE | TEAL_5 (3363) | LCRATSC_4_WHISVA_HORNSB | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89556 | 0.89413 | - | -
TONCOR | SOUTH_CE | TEAL_5 (3363) | LCRATSC_5_HORNSB_EUCLID | 345 | Bus Low Volts | 0.9 | - | - | - | 0.88733 | 0.88728 | 0.89954 | -
TONCOR | SOUTH_CE | TEAL_5 (3363) | LCRATSC_6_EUCLID_JOHNDU | 345 | Bus Low Volts | 0.9 | - | - | - | 0.86629 | 0.85793 | 0.87567 | -
TONCOR | SOUTH_CE | TEAL_5 (3363) | LCRATSC_7_JOHNDU_ZORN__ | 345 | Bus Low Volts | 0.9 | - | - | - | 0.8874 | 0.89318 | - | -
TONCOR | SOUTH_CE | TEAL_5 (3363) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | 0.93207 | 0.93143 | 0.94825 | -
TONCOR | SOUTH_CE | TEAL_8 (3362) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88298 | - | -
TONCOR | NORTH_CE | TEMP_PEC__5 (3412) | L_003412TEMP_PEC__5-003414TEMP_SS__5C1 | 345 | Bus High Volts | 1.05 | - | 1.0587 | - | - | - | - | -
TONCOR | NORTH_CE | TEMP_PEC__5 (3412) | TEMPLE PECAN CREEK/BELFALLS - TEMPLE_5 (DOUBLE B TO B) | 345 | Bus High Volts | 1.05 | - | 1.0593 | - | - | - | - | -
TONCOR | NORTH_CE | TEMP_SS_R_8 (13415) | L_003415TEMP_SS__8-013415TEMP_SS_R_8C1 | 138 | Bus High Volts | 1.05 | - | - | 1.0544 | 1.0506 | 1.0615 | 1.0509 | -
TONCOR | EAST | TENNCLNY_8 (3281) | JEW-LONG_LAKE-PAL_S_8 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0585 | - | - | - | - | - | -
TONCOR | EAST | TENNCLNY_8 (3281) | L_003279LONGLKTA_8-003280LONGLAKE_8C1 | 138 | Bus High Volts | 1.05 | 1.057 | - | - | - | - | - | -
TONCOR | EAST | TENNCLNY_8 (3281) | L_003280LONGLAKE_8-003284BETO_8C1 | 138 | Bus High Volts | 1.05 | 1.0621 | - | - | - | - | - | -
TONCOR | EAST | TENNCLNY_8 (3281) | L_003281TENNCLNY_8-003284BETO_8C1 | 138 | Bus High Volts | 1.05 | 1.0613 | - | - | - | - | - | -
TONCOR | EAST | TENNCLNY_8 (3281) | L_003281TENNCLNY_8-003499BLAKFTAP_8C1 | 138 | Bus High Volts | 1.05 | 1.0594 | - | - | - | - | - | -
TONCOR | EAST | TENNCLNY_8 (3281) | L_003281TENNCLNY_8-888840SKULLCREEK_POIC1 | 138 | Bus High Volts | 1.05 | - | - | 1.0542 | 1.051 | - | 1.0525 | -
TONCOR | EAST | TENNCLNY_8 (3281) | L_003499BLAKFTAP_8-003509BBRN_OPN_8C1 | 138 | Bus High Volts | 1.05 | 1.0557 | - | - | - | - | - | -
TONCOR | EAST | TENNCLNY_8 (3281) | L_003509BBRN_OPN_8-003510PINOAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0576 | - | - | - | - | - | -
TONCOR | EAST | TENNCLNY_8 (3281) | SKULLCREEK_CON | 138 | Bus High Volts | 1.05 | - | - | 1.0543 | 1.0509 | - | 1.0526 | -
TONCOR | FAR_WEST | TEXHARVY_8 (1221) | L_001221TEXHARVY_8-001226ARUBA1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0703 | - | - | - | - | -
TONCOR | FAR_WEST | TEXHARVY_8 (1221) | L_001222PECKTAP_8-001226ARUBA1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0568 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001023MIDLNDE_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0506 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001159NOANDREW_8-001167MUSTANG_8C1 | 138 | Bus High Volts | 1.05 | - | 1.05 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001163LAMESA_8-010008LAMESA2_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0508 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001170PAULDTAP2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0502 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0532 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0528 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0532 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0552 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0549 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001177TEXMABEE_8-011175BAIRDLAK_8C1 | 138 | Bus High Volts | 1.05 | 1.0575 | 1.0729 | 1.056 | 1.0589 | 1.0529 | 1.0562 | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | 1.0563 | 1.0723 | 1.0548 | 1.0577 | 1.0516 | 1.0549 | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0572 | 1.0734 | 1.0557 | 1.0587 | 1.0526 | 1.0558 | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0687 | - | 1.0504 | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0541 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.056 | 1.072 | 1.0544 | 1.0574 | 1.0513 | 1.0546 | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0505 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_001393DAWSON115_8-900060OTHER_140C1 | 138 | Bus High Volts | 1.05 | - | 1.0501 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0537 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_011167ALKALILK2_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0523 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_011167ALKALILK2_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | 1.0574 | 1.0729 | 1.0559 | 1.0588 | 1.0528 | 1.0561 | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | - | 1.0555 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0531 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | NORTH ANDREWS - LAMESA - MCKENZIE 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0556 | 1.0614 | 1.0513 | 1.059 | 1.0543 | 1.0565 | -
TONCOR | FAR_WEST | TEXMABEE_8 (1177) | NORTH ANDREWS - MCKENZIE 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0526 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMATAP_8 (1179) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | 1.0575 | 1.0737 | 1.056 | 1.059 | 1.0529 | 1.0561 | -
TONCOR | FAR_WEST | TEXMATAP_8 (1179) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0672 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMATAP2_8 (1171) | L_001023MIDLNDE_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.054 | - | - | - | - | -
TONCOR | FAR_WEST | TEXMATAP2_8 (1171) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0624 | - | - | - | - | -
TONCOR | NORTH_CE | THMSAVE1_8 (13696) | L_012442PARKD_2EN8-012446MDLTM2_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.8897 | - | - | 0.89193 | -
TONCOR | NORTH_CE | THMSAVE1_8 (13696) | L_012446MDLTM2_8-012904ENETOH2_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.86856 | 0.89356 | - | 0.87117 | -
TONCOR | NORTH_CE | THOMAVE1_T8 (2840) | L_012442PARKD_2EN8-012446MDLTM2_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.88971 | - | - | 0.89194 | -
TONCOR | NORTH_CE | THOMAVE1_T8 (2840) | L_012446MDLTM2_8-012904ENETOH2_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.86857 | 0.89357 | - | 0.87118 | -
TONCOR | NORTH_CE | THOMAVE2_8 (12889) | L_002903ENET1_8-002909DEEPELM_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0801 | 1.1019 | 1.0947 | 1.0963 | 1.0693 | -
TONCOR | NORTH_CE | THOMAVE2_8 (12889) | L_002906NNET1T_8-002909DEEPELM_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0737 | 1.1085 | 1.101 | 1.1021 | 1.0757 | -
TONCOR | NORTH_CE | THOMAVE2_8 (12889) | L_012441PARKD_1EN8-012445MDLTM1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0536 | - | - | - | - | -
TONCOR | NORTH_CE | THOMAVE2_T8 (2841) | L_002903ENET1_8-002909DEEPELM_8C1 | 138 | Bus High Volts | 1.05 | - | 1.08 | 1.1018 | 1.0947 | 1.0962 | 1.0692 | -
TONCOR | NORTH_CE | THOMAVE2_T8 (2841) | L_002906NNET1T_8-002909DEEPELM_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0736 | 1.1084 | 1.101 | 1.1021 | 1.0756 | -
TONCOR | NORTH_CE | THOMAVE2_T8 (2841) | L_012441PARKD_1EN8-012445MDLTM1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0535 | - | - | - | - | -
TONCOR | FAR_WEST | THRYSIX_P8 (11227) | L_001221TEXHARVY_8-001226ARUBA1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0711 | - | - | - | - | -
TONCOR | FAR_WEST | THRYSIX_P8 (11227) | L_001221TEXHARVY_8-011226PEMBERTN_8C1 | 138 | Bus High Volts | 1.05 | - | 1.072 | - | - | - | - | -
TONCOR | FAR_WEST | THRYSIX_P8 (11227) | L_001222PECKTAP_8-001226ARUBA1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0585 | - | - | - | - | -
TONCOR | FAR_WEST | THRYSIX_P8 (11227) | L_011226PEMBERTN_8-011227THRYSIX_P8C1 | 138 | Bus High Volts | 1.05 | 1.0514 | 1.086 | 1.074 | 1.0702 | 1.067 | 1.0658 | -
RIPTIT | FAR_WEST | TI_SOLAR_8 (135019) | Pre-contingency | 138 | Bus High Volts | 1.05 | - | 1.0597 | - | - | - | - | -
TBREC | NORTH_CE | TIMBERGREN (430) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91548 | - | -
TONCOR | NORTH_CE | TINROOF_8 (3485) | L_003415TEMP_SS__8-003485TINROOF_8C1 | 138 | Bus High Volts | 1.05 | 1.1336 | 1.0757 | 1.126 | 1.106 | 1.1047 | 1.0815 | -
TTNMP | FAR_WEST | TNARROWHCC1 (38481) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0691 | - | - | - | - | -
TTNMP | FAR_WEST | TNARROWHCP1 (38482) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0697 | - | - | - | - | -
TTNMP | FAR_WEST | TNARROWHD_1 (38480) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0711 | - | - | - | - | -
TTNMP | FAR_WEST | TNBCCASTLE1 (38097) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.8993 | 0.87319 | - | -
TTNMP | FAR_WEST | TNBCCASTLE1 (38097) | L_001086BARSTOWNW_8-011105PECONE_P8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88812 | - | -
TTNMP | FAR_WEST | TNBCCASTLE1 (38097) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86726 | 0.84977 | 0.89135 | -
TTNMP | FAR_WEST | TNBLNGLEAC1 (38123) | New Shunt 900021 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88035 | 0.87331 | 0.87921 | -
TTNMP | FAR_WEST | TNBLNGLEAC1 (38123) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.92019 | - | - | - | -
TTNMP | FAR_WEST | TNBLNGLEAM1 (38122) | New Shunt 900021 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88073 | 0.87375 | 0.87965 | -
TTNMP | FAR_WEST | TNBLNGLEAM1 (38122) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.92049 | - | - | - | -
TTNMP | FAR_WEST | TNBLNGLEAT1 (38121) | New Shunt 900021 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88101 | 0.87406 | 0.87996 | -
TTNMP | FAR_WEST | TNBLNGLEAT1 (38121) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.92068 | - | - | - | -
TTNMP | FAR_WEST | TNCAYMUSC_1 (38412) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0631 | - | - | - | - | -
TTNMP | FAR_WEST | TNCAYMUSP_1 (38411) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0617 | - | - | - | - | -
TTNMP | FAR_WEST | TNCAYMUSVQ1 (38410) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.063 | - | - | - | - | -
TTNMP | FAR_WEST | TNCENTRY1_1 (38431) | G_135591BRP_PAVO_BTUBT | 138 | Bus Low Volts | 0.9 | - | - | 0.89933 | - | - | - | -
TTNMP | FAR_WEST | TNCENTRY1_1 (38431) | L_038430TNWHITEBKR1-038445TNGIRVIN__1C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89147 | 0.89209 | 0.89269 | 0.89822 | -
TTNMP | FAR_WEST | TNCENTRY1_1 (38431) | L_038430TNWHITEBKR1-135592BRP_PAVO_8C1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89933 | - | - | - | -
TTNMP | FAR_WEST | TNCENTRY1_1 (38431) | New Girvin - Whitebk Ckt 2 | 138 | Bus Low Volts | 0.9 | - | - | 0.89147 | 0.8921 | 0.89269 | 0.89822 | -
TTNMP | FAR_WEST | TNCENTRY1_1 (38431) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.94026 | 0.94139 | 0.94225 | 0.94519 | -
TTNMP | FAR_WEST | TNCENTRY1_1 (38431) | S_038430TNWHITEBKR11 | 138 | Bus Low Volts | 0.9 | - | 0.89451 | - | - | - | - | -
TTNMP | FAR_WEST | TNCENTRY2_1 (38432) | Pre-contingency | 138 | Bus Low Volts | 0.95 | 0.89721 | 0.87279 | 0.87341 | 0.88209 | 0.87925 | 0.88381 | -
TTNMP | FAR_WEST | TNCOTTNWD_1 (38099) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88295 | - | -
TTNMP | FAR_WEST | TNCOTTNWD_1 (38099) | L_001086BARSTOWNW_8-011105PECONE_P8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89771 | - | -
TTNMP | FAR_WEST | TNCOTTNWD_1 (38099) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87705 | 0.85981 | - | -
TTNMP | FAR_WEST | TNCOTTNWD_1 (38099) | L_038097TNBCCASTLE1-038099TNCOTTNWD_1C1 | 138 | Bus High Volts | 1.05 | 1.055 | - | - | - | - | - | -
TTNMP | FAR_WEST | TNCOYOTSPG1 (38113) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.94898 | - | - | - | -
TTNMP | FAR_WEST | TNETOYAHC_1 (38119) | New Shunt 900021 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89986 | - | -
TTNMP | FAR_WEST | TNETOYAHC_1 (38119) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.93684 | - | - | - | -
TTNMP | FAR_WEST | TNETOYAHM_1 (38118) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.93732 | - | - | - | -
TTNMP | FAR_WEST | TNETOYAHT_1 (38117) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.93734 | - | - | - | -
TTNMP | FAR_WEST | TNFAULKNER1 (38124) | New Shunt 900021 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.84224 | 0.8305 | 0.83689 | -
TTNMP | FAR_WEST | TNFAULKNER1 (38124) | Pre-contingency | 138 | Bus Low Volts | 0.95 | 0.92918 | - | 0.89237 | - | - | - | -
TTNMP | FAR_WEST | TNGRISHAM_1 (38100) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88298 | - | -
TTNMP | FAR_WEST | TNGRISHAM_1 (38100) | L_001086BARSTOWNW_8-011105PECONE_P8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89773 | - | -
TTNMP | FAR_WEST | TNGRISHAM_1 (38100) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87707 | 0.85985 | - | -
TTNMP | FAR_WEST | TNGRISHAM_1 (38100) | L_038097TNBCCASTLE1-038099TNCOTTNWD_1C1 | 138 | Bus High Volts | 1.05 | 1.0547 | - | - | - | - | - | -
TTNMP | FAR_WEST | TNGRISHAMC1 (38101) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88297 | - | -
TTNMP | FAR_WEST | TNGRISHAMC1 (38101) | L_001086BARSTOWNW_8-011105PECONE_P8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89771 | - | -
TTNMP | FAR_WEST | TNGRISHAMC1 (38101) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.87706 | 0.85984 | - | -
TTNMP | FAR_WEST | TNGRISHAMC1 (38101) | L_038097TNBCCASTLE1-038099TNCOTTNWD_1C1 | 138 | Bus High Volts | 1.05 | 1.0547 | - | - | - | - | - | -
TTNMP | FAR_WEST | TNHACKBERY1 (38370) | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 138 | Bus High Volts | 1.05 | - | 1.0711 | - | - | - | - | -
TTNMP | FAR_WEST | TNLONESTAR1 (38190) | L_038190TNLONESTAR1-038191TNBCGWRWNK1C1 | 138 | Bus High Volts | 1.05 | 1.0726 | 1.0503 | 1.0562 | 1.0695 | 1.0685 | 1.074 | -
TTNMP | FAR_WEST | TNREEVSCOT1 (38114) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.949 | - | - | - | -
TTNMP | FAR_WEST | TNSANDLAKE1 (38105) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89757 | - | -
TTNMP | FAR_WEST | TNSANDLAKE1 (38105) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86305 | 0.84326 | 0.88525 | -
TTNMP | FAR_WEST | TNSNDLKCEC1 (38106) | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89409 | - | -
TTNMP | FAR_WEST | TNSNDLKCEC1 (38106) | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.85987 | 0.83954 | 0.88172 | -
TONCOR | NORTH_CE | TOPEKA1_5 (12398) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89484 | - | -
TONCOR | NORTH_CE | TOPEKA1_5 (12398) | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89832 | - | -
TONCOR | NORTH_CE | TOPEKA1_5 (12398) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89876 | - | -
TONCOR | NORTH_CE | TOPEKA1_5 (12398) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8969 | - | -
TONCOR | NORTH_CE | TOPEKA1_5 (12398) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | 0.9481 | 0.94612 | 0.93197 | - | -
TONCOR | NORTH_CE | TOPEKA1_5 (12398) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89251 | - | -
TONCOR | NORTH_CE | TOPEKA1_5 (12398) | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89954 | - | -
TONCOR | NORTH_CE | TOPEKA1_5 (12398) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89192 | - | - | -
TONCOR | SOUTH_CE | TOR_SR1_8 (3714) | Pre-contingency | 138 | Bus High Volts | 1.05 | 1.0629 | - | - | 1.0539 | - | - | -
TONCOR | SOUTH_CE | TOR_SR2_8 (3713) | Pre-contingency | 138 | Bus High Volts | 1.05 | 1.0629 | - | - | 1.0539 | - | - | -
TONCOR | SOUTH_CE | TORTOISE_5 (3717) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.87659 | - | -
TONCOR | FAR_WEST | TOWA_P8 (11069) | L_001097CULBERSON_8-011082MAVRKDRW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89122 | - | - | -
TAEPTC | SOUTHERN | TPCO4A (80475) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8814 | - | -
TAEPTC | SOUTHERN | TPCO4A (80475) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8934 | - | -
TAEPTC | SOUTHERN | TPCO4A (80475) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90721 | - | -
TAEPTC | SOUTHERN | TPCO4B (80476) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8814 | - | -
TAEPTC | SOUTHERN | TPCO4B (80476) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.8934 | - | -
TAEPTC | SOUTHERN | TPCO4B (80476) | SAN_PAT_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90721 | - | -
THNEC1 | EAST | TPLNTSP (6735) | L_003358CENTVILL_8-003394JEWETTA_8C1 | 138 | Bus High Volts | 1.05 | 1.0639 | - | - | - | - | - | -
TAEN | SOUTH_CE | TPOST_LD1 (9278) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94067 | - | - | -
TAEN | SOUTH_CE | TPOST_LD1 (9278) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85354 | - | -
TAEN | SOUTH_CE | TPOST_LD1 (9278) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94411 | - | -
TAEN | SOUTH_CE | TPOST_LD1 (9278) | L_007356L_MARSFO8_1Y-070505P_TRADPO8_1_C1 | 138 | Bus Low Volts | 0.95 | 0.94274 | - | 0.94061 | 0.93764 | - | 0.93679 | -
TAEN | SOUTH_CE | TPOST_LD1 (9278) | PEC_T315_T323 | 138 | Bus Low Volts | 0.95 | 0.94259 | - | 0.94036 | 0.9373 | - | 0.93647 | -
TAEN | SOUTH_CE | TPOST_LD1 (9278) | Pre-contingency | 138 | Bus Low Volts | 0.98 | - | - | - | 0.97891 | - | 0.97794 | -
TAEN | SOUTH_CE | TPOST_LD2 (9281) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94063 | - | - | -
TAEN | SOUTH_CE | TPOST_LD2 (9281) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.8535 | - | -
TAEN | SOUTH_CE | TPOST_LD2 (9281) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94408 | - | -
TAEN | SOUTH_CE | TPOST_LD2 (9281) | L_007356L_MARSFO8_1Y-070505P_TRADPO8_1_C1 | 138 | Bus Low Volts | 0.95 | 0.9427 | - | 0.94058 | 0.9376 | - | 0.93675 | -
TAEN | SOUTH_CE | TPOST_LD2 (9281) | PEC_T315_T323 | 138 | Bus Low Volts | 0.95 | 0.94255 | - | 0.94032 | 0.93726 | - | 0.93643 | -
TAEN | SOUTH_CE | TPOST_LD2 (9281) | Pre-contingency | 138 | Bus Low Volts | 0.98 | - | - | - | 0.97888 | - | 0.9779 | -
TAEN | SOUTH_CE | TPOST_LD3 (9282) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94066 | - | - | -
TAEN | SOUTH_CE | TPOST_LD3 (9282) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85353 | - | -
TAEN | SOUTH_CE | TPOST_LD3 (9282) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.9441 | - | -
TAEN | SOUTH_CE | TPOST_LD3 (9282) | L_007356L_MARSFO8_1Y-070505P_TRADPO8_1_C1 | 138 | Bus Low Volts | 0.95 | 0.94273 | - | 0.9406 | 0.93763 | - | 0.93678 | -
TAEN | SOUTH_CE | TPOST_LD3 (9282) | PEC_T315_T323 | 138 | Bus Low Volts | 0.95 | 0.94258 | - | 0.94035 | 0.93729 | - | 0.93646 | -
TAEN | SOUTH_CE | TPOST_LD3 (9282) | Pre-contingency | 138 | Bus Low Volts | 0.98 | - | - | - | 0.97891 | - | 0.97793 | -
TONCOR | NORTH_CE | TRICRN1_5 (2432) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | 0.94981 | 0.94618 | - | -
TONCOR | NORTH_CE | TRICRN1_5 (2432) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8876 | - | -
TAEN | SOUTH_CE | TRIDGE_MB1 (9190) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.92954 | - | 0.94963 | -
TAEN | SOUTH_CE | TRIDGE_MB1 (9190) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85735 | - | -
TAEN | SOUTH_CE | TRIDGE_MB2 (9191) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.92951 | - | 0.94961 | -
TAEN | SOUTH_CE | TRIDGE_MB2 (9191) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85737 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90266 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | 3WT_002431DESSW1_5_002424DESSW1_8_012431DESSW1_3 C 1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91567 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91938 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91957 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91873 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91736 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91893 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9175 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91939 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91959 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91824 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91816 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | Bus Low Volts | 0.92 | - | - | - | 0.90748 | - | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91588 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91786 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91411 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90709 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91774 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | BLUBIRD_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91701 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | CEDAR HILL - DESOTO/LOOP NINE 345 KV DCKT (DOUBLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91526 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89679 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90094 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | DESOTO - PEBBLE CREEK 138 KV SWITCH (SINGLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90374 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | DRY_CREEK_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91815 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | E_ETCCS_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90987 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | E_FRNYPP_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91644 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | E_FRNYPP_CC2_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91616 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91219 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91019 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | ENNIS - PEBBLE CREEK 138 KV SWITCH (SINGLE B TO B) | 138 | Bus Low Volts | 0.92 | - | 0.91974 | 0.8726 | 0.8652 | 0.86716 | 0.88713 | -
TBREC | NORTH_CE | TRUMBULL8 (221) | G_150023MCSES_UNIT8UN8 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91707 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | G_150112CPSES_UNIT2UU2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91887 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | GLASGOW_CON | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90999 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_000221TRUMBULL8-012344GAMMA_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91443 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91748 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91697 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_001906VENUS_S5-011901BRITNRD1_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91982 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91742 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_002217BATCHLRD_8-002466BIGONION_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90709 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_002217BATCHLRD_8-003159ELROD_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91019 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_002229PEBBLCRK_8-002328RED_OAK1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90208 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_002328RED_OAK1_8-002424DESSW1_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.91812 | 0.89918 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_002427WATMLL_W5-002432TRICRN1_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9147 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_002427WATMLL_W5-002432TRICRN1_5C2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9147 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91718 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90187 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91628 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91655 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_002466BIGONION_5-888877GLASGOW_POIC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91149 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_003159ELROD_5-068091NAVARROC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91305 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_012329SHANKLSW_8-012344GAMMA_8C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9146 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_015200FORBESR1_5-068090SAMSWC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91779 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91602 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91767 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | L_888877GLASGOW_POI-068091NAVARROC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91772 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90358 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90236 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91704 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91244 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90779 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | P7-1_E1>LEG-OUTLAW_ERC | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91973 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.93429 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91775 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.89416 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91905 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | TRIN-SK*ME (DOUBLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91796 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.9171 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90299 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91867 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90956 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91855 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90351 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91841 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89166 | - | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91964 | - | -
TBREC | NORTH_CE | TRUMBULL8 (221) | XFMR-MTCK_8T8-8 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91707 | - | -
TONCOR | FAR_WEST | TUNSTLL_8 (11183) | L_011180ARYOBLUFF_T8-011199RDRUNNER_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.82952 | - | -
TONCOR | FAR_WEST | TUNSTLL_8 (11183) | L_011183TUNSTLL_8-011199RDRUNNER_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.85824 | 0.7699 | - | -
TONCOR | EAST | TYLERGND_5 (3102) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89844 | 0.87167 | - | -
TONCOR | EAST | TYLERGND_5 (3102) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89478 | - | - | -
TONCOR | EAST | TYLERGND_5 (3102) | TRIN-SK*ME (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88398 | - | -
TAEN | SOUTH_CE | UTBALC (9283) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93816 | - | - | -
TAEN | SOUTH_CE | UTBALC (9283) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85511 | - | -
TAEN | SOUTH_CE | UTBALC (9283) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94897 | - | -
TBREC | NORTH_CE | VALLYBRNCH (428) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.90858 | - | -
TAEN | SOUTH_CE | VEGA (9285) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85942 | - | -
TONCOR | NORTH_CE | VENUS (1908) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.86689 | 0.83264 | 0.89345 | -
TONCOR | NORTH_CE | VENUS (1908) | BEPC_306 | 138 | Bus Low Volts | 0.9 | 0.78305 | 0.73045 | - | - | - | - | -
TONCOR | NORTH_CE | VENUS (1908) | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | Bus Low Volts | 0.9 | 0.78302 | 0.72967 | - | - | - | - | -
TONCOR | NORTH_CE | VENUS_N5 (1907) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94248 | - | -
TONCOR | NORTH_CE | VENUS1_8 (1909) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89278 | - | -
TONCOR | NORTH_CE | VENUS1_8 (1909) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.93348 | - | -
TONCOR | NORTH_CE | VENUS1_8 (1909) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8958 | - | -
TONCOR | NORTH_CE | VENUS2_8 (1910) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94322 | - | -
TONCOR | NORTH_CE | VENUS2_8 (1910) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89944 | - | -
TBREC | NORTH_CE | VENUS3_8 (441) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.92 | - | - | 0.90332 | 0.8685 | 0.83422 | 0.89511 | -
TAEPTN | FAR_WEST | VERH4A (60207) | L_060207VERH4A-060209ORIGIN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.90828 | 0.91066 | - | -
TAEPTN | FAR_WEST | VERH4A (60207) | L_060209ORIGIN4A-060716SGSA4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89844 | 0.89949 | - | -
TAEPTN | FAR_WEST | VERH4A (60207) | LCRA TSC_T454_T484 | 138 | Bus High Volts | 1.05 | 1.0547 | - | - | - | - | - | -
TAEPTN | FAR_WEST | VERH4A (60207) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | 0.91785 | - | - | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89591 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89552 | - | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89754 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8864 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89076 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | DESOTO - PEBBLE CREEK 138 KV SWITCH (SINGLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88714 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | L_002217BATCHLRD_8-002466BIGONION_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89754 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | L_002229PEBBLCRK_8-002328RED_OAK1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88553 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | L_002328RED_OAK1_8-002424DESSW1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.89945 | 0.88226 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89636 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89314 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8917 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89873 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | 0.9424 | 0.92509 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88322 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8931 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89869 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89339 | - | -
TONCOR | NORTH_CE | VIOLET_8 (2230) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88105 | - | - | -
TONCOR | SOUTH_CE | VOSSLAKE_8 (3750) | Voss Lake - Sandow 138 kV (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.0555 | - | - | - | - | - | -
TAEN | SOUTH_CE | WALNUTCK (9284) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94597 | - | - | -
TAEN | SOUTH_CE | WALNUTCK (9284) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.86079 | - | -
TAEN | SOUTH_CE | WARREN (9286) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.94107 | - | - | -
TAEN | SOUTH_CE | WARREN (9286) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85424 | - | -
TAEN | SOUTH_CE | WARREN (9286) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94853 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89842 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89858 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89877 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89884 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | 0.88366 | - | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89579 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89819 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8973 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89116 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | BLUBIRD_CON | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89997 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88193 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88616 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | E_FRNYPP_CC1_TRAIN | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89811 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | E_FRNYPP_CC2_TRAIN | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89836 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89144 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89405 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | G_150023MCSES_UNIT8UN8 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89996 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | GLASGOW_CON | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89431 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89923 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89116 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89405 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | L_002427WATMLL_W5-002432TRICRN1_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89644 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | L_002427WATMLL_W5-002432TRICRN1_5C2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89644 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8927 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89848 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89869 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89614 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | L_003159ELROD_5-068091NAVARROC1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89731 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.8996 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89995 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88506 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88626 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89995 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89668 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89198 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | 0.93513 | 0.93048 | 0.91901 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.87361 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | TRIN-RICH (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89996 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | TRIN-SK*ME (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89625 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88561 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89152 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89927 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.88679 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89636 | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | Bus Low Volts | 0.9 | - | - | 0.89731 | 0.86877 | - | - | -
TONCOR | NORTH_CE | WATMLL_W5 (2427) | XFMR-MTCK_8T8-8 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89996 | - | -
TONCOR | NORTH_CE | WAX_N_8 (2320) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88976 | - | -
TONCOR | NORTH_CE | WAX_NW_8 (2309) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.88541 | 0.84944 | - | -
TONCOR | NORTH_CE | WAX_NW_8 (2309) | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89572 | - | -
TONCOR | NORTH_CE | WAX_NW_8 (2309) | L_002305AIRPRD_T8-002307MDLTHTXI1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8996 | - | -
TONCOR | NORTH_CE | WAX_NW_8 (2309) | L_002308MDLTH_S_8-002309WAX_NW_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89788 | - | -
TONCOR | NORTH_CE | WAX_PMP1_8 (2319) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87985 | - | -
TONCOR | NORTH_CE | WAX_PMP1_8 (2319) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94798 | - | -
TONCOR | NORTH_CE | WAX_PMP2_8 (2315) | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88414 | - | -
TONCOR | NORTH_CE | WEBB1_5 (1911) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89922 | - | -
TONCOR | NORTH_CE | WEBB1_5 (1911) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94167 | - | -
TONCOR | NORTH_CE | WEBB3_5 (1904) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89502 | - | -
TONCOR | NORTH_CE | WEBB3_5 (1904) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93388 | - | -
TONCOR | NORTH_CE | WEBB3_5 (1904) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89964 | - | -
TONCOR | NORTH_CE | WEBB3_5 (1904) | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89642 | - | -
TAEN | SOUTH_CE | WEBBERSOL (9287) | AEN_AU-DG¦DL_2013 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.92435 | - | -
TAEN | SOUTH_CE | WEBBERSOL (9287) | AEN_DL-AU¦LP_2013 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94952 | - | -
TAEN | SOUTH_CE | WEBBERSOL (9287) | AEN_LP-AU¦DL_2013 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94408 | - | -
TAEN | SOUTH_CE | WEBBERSOL (9287) | AEN_LY-FPP:CIS-HO | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94732 | - | -
TAEN | SOUTH_CE | WEBBERSOL (9287) | AEN_LY-FPP¦CIS | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94041 | - | -
TAEN | SOUTH_CE | WEBBERSOL (9287) | G_RIO_TRAIN | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94981 | - | -
TAEN | SOUTH_CE | WEBBERSOL (9287) | J5LCA1C1_B | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94973 | - | -
TAEN | SOUTH_CE | WEBBERSOL (9287) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.87213 | - | -
TAEN | SOUTH_CE | WEBBERSOL (9287) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.9133 | - | -
TAEN | SOUTH_CE | WEBBERSOL (9287) | L_005133ELMCREEK-005380SHAULAC1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94901 | - | -
TAEN | SOUTH_CE | WEBBERSOL (9287) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94961 | - | -
TAEN | SOUTH_CE | WEBBERSOL (9287) | L_009045DUNLAP8-009328AUSTROP8C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.93925 | - | -
TAEN | SOUTH_CE | WEBBERSOL (9287) | LCRA TSC_T185_T246 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94998 | - | -
TAEN | SOUTH_CE | WEBBERSOL (9287) | LCRA TSC_T255_TAE3121_1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.93403 | - | -
TAEN | SOUTH_CE | WEBBERSOL (9287) | LCRATSC_6_EUCLID_JOHNDU | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94122 | - | -
TAEN | SOUTH_CE | WEBBERSOL (9287) | Pre-contingency | 138 | Bus Low Volts | 0.98 | - | - | - | - | 0.9682 | - | -
TAEN | SOUTH_CE | WELLSB_LD1 (9288) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.92666 | - | 0.94563 | -
TAEN | SOUTH_CE | WELLSB_LD1 (9288) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85197 | - | -
TAEN | SOUTH_CE | WELLSB_LD1 (9288) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94619 | - | -
TAEN | SOUTH_CE | WELLSB_LD1 (9288) | LCRATSC_6_EUCLID_JOHNDU | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94892 | - | -
TAEN | SOUTH_CE | WELLSB_LD2 (9289) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.92666 | - | 0.94563 | -
TAEN | SOUTH_CE | WELLSB_LD2 (9289) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85197 | - | -
TAEN | SOUTH_CE | WELLSB_LD2 (9289) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94619 | - | -
TAEN | SOUTH_CE | WELLSB_LD2 (9289) | LCRATSC_6_EUCLID_JOHNDU | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94892 | - | -
TONCOR | NORTH_CE | WESTRIDGE1_8 (2380) | L_002370COLLINSS1_8-002380WESTRIDGE1_8C1 | 138 | Bus Low Volts | 0.9 | 0.87281 | - | 0.86569 | 0.86005 | 0.86024 | 0.86099 | -
TONCOR | FAR_WEST | WFCAMPTA_9 (1240) | L_011242CRTNYCRK_8-060792ATHEY4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.89351 | 0.86981 | 0.83817 | 0.85495 | -
TAEN | SOUTH_CE | WHELESS (9291) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93924 | - | - | -
TAEN | SOUTH_CE | WHELESS (9291) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85529 | - | -
TAEN | SOUTH_CE | WHELESS (9291) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94845 | - | -
TAEPTC | SOUTHERN | WHITEPT4A (8961) | E_INGLCOSW_CC1_TRAIN | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91967 | - | -
TAEPTC | SOUTHERN | WHITEPT4A (8961) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91321 | - | -
TAEPTC | SOUTHERN | WHITEPT7A (8956) | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | Bus Low Volts | 0.92 | - | - | - | - | 0.90059 | - | -
TBREC | NORTH_CE | WHITNEY5 (240) | L_000240WHITNEY5-000246BOSQUESW5C1 | 345 | Bus High Volts | 1.05 | - | 1.0716 | 1.0528 | 1.0513 | 1.0504 | 1.0691 | -
TAEN | SOUTH_CE | WI138_CAP (9018) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93584 | - | - | -
TAEN | SOUTH_CE | WI138_CAP (9018) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85468 | - | -
TAEN | SOUTH_CE | WI138_CAP (9018) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94908 | - | -
TAEN | SOUTH_CE | WILIAMSN (9295) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | Bus Low Volts | 0.95 | - | - | - | 0.93581 | - | - | -
TAEN | SOUTH_CE | WILIAMSN (9295) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.85465 | - | -
TAEN | SOUTH_CE | WILIAMSN (9295) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94905 | - | -
TONCOR | FAR_WEST | WILLOWVAL_5 (1302) | C5-WETT-2_B | 345 | Bus High Volts | 1.05 | 1.0583 | 1.0573 | 1.0576 | - | - | - | -
TONCOR | FAR_WEST | WILLOWVAL_5 (1302) | C5-WETT-2_B-1 | 345 | Bus High Volts | 1.05 | - | - | - | 1.0555 | - | - | -
TONCOR | FAR_WEST | WILLOWVAL_5 (1302) | C5-WETT-2_B-2 | 345 | Bus High Volts | 1.05 | - | - | - | 1.0556 | - | - | -
TONCOR | FAR_WEST | WILLOWVAL_5 (1302) | L_059900LONG_DRAW-059905FARADAYC1 | 345 | Bus High Volts | 1.05 | 1.0584 | 1.0572 | 1.0578 | 1.0556 | - | - | -
TONCOR | NORTH_CE | WILMER1_8 (3083) | L_002429WATMLL_8-003083WILMER1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | 0.77933 | 0.76518 | 0.8225 | -
TONCOR | NORTH_CE | WILMER1_8 (3083) | L_002434SGVLSW1_8-003076SGVL1_8C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89795 | - | -
TONCOR | NORTH_CE | WILSNCRK_P8 (2366) | L_000675ROCKHILL-002380WESTRIDGE1_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0507 | - | - | - | - | -
TONCOR | NORTH_CE | WILSNCRK_P8 (2366) | L_002370COLLINSS1_8-002380WESTRIDGE1_8C1 | 138 | Bus Low Volts | 0.9 | 0.88958 | - | 0.88269 | 0.87738 | 0.87744 | 0.87817 | -
TLCRA | SOUTH_CE | WINCHES (9042) | AEN_FPP-WH.DC | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94647 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | AEN_LY-FPP:CIS-HO | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94542 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | AEN_LY-FPP¦CIS | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93171 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | AEN_P7 FPP-LP.DC_1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94957 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93599 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94804 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | DVCPA1C21B_1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94916 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | G_RIO_TRAIN | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94923 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | Bus Low Volts | 0.95 | - | - | - | 0.9427 | - | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | J5LCA1C1_B | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94916 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.83427 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | L_005068CACHENA-005133ELMCREEKC2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.89732 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94879 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | L_005133ELMCREEK-005380SHAULAC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93301 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | L_005915SO_TEX__345A-008715RADIANT7AC1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94972 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.93356 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | LCRA TSC_T255_TAE3121_1 | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.92124 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | P7-1_E1>>T1839X2_ERC | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94946 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | P7-1_E1>>T3944Z_ERC | 345 | Bus Low Volts | 0.95 | - | - | - | - | 0.94755 | - | -
TLCRA | SOUTH_CE | WINCHES (9042) | Pre-contingency | 345 | Bus Low Volts | 0.98 | - | - | - | - | 0.97213 | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | 3WT_001302WILLOWVAL_5_001301WILLOWVAL_8_018537WILLOWVAL_3 C 3 | 138 | Bus High Volts | 1.05 | - | 1.0537 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001163LAMESA_8-001307KEYLYNTE_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0601 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001163LAMESA_8-010008LAMESA2_8C1 | 138 | Bus High Volts | 1.05 | 1.0548 | 1.0655 | 1.0509 | 1.0562 | 1.051 | 1.0528 | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001163LAMESA_8-011363HARDYMGN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0517 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001171TEXMATAP2_8-001172MIDLD349_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001171TEXMATAP2_8-011279GODDARD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0511 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001172MIDLD349_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0516 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001175TARZANSW_8-001195MARNSFLD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0537 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001175TARZANSW_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0538 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001177TEXMABEE_8-011175BAIRDLAK_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0558 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001179TEXMATAP_8-001200MARNSFLD1_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0555 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001179TEXMATAP_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0559 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001181ANDHWY87_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0576 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001183MIDCONW_8-011299MOCKNGBD2_T8C1 | 138 | Bus High Volts | 1.05 | - | 1.0535 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001195MARNSFLD2_T8-011145KELTONWND_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0525 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001200MARNSFLD1_T8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0553 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001301WILLOWVAL_8-001308GAILLYNT_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0624 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001307KEYLYNTE_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0605 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001308GAILLYNT_8-011615ONC900120_TAPC1 | 138 | Bus High Volts | 1.05 | - | 1.0607 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_001355BUZZDRAW_8-011363HARDYMGN_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0526 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_010008LAMESA2_8-018880JIMPAYNE_8C1 | 138 | Bus High Volts | 1.05 | 1.0517 | 1.0623 | - | 1.0531 | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_011145KELTONWND_8-011179S_CURTIS_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0521 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_011167ALKALILK2_8-011169MCKENZIEDR_8C1 | 138 | Bus High Volts | 1.05 | - | 1.052 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_011167ALKALILK2_8-011206DILLON_P8C1 | 138 | Bus High Volts | 1.05 | - | 1.0513 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | L_011175BAIRDLAK_8-011177FASKENC_8C1 | 138 | Bus High Volts | 1.05 | - | 1.0558 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | LAMESA - BUZZARD DRAW 138 KV LINE 2018 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0517 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | LAMESA - BUZZARD DRAW 69/138 KV DCKT LINE 2019 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0532 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | MCKENZIE DR - MIDLAND COUNTY NW/MIDLAND EAST 2025 SUM - FUTURE (DOUBLE B TO B) G | 138 | Bus High Volts | 1.05 | 1.0627 | 1.0846 | 1.0613 | 1.0609 | 1.0576 | 1.0602 | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | MIDLAND COUNTY NW - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.058 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | MIDLAND COUNTY NW - MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0575 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (SINGLE B TO B) F | 138 | Bus High Volts | 1.05 | - | 1.0543 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0532 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | NORTH ANDREWS - MCKENZIE 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0523 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | WILLOW VALLEY - LAMESA 138 KV (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0602 | - | - | - | - | -
TGSEC | FAR_WEST | WLAMESA_8 (9420) | WILLOW VALLEY TRANSFORMER 1 (SINGLE B TO B) | 138 | Bus High Volts | 1.05 | - | 1.0537 | - | - | - | - | -
TONCOR | NORTH_CE | WLEVEE1_5 (2398) | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89467 | - | -
TONCOR | NORTH_CE | WLEVEE1_5 (2398) | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89814 | - | -
TONCOR | NORTH_CE | WLEVEE1_5 (2398) | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89856 | - | -
TONCOR | NORTH_CE | WLEVEE1_5 (2398) | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89675 | - | -
TONCOR | NORTH_CE | WLEVEE1_5 (2398) | Pre-contingency | 345 | Bus Low Volts | 0.95 | - | - | 0.94779 | 0.94601 | 0.93184 | - | -
TONCOR | NORTH_CE | WLEVEE1_5 (2398) | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89224 | - | -
TONCOR | NORTH_CE | WLEVEE1_5 (2398) | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | Bus Low Volts | 0.9 | - | - | - | - | 0.89936 | - | -
TONCOR | NORTH_CE | WLEVEE1_5 (2398) | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | Bus Low Volts | 0.9 | - | - | - | 0.89158 | - | - | -
TONCOR | NORTH_CE | WNET1_8 (2874) | EAST LEVEE-WEST NETWORK-INDUSTRIAL DCKT (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | - | - | - | - | - | 1.0624 | -
TONCOR | NORTH_CE | WNET2_8 (2875) | INDUSTRIAL-WEST NETWORK-EAST LEVEE DCKT (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.1403 | - | 1.1518 | 1.1553 | 1.1516 | 1.0641 | -
TONCOR | NORTH_CE | WNET3_8 (2876) | INDUSTRIAL-SARGENT RD DCKT (DOUBLE B TO B) A | 138 | Bus High Volts | 1.05 | 1.0638 | - | 1.0666 | 1.0671 | 1.0688 | - | -
TONCOR | NORTH_CE | WNET3_8 (2876) | INDUSTRIAL-WEST NETWORK-EAST LEVEE DCKT (DOUBLE B TO B) | 138 | Bus High Volts | 1.05 | 1.1403 | - | 1.1518 | 1.1553 | 1.1516 | 1.0641 | -
TONCOR | NORTH_CE | WNET3_8 (2876) | L_002876WNET3_8-002974INDUST_W8C1 | 138 | Bus High Volts | 1.05 | 1.0611 | - | 1.0662 | 1.0618 | 1.0603 | - | -
TAEPTN | FAR_WEST | WOLFBERR2A (60375) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.90777 | 0.88438 | 0.88968 | -
TAEPTN | FAR_WEST | WOLFBERR2A (60375) | L_006536BIGLAKE4B-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | - | 0.91983 | - | -
TAEPTN | FAR_WEST | WOLFBERR2A (60375) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.8918 | 0.87587 | 0.89165 | -
TAEPTN | FAR_WEST | WOLFBERR2A (60375) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88884 | 0.87217 | 0.88808 | -
TAEPTN | FAR_WEST | WOLFBERR2A (60375) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88297 | 0.86616 | 0.88229 | -
TAEPTN | FAR_WEST | WOLFBERR2A (60375) | L2020944-A | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88891 | 0.8723 | 0.88814 | -
TONCOR | FAR_WEST | WOLFCAMP_9 (1241) | L_011242CRTNYCRK_8-060792ATHEY4AC1 | 138 | Bus Low Volts | 0.9 | - | - | 0.88904 | 0.86479 | 0.83268 | 0.84957 | -
TONCOR | FAR_WEST | WOLFCAMP2_T8 (11262) | L_011242CRTNYCRK_8-060792ATHEY4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.8784 | 0.89408 | -
TGSEC | FAR_WEST | WOLFCAMP4A (60799) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91025 | 0.84929 | 0.82909 | 0.84535 | -
TSTEC | COAST | WRBRTN8 (5607) | E_NUECES_B_CC1_TRAIN | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89049 | - | -
TSTEC | COAST | WRBRTN8 (5607) | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89456 | - | -
TSTEC | COAST | WRBRTN8 (5607) | L_005068CACHENA-005133ELMCREEKC2 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.88773 | - | -
TSTEC | COAST | WRBRTN8 (5607) | L_005607WRBRTN8-008172VICTORIA4AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.86575 | - | -
TSTEC | COAST | WRBRTN8 (5607) | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.87976 | - | -
TSTEC | COAST | WRBRTN8 (5607) | L_008579KATOEN7A-008606GODDARD7AC1 | 138 | Bus Low Volts | 0.9 | - | - | - | - | 0.89781 | - | -
TSTEC | COAST | WRBRTN8 (5607) | Pre-contingency | 138 | Bus Low Volts | 0.95 | - | - | - | - | 0.94137 | - | -
TONCOR | NORTH_CE | WYLIE_P8 (2693) | L_002472ROYSE_N_8-002693WYLIE_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0693 | 1.0622 | - | -
ERCC | NORTH_CE | WYLIE_RC (6881) | L_002472ROYSE_N_8-002693WYLIE_P8C1 | 138 | Bus High Volts | 1.05 | - | - | - | 1.0693 | 1.0622 | - | -
TONCOR | FAR_WEST | YOSEMT_8 (23858) | Rockhound-Blue Acres & Grey Well Draw 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | 1.0724 | 1.0926 | - | - | - | - | -
TONCOR | FAR_WEST | YOSEMT_8 (23858) | Rockhound-Blue Acres 138 kV ONCOR WTIP RPG Submittal | 138 | Bus High Volts | 1.05 | 1.074 | 1.0923 | - | - | - | - | -
TAEPTN | WEST | YUCCA4A (6036) | L_006036YUCCA4A-006525ESMERALD4AC1 | 138 | Bus Low Volts | 0.92 | 0.81441 | - | 0.73025 | - | - | - | -
TAEPTN | WEST | YUCCA4A (6036) | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | Bus Low Volts | 0.92 | - | - | 0.91485 | 0.88568 | 0.85949 | 0.86419 | -
TAEPTN | WEST | YUCCA4A (6036) | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89888 | 0.88444 | 0.90041 | -
TAEPTN | WEST | YUCCA4A (6036) | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.8961 | 0.88095 | 0.89685 | -
TAEPTN | WEST | YUCCA4A (6036) | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | Bus Low Volts | 0.92 | - | - | - | 0.88914 | 0.87542 | 0.89136 | -
TAEPTN | WEST | YUCCA4A (6036) | L2020944-A | 138 | Bus Low Volts | 0.92 | - | - | - | 0.89618 | 0.88107 | 0.89691 | -

## Branches
Owner | Zone From | Zone To | WZs | Element | Contingency | From Bus kV | To Bus kV | Category | Limit | 2026sum% | 2027min% | 2027sum% | 2029sum% | 2030sum% | 2030sum_EHV% | Notes
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | AGNESSWTCH ( 511) -> WTHFRDSS_8 ( 1592) CKT 1 | BEPC_006 | 138 | 138 | Branch Amp | 866.0253 | - | - | - | - | 122.3277 | 109.2751 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | AIRPRD_T8 ( 2305) -> MDLTHTXI1_8 ( 2307) CKT 1 | L_000223SAINTPAUL-000404JESSICAC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.2522 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | AIRPRD_T8 ( 2305) -> MDLTHTXI1_8 ( 2307) CKT 1 | L_000404JESSICA-000419LILLIAN8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.9463 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLENSTR (500091) -> ALLENSWS2_8 (12513) CKT 2 | ALLEN SW - PLANO TENNYSON 345 KV & ALLEN SW - RENNER 345 KV (DOUBLE B TO B) | 138 | 1 | Branch MVA | 716 | - | - | - | 107.1794 | 116.7433 | 109.7383 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLENSTR (500091) -> ALLENSWS2_8 (12513) CKT 2 | L_002514ALLENSW2_5-002522PL_TENNY_5C1 | 138 | 1 | Branch MVA | 716 | - | - | - | 106.5204 | 116.0775 | 108.6514 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLENSTR (500091) -> ALLENSWS2_8 (12513) CKT 2 | NORTHWEST CARROLLTON - RENNER 345 KV & PLANO TENNYSON - ALLEN SW 345 KV (DOUBLE B TO B) | 138 | 1 | Branch MVA | 716 | - | - | - | 106.9518 | 115.9731 | 108.605 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLENSW2_5 ( 2514) -> ALLENSTR (500091) CKT 2 | ALLEN SW - PLANO TENNYSON 345 KV & ALLEN SW - RENNER 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 716 | - | - | - | 108.5859 | 118.1585 | 111.0554 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLENSW2_5 ( 2514) -> ALLENSTR (500091) CKT 2 | L_002514ALLENSW2_5-002522PL_TENNY_5C1 | 345 | 1 | Branch MVA | 716 | - | - | - | 107.5173 | 117.4837 | 110.2207 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLENSW2_5 ( 2514) -> ALLENSTR (500091) CKT 2 | NORTHWEST CARROLLTON - RENNER 345 KV & PLANO TENNYSON - ALLEN SW 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 716 | - | - | - | 108.1761 | 117.4339 | 110.1875 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLENSW2_5 ( 2514) -> PL_TENNY_5 ( 2522) CKT 1 | 3WT_002514ALLENSW2_5_012513ALLENSWS2_8_012512ALLENSW2_3 C 2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2018 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLENSW2_5 ( 2514) -> PL_TENNY_5 ( 2522) CKT 1 | L_002512ALLENSW2_8-012513ALLENSWS2_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2018 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLENSWS2_8 (12513) -> ALLENSW2_8 ( 2512) CKT 1 | ALLEN SW - PLANO TENNYSON 345 KV & ALLEN SW - RENNER 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 3200.5283 | - | - | - | - | 109.5273 | 101.9728 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLENSWS2_8 (12513) -> ALLENSW2_8 ( 2512) CKT 1 | L_002514ALLENSW2_5-002522PL_TENNY_5C1 | 138 | 138 | Branch Amp | 3200.5283 | - | - | - | 100.0179 | 108.6548 | 101.1452 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLENSWS2_8 (12513) -> ALLENSW2_8 ( 2512) CKT 1 | NORTHWEST CARROLLTON - RENNER 345 KV & PLANO TENNYSON - ALLEN SW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 3200.5283 | - | - | - | - | 108.9141 | 101.1787 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLISON_T8 ( 1568) -> KRUM ( 670) CKT 1 | BASECAMP - BENNETT RD SW 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.1665 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLISON_T8 ( 1568) -> KRUM ( 670) CKT 1 | BEPC_005_1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0751 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLISON_T8 ( 1568) -> KRUM ( 670) CKT 1 | BEPC_242 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9959 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLISON_T8 ( 1568) -> KRUM ( 670) CKT 1 | EAGLE MOUNTAIN - HICKS/BENNETT 138 KV (DOUBLE B TO B) A NEWLOAD | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.0906 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLISON_T8 ( 1568) -> KRUM ( 670) CKT 1 | L_000541RENO-000595KEETERC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0639 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLISON_T8 ( 1568) -> KRUM ( 670) CKT 1 | L_000579JCKCNTY8-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9809 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLISON_T8 ( 1568) -> KRUM ( 670) CKT 1 | L_000595KEETER-000596COTTONDALEC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3966 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLISON_T8 ( 1568) -> KRUM ( 670) CKT 1 | L_000596COTTONDALE-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9831 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLISON_T8 ( 1568) -> KRUM ( 670) CKT 1 | L_001570RHOME_8-001594DECATUR_T8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.2341 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLISON_T8 ( 1568) -> KRUM ( 670) CKT 1 | L_001582BENNETT_8-001594DECATUR_T8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.2329 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLISON_T8 ( 1568) -> KRUM ( 670) CKT 1 | RAMHORN - HICKS & BASE CAMP - BENNET DC 345 &138 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.9324 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLISON_T8 ( 1568) -> KRUM ( 670) CKT 1 | RAMHORN - HICKS 345 AND BASE CAMP - BENNET 138 (DOUBLE B TO B) CKT 2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.7379 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLISON_T8 ( 1568) -> KRUM ( 670) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (COMMON TOWER) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.9068 | 101.7729 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLISON_T8 ( 1568) -> KRUM ( 670) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.7379 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALLISON_T8 ( 1568) -> KRUM ( 670) CKT 1 | WISE COUNTY (BEC) - ALVORD/BRIDGEPORT(BEC) (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.9428 | - | -
TSTEC | COAST | COAST | COAST, COAST | ALOESUB9 ( 5606) -> WARBURTONSW9 ( 5605) CKT 1 | L_005502RAYBURN8-005680LOOP463SUB8C1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 105.6013 | - | -
TSTEC | COAST | COAST | COAST, COAST | ALOESUB9 ( 5606) -> WARBURTONSW9 ( 5605) CKT 1 | L_005607WRBRTN8-008172VICTORIA4AC1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | 148.8937 | 189.2148 | 134.2034 | -
TSTEC | COAST | COAST | COAST, COAST | ALOESUB9 ( 5606) -> WARBURTONSW9 ( 5605) CKT 1 | L_005680LOOP463SUB8-008172VICTORIA4AC1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 102.0282 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALVARADO1_8 ( 2297) -> GRIFFTH_P8 ( 1905) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | 116.3792 | 128.1623 | 155.8316 | 194.3474 | 208.1773 | 177.8365 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALVARADO1_8 ( 2297) -> GRIFFTH_P8 ( 1905) CKT 1 | BEPC_306 | 138 | 138 | Branch Amp | 861.8416 | 161.5349 | 204.0023 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALVARADO1_8 ( 2297) -> GRIFFTH_P8 ( 1905) CKT 1 | CLEBURNE-BURLESON 138 KV (SINGLE B TO B) B WILSHIRE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.5678 | 109.6837 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALVARADO1_8 ( 2297) -> GRIFFTH_P8 ( 1905) CKT 1 | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | 138 | Branch Amp | 861.8416 | 134.4796 | 195.5299 | 216.4345 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALVARADO1_8 ( 2297) -> GRIFFTH_P8 ( 1905) CKT 1 | L_000442RAILPORT-001908VENUSC1 | 138 | 138 | Branch Amp | 861.8416 | 136.7426 | 195.7944 | 220.7579 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALVARADO1_8 ( 2297) -> GRIFFTH_P8 ( 1905) CKT 1 | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | 138 | Branch Amp | 861.8416 | 161.54 | 204.2178 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALVARADO1_8 ( 2297) -> GRIFFTH_P8 ( 1905) CKT 1 | L_002203MNTVALLY_P8-002210JOSHUA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.1349 | 108.2794 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALVARADO1_8 ( 2297) -> GRIFFTH_P8 ( 1905) CKT 1 | L_002210JOSHUA_8-002279CLEBRNSW_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.671 | 109.8082 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALVARADO1_8 ( 2297) -> GRIFFTH_P8 ( 1905) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4237 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ALVARADO1_8 ( 2297) -> GRIFFTH_P8 ( 1905) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5911 | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN_POI_8 (42110) -> ANGLTN26T1_8 (42111) CKT 26 | L_042050CLUTE___B138-043150RIWOOD_X82B8C82 | 138 | 138 | Branch Amp | 1916.1333 | - | - | - | - | 103.0249 | 107.7009 | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN_POI_8 (42110) -> ANGLTN26T1_8 (42111) CKT 26 | L_042110ANGLTN_POI_8-043150RIWOOD_X82B8C82 | 138 | 138 | Branch Amp | 1916.1333 | - | - | - | - | 103.2334 | 107.9104 | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN_POI_8 (42110) -> RIWOOD_X82B8 (43150) CKT 82 | L_042030SAMARI__B138-042050CLUTE___B138C26 | 138 | 138 | Branch Amp | 1175.6189 | 104.5418 | - | - | 109.8404 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN_POI_8 (42110) -> RIWOOD_X82B8 (43150) CKT 82 | L_042030SAMARI__B138-042110ANGLTN_POI_8C&1-MS | 138 | 138 | Branch Amp | 1175.6189 | 104.5563 | - | - | 109.855 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN_POI_8 (42110) -> RIWOOD_X82B8 (43150) CKT 82 | L_042100HUDSON_POI_8-042960MUSTNG_S04_8C04 | 138 | 138 | Branch Amp | 1175.6189 | 101.1994 | - | - | - | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN_POI_8 (42110) -> RIWOOD_X82B8 (43150) CKT 82 | L_042960MUSTNG_S04_8-043500WEBSTR_B138AC&1-MS | 138 | 138 | Branch Amp | 1175.6189 | 100.0674 | - | - | 103.114 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN_POI_8 (42110) -> RIWOOD_X82B8 (43150) CKT 82 | L_888849CLUTCH_CITY_POI-042960MUSTNG_S04_8C04 | 138 | 138 | Branch Amp | 1175.6189 | - | - | - | 104.2232 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN_POI_8 (42110) -> RIWOOD_X82B8 (43150) CKT 82 | P7-1_E1>>T0405 | 138 | 138 | Branch Amp | 1175.6189 | 100.1862 | - | - | 102.5652 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN_POI_8 (42110) -> RIWOOD_X82B8 (43150) CKT 82 | P7-1_E1>>T0463 | 138 | 138 | Branch Amp | 1175.6189 | 100.1145 | - | - | 103.1488 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN_POI_8 (42110) -> RIWOOD_X82B8 (43150) CKT 82 | P7-1_E1>>T0493 | 138 | 138 | Branch Amp | 1175.6189 | - | - | - | 102.8889 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN_POI_8 (42110) -> RIWOOD_X82B8 (43150) CKT 82 | Pre-contingency | 138 | 138 | Amps | 903.6786 | - | - | - | - | 142.8461 | 149.4488 | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN26T1_8 (42111) -> SAMARI__B138 (42030) CKT 26 | L_042050CLUTE___B138-043150RIWOOD_X82B8C82 | 138 | 138 | Branch Amp | 1171.4352 | 106.0206 | - | - | 111.4075 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN26T1_8 (42111) -> SAMARI__B138 (42030) CKT 26 | L_042100HUDSON_POI_8-042960MUSTNG_S04_8C04 | 138 | 138 | Branch Amp | 1171.4352 | 104.4112 | - | - | - | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN26T1_8 (42111) -> SAMARI__B138 (42030) CKT 26 | L_042110ANGLTN_POI_8-043150RIWOOD_X82B8C82 | 138 | 138 | Branch Amp | 1171.4352 | 106.3426 | - | - | 111.741 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN26T1_8 (42111) -> SAMARI__B138 (42030) CKT 26 | L_042110ANGLTN_POI_8-043380W_COL__POI_8C&1-MS | 138 | 138 | Branch Amp | 1171.4352 | - | - | - | 100.4518 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN26T1_8 (42111) -> SAMARI__B138 (42030) CKT 26 | L_042570ARCHER_POI_8-044430MANVEL_S26_8C26 | 138 | 138 | Branch Amp | 1171.4352 | - | - | - | 102.231 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN26T1_8 (42111) -> SAMARI__B138 (42030) CKT 26 | L_042940MONSAN_POI_8-043070PETSON_X04B8C04 | 138 | 138 | Branch Amp | 1171.4352 | 101.0589 | - | - | - | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN26T1_8 (42111) -> SAMARI__B138 (42030) CKT 26 | L_042960MUSTNG_S04_8-043500WEBSTR_B138AC&1-MS | 138 | 138 | Branch Amp | 1171.4352 | 103.2426 | - | - | 106.386 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN26T1_8 (42111) -> SAMARI__B138 (42030) CKT 26 | L_043070PETSON_X04B8-044890SNUG___POI_8C04 | 138 | 138 | Branch Amp | 1171.4352 | 101.7452 | - | - | - | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN26T1_8 (42111) -> SAMARI__B138 (42030) CKT 26 | L_888849CLUTCH_CITY_POI-042960MUSTNG_S04_8C04 | 138 | 138 | Branch Amp | 1171.4352 | - | - | - | 107.531 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN26T1_8 (42111) -> SAMARI__B138 (42030) CKT 26 | P7-1_E1>>T0405 | 138 | 138 | Branch Amp | 1171.4352 | 103.3652 | - | - | 105.8194 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN26T1_8 (42111) -> SAMARI__B138 (42030) CKT 26 | P7-1_E1>>T0463 | 138 | 138 | Branch Amp | 1171.4352 | 103.2912 | - | - | 106.4219 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN26T1_8 (42111) -> SAMARI__B138 (42030) CKT 26 | P7-1_E1>>T0493 | 138 | 138 | Branch Amp | 1171.4352 | 103.0129 | - | - | 106.1535 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ANGLTN26T1_8 (42111) -> SAMARI__B138 (42030) CKT 26 | P7-1_E1>>T2626D | 138 | 138 | Branch Amp | 1171.4352 | - | - | - | 102.4269 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ANNASW_5 ( 2373) -> COLLINSS1_5 ( 2372) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 2999.8782 | - | - | - | - | 100.4779 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ANNASW_5 ( 2373) -> COLLINSS1_5 ( 2372) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 2999.8782 | - | - | - | - | 100.4274 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ANNASW_5 ( 2373) -> COLLINSS1_5 ( 2372) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 2999.8782 | - | - | - | - | 102.0577 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ANNASW_5 ( 2373) -> COLLINSS1_5 ( 2372) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 2999.8782 | - | - | - | - | 102.165 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ANNASW_5 ( 2373) -> COLLINSS1_5 ( 2372) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 2999.8782 | - | - | - | - | 101.9976 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ANNASW_5 ( 2373) -> COLLINSS1_5 ( 2372) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 2999.8782 | - | - | - | - | 102.2654 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ANNASW_5 ( 2373) -> COLLINSS1_5 ( 2372) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 2999.8782 | - | - | - | - | 104.3995 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ANNASW_5 ( 2373) -> COLLINSS1_5 ( 2372) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 2999.8782 | - | - | - | 101.4984 | 108.6157 | 102.0828 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ANNASW_5 ( 2373) -> COLLINSS1_5 ( 2372) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 2999.8782 | - | - | - | - | 104.3639 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ANNASW_5 ( 2373) -> COLLINSS1_5 ( 2372) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 2999.8782 | - | - | - | 101.4579 | 108.5486 | 102.0464 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ANNASW_5 ( 2373) -> COLLINSS1_5 ( 2372) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 345 | 345 | Branch Amp | 2999.8782 | - | - | - | - | 103.5394 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ANNASW_5 ( 2373) -> COLLINSS1_5 ( 2372) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 345 | 345 | Branch Amp | 2999.8782 | - | - | - | - | 102.7238 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ANNASW_5 ( 2373) -> COLLINSS1_5 ( 2372) CKT 1 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2999.8782 | - | - | - | 109.2242 | 117.4116 | 106.6687 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ANNASW_5 ( 2373) -> COLLINSS1_5 ( 2372) CKT 1 | KRUMW-WEST DENT/DUNHAM 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2999.8782 | - | - | - | - | 103.04 | - | -
ERCOT | COAST | COAST | COAST, COAST | APTXCITY_8 (112014) -> APTXCITY_5 (112012) CKT T1 | Pre-contingency | 138 | 34.5 | MVA | 100 | 116.7485 | 115.4098 | 118.4511 | 110.2425 | 109.6634 | 112.5362 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | AQUIFER_8 (11377) -> MCLLVAIN_8 (11182) CKT 1 | L_011097SANDLAKE_8-011612ONC900009_TAPC1 | 138 | 138 | Branch Amp | 2539.5042 | - | - | - | - | 102.1459 | - | -
TAEPTC,TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | ARANSASP4A ( 8430) -> INGLESID4A ( 8425) CKT 1 | L_008422I_DUPSW4A-008425INGLESID4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | 157.1331 | 161.5408 | 184.0589 | 159.3687 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ARGYLEN_8 (11986) -> ARGYLE1_8 ( 1984) CKT 1 | L_000612BLUHORSE-000680NRTHSANGERC1 | 138 | 138 | Branch Amp | 878.5764 | - | - | - | - | 109.6229 | 101.019 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ARGYLEN_8 (11986) -> ARGYLE1_8 ( 1984) CKT 1 | L_000612BLUHORSE-000684SPRINGC1 | 138 | 138 | Branch Amp | 878.5764 | - | - | - | 101.7926 | 112.8216 | 104.1824 | -
TONCOR | EAST | EAST | EAST, EAST | ATHENS_8 ( 3238) -> MURCHISN_8 ( 3240) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 133.8783 | - | - | - | - | 100.6783 | - | -
TONCOR | EAST | EAST | EAST, EAST | ATHENS_8 ( 3238) -> MURCHISN_8 ( 3240) CKT 1 | L_003107ELKTONSUB_8-003196TYLERSWE_8C1 | 138 | 138 | Branch Amp | 133.8783 | - | - | 109.6294 | 123.3613 | 135.8246 | 128.4987 | -
TONCOR | EAST | EAST | EAST, EAST | ATHENS_8 ( 3238) -> MURCHISN_8 ( 3240) CKT 1 | L_003196TYLERSWE_8-003197TYLERSW_8C2 | 138 | 138 | Branch Amp | 133.8783 | - | - | - | - | 109.3699 | 102.2426 | -
TONCOR | EAST | EAST | EAST, EAST | ATHENS_8 ( 3238) -> MURCHISN_8 ( 3240) CKT 1 | TYLERSWSTA-ELKTON_8(SINGLE B TO B) | 138 | 138 | Branch Amp | 133.8783 | - | - | - | - | 112.177 | 104.9664 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | ATSO2A ( 6511) -> OZNC2A ( 6552) CKT 1 | L_006562FDRAN4A-060412CARVER4AC1 | 69 | 69 | Branch Amp | 317.961 | - | 125.4602 | 127.997 | - | 121.2101 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | AUSTROP8 ( 9328) -> DUNLAP8 ( 9045) CKT 1 | AEN_DL-AU¦LP_2013 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | - | 108.2348 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | AUSTROP8 ( 9328) -> L_SETTLE8_1Y ( 7327) CKT 1 | L_007310L_SIMGID8_1Y-007327L_SETTLE8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 103.329 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | AUSTROP8 ( 9328) -> L_WEBBER8_1Y ( 7329) CKT 1 | L_007310L_SIMGID8_1Y-007322L_BASTCI8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 105.2781 | 117.3299 | 121.3951 | 117.2392 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | AUSTROP8 ( 9328) -> L_WEBBER8_1Y ( 7329) CKT 1 | LCRA TSC_T171_T172_1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 105.1466 | 117.2106 | 121.1681 | 116.9778 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | AZLE1_8 ( 2062) -> BASECAMP_8 ( 1860) CKT 1 | BEPC_006 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 122.5724 | 108.0181 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | AZLE1_8 ( 2062) -> BASECAMP_8 ( 1860) CKT 1 | BEPC_283_1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 104.7164 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | AZLE1_8 ( 2062) -> BASECAMP_8 ( 1860) CKT 1 | L_000570WISECNTY-000571HIDEOUTC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 103.8389 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | AZLE1_8 ( 2062) -> BASECAMP_8 ( 1860) CKT 1 | L_000571HIDEOUT-000579JCKCNTY8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 104.7442 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALE_S5 ( 3711) -> STJOHNS_5 ( 3384) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 130.1797 | 117.2388 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALE_S5 ( 3711) -> STJOHNS_5 ( 3384) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 125.6115 | 112.1742 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALE_S5 ( 3711) -> STJOHNS_5 ( 3384) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 119.0089 | 106.6586 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALE_S5 ( 3711) -> STJOHNS_5 ( 3384) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 109.761 | 100.2395 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALE_S5 ( 3711) -> STJOHNS_5 ( 3384) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.558 | - | -
TAEPTN | WEST | WEST | WEST, WEST | BALLINGE2A ( 6338) -> MORO2A (60019) CKT 1 | L_006340BALLINGE4A-006360COLE_IVI4AC1 | 69 | 69 | Branch Amp | 426.7371 | - | - | - | 111.7195 | - | 111.9957 | -
TAEPTN | WEST | WEST | WEST, WEST | BALLINGE2A ( 6338) -> MORO2A (60019) CKT 1 | L_006347COLETAP4A-006355SANA4AC1 | 69 | 69 | Branch Amp | 426.7371 | - | - | - | 105.985 | - | 106.1795 | -
TAEPTN | WEST | WEST | WEST, WEST | BALLINGE2A ( 6338) -> MORO2A (60019) CKT 1 | L_006347COLETAP4A-006360COLE_IVI4AC1 | 69 | 69 | Branch Amp | 426.7371 | - | - | - | 111.0822 | - | 111.3668 | -
TAEPTN | WEST | WEST | WEST, WEST | BALLINGE2A ( 6338) -> MORO2A (60019) CKT 1 | L2020903 | 69 | 69 | Branch Amp | 426.7371 | - | - | - | 107.4349 | - | 107.4179 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | BENNETT RD-WISE CTY 138 KV | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 118.1651 | 111.6166 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | BEPC_005_1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.0783 | 110.2839 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | BEPC_114 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 108.6154 | 102.5525 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | BEPC_21 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 103.3267 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | BEPC_243 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 109.5524 | 103.6311 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | BEPC_246 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 101.2598 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | BEPC_2541 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 101.0702 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | BEPC_283_1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 131.151 | 123.0481 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | E_WHCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.0368 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | E_WHCCS2_CC2_TRAIN | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.1346 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | G_150111CPSES_UNIT1UU1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.1474 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | G_150112CPSES_UNIT2UU2 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.1519 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | G_888879BLUBIRD_POIUS1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.028 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000501HILLTOP8-000508RIKERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 106.0234 | 130.8371 | 123.7937 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000508RIKER-000516ZIONHILLC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 106.0243 | 130.8384 | 123.7951 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000516ZIONHILL-000543SWIMMERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | 101.3413 | 108.0736 | 132.9653 | 125.8523 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000543SWIMMER-000588WILLOWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | 102.2842 | 108.998 | 133.9161 | 126.7794 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000570WISECNTY-000571HIDEOUTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | 100.3556 | 106.1289 | 130.2067 | 122.0598 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000571HIDEOUT-000579JCKCNTY8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | 101.2057 | 106.9938 | 131.1476 | 122.9649 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000579JCKCNTY8-000580WSTBROOKC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | 102.7609 | 109.5024 | 134.4373 | 127.2874 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000579JCKCNTY8-000600BRIDGEPORTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 108.8007 | 102.7634 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000580WSTBROOK-000588WILLOWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | 102.4771 | 109.1931 | 134.1011 | 126.9601 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000590PERCHHILL-000600BRIDGEPORTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 107.2689 | 101.2705 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000590PERCHHILL-000608CRAFTONC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 106.1341 | 100.1662 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000608CRAFTON-000620BOWIE8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 105.5509 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000620BOWIE8-000741DYEMOUNDC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 101.3399 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000670KRUM-001568ALLISON_T8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.0627 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000684SPRING-000691VALLEYVIEWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 101.8162 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000690MYRA-000691VALLEYVIEWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 102.1341 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000690MYRA-000695MUENSTERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.5838 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000695MUENSTER-000730WOLFRIDGEC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.9456 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000741DYEMOUND-000762HARDYSWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 101.0253 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_000746STJO8-000762HARDYSWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.886 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_001565BRDGPORT_8-001590BRDGPORT_T8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.1607 | 110.551 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_001568ALLISON_T8-888887CONNOLLY_B1C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.3236 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | L_001582BENNETT_8-001590BRDGPORT_T8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.1581 | 110.5484 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.607 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.0741 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | WISE COUNTY - JACK COUNTY (BEPC) 138 KV (SINGLE B TO B) HIDEOUT | 138 | 138 | Branch Amp | 1606.5397 | - | - | 101.2892 | 107.082 | - | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | WISE COUNTY (BEC) - ALVORD/BRIDGEPORT(BEC) (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.0769 | 110.2839 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BALSORA_8 ( 1598) -> COTTONDALE ( 596) CKT 1 | XFMR-WHCCS2_5-1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.0478 | - | -
TONCOR | WEST | WEST | WEST, WEST | BARBER_LK2_8 ( 1190) -> FRONTIER_P8 (11393) CKT 1 | L_010050RANGER_8-011393FRONTIER_P8C1 | 138 | 138 | Branch Amp | 2568.79 | - | 129.4532 | - | - | - | - | -
RGOLSP | WEST | WEST | WEST, WEST | BARNHRT2A ( 6530) -> BARNHART2A ( 6537) CKT 1 | L_006036YUCCA4A-060360CASSAVA4AC1 | 69 | 69 | Branch Amp | 290.3486 | - | - | - | 100.015 | 113.1669 | 114.4158 | -
TRAYBN | EAST | EAST | EAST, EAST | BARRETT_POI (888848) -> LNOK_RC ( 6871) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 978.9851 | - | - | - | - | 103.5002 | - | -
TRAYBN | EAST | EAST | EAST, EAST | BARRETT_POI (888848) -> LNOK_RC ( 6871) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 978.9851 | - | - | - | - | 104.7279 | - | -
TRAYBN | EAST | EAST | EAST, EAST | BARRETT_POI (888848) -> LNOK_RC ( 6871) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 978.9851 | - | - | - | - | 100.2721 | - | -
TRAYBN | EAST | EAST | EAST, EAST | BARRETT_POI (888848) -> LNOK_RC ( 6871) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 978.9851 | - | - | - | - | 105.2587 | - | -
TRAYBN | EAST | EAST | EAST, EAST | BARRETT_POI (888848) -> LNOK_RC ( 6871) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 978.9851 | - | - | - | - | 101.4787 | - | -
TRAYBN | EAST | EAST | EAST, EAST | BARRETT_POI (888848) -> LNOK_RC ( 6871) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 978.9851 | - | - | - | - | 106.4562 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BARSTOWNW_8 ( 1086) -> PECONE_P8 (11105) CKT 1 | L_011097SANDLAKE_8-011612ONC900009_TAPC1 | 138 | 138 | Branch Amp | 2539.5042 | - | - | - | - | 108.4885 | 100.7607 | -
TCNPE | COAST | COAST | COAST, COAST | BASF___POI_8 (42150) -> BRZPRT_S02_8 (42210) CKT 02 | P7-1_E1>>T2682EX1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 106.4505 | -
TCNPE | COAST | COAST | COAST, COAST | BASF___POI_8 (42150) -> BRZPRT_S02_8 (42210) CKT 02 | P7-1_E1>>T2682EX2 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 107.5728 | -
TCNPE | COAST | COAST | COAST, COAST | BASF___POI_8 (42150) -> BRZPRT_S02_8 (42210) CKT 02 | P7-1_E1>>T2682GY1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 107.6872 | -
TCNPE | COAST | COAST | COAST, COAST | BASF___POI_8 (42150) -> BRZPRT_S02_8 (42210) CKT 02 | P7-1_E1>>T2682GY2 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 107.6865 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.7698 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3089 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 1 | L_002217BATCHLRD_8-002427WATMLL_W5C2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | 112.2986 | 164.4593 | - | 154.9353 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.6311 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.3662 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 111.8707 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 109.0123 | - | 105.9326 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 103.565 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 1 | VENUS-NAVARRO 345 KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.5082 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 1 | Watermill Switch-Batchler Rd SW 345 kV Line CKT2(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 164.4593 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 119.1391 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 2 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.8441 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 2 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3829 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 2 | L_002217BATCHLRD_8-002427WATMLL_W5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | 112.3083 | 164.477 | - | 154.9454 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 2 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.7052 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 2 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.444 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 2 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 111.9524 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 2 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 109.0919 | - | 106.0091 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 2 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 103.6398 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 2 | VENUS-NAVARRO 345 KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.586 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 2 | Watermill Switch-Batchler Rd SW 345 kV Line CKT1(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | 112.3083 | 164.477 | - | 154.9454 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 ( 2217) -> WATMLL_W5 ( 2427) CKT 2 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 119.226 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 (2217) -> BIGONION_5 (2466) CKT 1 | Pre-contingency | 345 | 345 | Amps | 2729.4439 | - | - | - | 106.625 | 123.301 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 (2217) -> ELROD_5 (3159) CKT 1 | Pre-contingency | 345 | 345 | Amps | 2729.4439 | - | - | - | - | 115.5296 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 (2217) -> WATMLL_W5 (2427) CKT 1 | Pre-contingency | 345 | 345 | Amps | 2729.4439 | - | - | - | - | 103.008 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BATCHLRD_8 (2217) -> WATMLL_W5 (2427) CKT 2 | Pre-contingency | 345 | 345 | Amps | 2729.4439 | - | - | - | - | 103.0824 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.2867 | 122.9545 | 133.5813 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 118.113 | 129.0289 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 111.3384 | 124.072 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 102.2734 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | L_003402LAKE_CRK2_5-003403LAKE_HALL_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 105.0528 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | L_003403LAKE_HALL_5-003405THOUSE__5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 106.8387 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | L_003405THOUSE__5-003412TEMP_PEC__5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 103.3279 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | L_003687BELL_E_5-003705BRANGUS_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.3765 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 102.7489 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 103.6883 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | LAKE CREEK - LAKE HALL/TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.1462 | 110.4498 | 128.5458 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | LAKE CREEK - LAKE HALL_5 (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 110.2977 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6962 | 118.2477 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 118.2806 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 113.7493 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 130.8053 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | THOUSE-LCRK*PCNCRK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 108.6664 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 113.556 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 105.2268 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 108.5092 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 108.0426 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 108.6819 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 139.8738 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | VENUS-FORT SMITH SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 104.3987 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELFALLS_8 ( 3404) -> TEMP_SS__5 ( 3414) CKT 1 | VENUS-SAM SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 103.4873 | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | AEN_LP-AU¦DL_2013 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.622 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.0925 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | E_BASTEN_CC1_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2267 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | G_170126CALAVER_JKS2UL2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4793 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | G_RIO_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.8633 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 128.441 | - | 102.0594 | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | J5LCA1C1_B | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.8746 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 122.9105 | - | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 126.788 | - | 100.358 | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 108.9815 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 120.9223 | 151.8694 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | L_003415TEMP_SS__8-003485TINROOF_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.7487 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.296 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.296 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.2116 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4743 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2276 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 108.3964 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.3793 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | LCRATSC_1_HUTTO__LIMMER | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2491 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | N5GSU2_B | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4793 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 115.9141 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 1 | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 105.2607 | 122.5166 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | AEN_LP-AU¦DL_2013 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.622 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.0925 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | E_BASTEN_CC1_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2267 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | G_170126CALAVER_JKS2UL2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4793 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | G_RIO_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.8633 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 128.441 | - | 102.0594 | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | J5LCA1C1_B | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.8746 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 122.9105 | - | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 126.788 | - | 100.358 | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 108.9815 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 120.9223 | 151.8694 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | L_003415TEMP_SS__8-003485TINROOF_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.7487 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | L_003696HUTTOSS__5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.296 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | L_003696HUTTOSS__5-003699SALADOSS_5C2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.296 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | L_005068CACHENA-005133ELMCREEKC2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.2116 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | L_005133ELMCREEK-005380SHAULAC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4743 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2276 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 108.3964 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.3793 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | LCRATSC_1_HUTTO__LIMMER | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2491 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | N5GSU2_B | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4793 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 115.9141 | - | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | BELL_E_5 ( 3687) -> SAND_TXU_5 (13429) CKT 2 | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 105.2607 | 122.5166 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | AEN_AU-DG¦DL_2013 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1266 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | AEN_DE-SK¦SK | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1554 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | AEN_DL-AU¦LP_2013 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.1329 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | AEN_DP-SK¦MC | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2964 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | AEN_GF-SR: EP-HC | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1402 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | AEN_GF-SR¦EP | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2482 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | AEN_LP-AU¦DL_2013 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2787 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | AEN_LY-FPP:CIS-HO | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0137 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | AEN_LY-FPP¦CIS | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.2193 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | AEN_P1-1_GEN_SH5A+5C | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.152 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.5982 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | AUSTROP - BEULAH/TORTOISE_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.3057 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | BELLCNTY8-BARTLETTSW (SINGLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 117.9127 | 128.8887 | 117.7544 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | BELLCNTY8-GABRIEL (LCRA) (SINGLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 117.0638 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | BEPC_215_2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 128.0051 | 116.8976 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | DVCPA1C21B_1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.1882 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | DVCPA1C21B_2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.6161 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | E_B_DAVIS_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.5338 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | E_BASTEN_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.1738 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | E_BRAUNIG_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2919 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | E_CCEC_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2578 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | E_DUKE_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7123 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | E_FERGCC_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.4909 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | E_GUADG_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1051 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | E_GUADG_CC2_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.077 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | E_INGLCOSW_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2989 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | E_LGE_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0649 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | E_LOSTPI_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0886 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | E_NEDIN_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4857 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | E_NUECES_B_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.7569 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | G_007044L_MARION5_1YUN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8685 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | G_007048L_GARFIE5_1YUN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4037 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | G_160131SAN_SANMIGG1UL1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0258 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | G_170073GID_GIDEONG3UN3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7846 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | G_170101FPPYD_FPP_G1UL1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0551 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | G_170102FPPYD_FPP_G2UL2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9499 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | G_170126CALAVER_JKS2UL2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.8343 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | G_170671CACHENA_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.455 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | G_RIO_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.0708 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | GEORGETOWN S - HUTTO_8 (SINGLE B TO B) B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4331 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | HUTTO - ROUND ROCK/GEORGETOWN SOUTH (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 100.3923 | 107.9725 | 100.217 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | 116.9917 | - | - | 137.534 | - | 126.388 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | J5LCA1C1_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.0858 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_000114BARTLETTSW-000122SCHWERTNERC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 117.4402 | 128.4395 | 117.3053 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_000114BARTLETTSW-000132BELLCNTY8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 118.2433 | 129.2253 | 118.0751 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_000122SCHWERTNER-007346L_GABRIE8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 115.3639 | 126.3171 | 115.2211 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_000128CHAPPARAL-000136TRIMMIERC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1098 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_000128CHAPPARAL-003423KILL_SS__8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1093 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.2915 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 861.8416 | 105.0282 | - | - | 113.2883 | 147.8047 | 107.7254 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_003415TEMP_SS__8-003485TINROOF_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.0954 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_003664RNDRCKWH_T_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 100.7194 | 108.3754 | 100.767 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_003664RNDRCKWH_T_8-003669RNDRCKWH1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 100.7207 | 108.3762 | 100.7688 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 861.8416 | 103.6516 | - | - | 103.8408 | 111.5075 | 103.93 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_003666HUTTOSS1_8-003670RNDRCKNE1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5248 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_003668RNDROCK1_8-007366L_CHIEBR8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | 101.2502 | - | - | - | 104.8082 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_003669RNDRCKWH1_8-007532L_GEORSO8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.6047 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_003677MIDNIGHT_8-007532L_GEORSO8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1124 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.3491 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.3491 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_003717TORTOISE_5-013429SAND_TXU_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.8123 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 110.1435 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.7851 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.8268 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4625 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_005380SHAULA-005915SO_TEX__345AC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4862 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7985 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_007041L_JOHNDU5_1Y-007047L_HORNSB5_1YC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5749 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.175 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_007343L_GEORGE8_1Y-007347L_RIVERY8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4618 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_007343L_GEORGE8_1Y-007366L_CHIEBR8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.571 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.2463 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_080071ZORILLO7A-080076AJO7AC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3641 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4626 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | LCRA TSC_T255_TAE3121_1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.6918 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | LCRA TSC_T359_T21422_1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 112.8644 | 123.0747 | 112.6876 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | LCRA TSC_T378_T642 | 138 | 138 | Branch Amp | 861.8416 | 103.1431 | - | - | - | 106.3083 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | LCRA TSC_T510_1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8553 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | LCRA TSC_T510_T512_1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1348 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | LCRATSC_1_HUTTO__LIMMER | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.2288 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | LCRATSC_4_WHISVA_HORNSB | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5084 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | LCRATSC_5_HORNSB_EUCLID | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.1514 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | LCRATSC_6_EUCLID_JOHNDU | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.7137 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | LCRATSC_7_JOHNDU_ZORN__ | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1654 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | M10000271115801 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4194 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | M105311105321 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0654 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | M115851115803 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3641 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | MB100002711580 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4194 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | MB1158011585 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3641 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | N5GSU2_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.8343 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | P7-1_E1>>T1839X1_ERC | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.55 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | P7-1_E1>>T1839X2_ERC | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.1285 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | P7-1_E1>>T2764Y_ERCa | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1981 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | P7-1_E1>>T3944Z_ERC | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.8889 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | R4U2A5C1_1_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3203 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | ROUND ROCK - WELLS BRANCH (LCRA) (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1113 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.3261 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.6899 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | SAN_PAT_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0238 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | STECL_10262 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0258 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | STP - HOUDINI & STP - SHAULA | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1371 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | TORTOISE - BEULAH/AUSTROP_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.1676 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | TORTOISE - SANDOW_8_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.9239 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7406 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | Voss Lake - Temple 138 kV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.3743 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 ( 132) -> SALADO1_8 ( 3640) CKT 1 | WAP - HOUDINI & STP - SHAULA | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7251 | - | -
TONCOR , TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY8 (132) -> TEMP_SS__8 (3415) CKT 1 | Pre-contingency | 138 | 138 | Amps | 1317.8646 | - | - | - | 109.5258 | 118.6038 | 108.009 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY9 ( 133) -> BELLCNTY8 ( 132) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 69 | 138 | Branch MVA | 75 | - | - | - | 142.7902 | - | 138.5186 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY9 ( 133) -> BELLCNTY8 ( 132) CKT 1 | L_000132BELLCNTY8-003415TEMP_SS__8C1 | 69 | 138 | Branch MVA | 75 | - | - | - | 109.9985 | 120.9233 | 111.1873 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELLCNTY9 ( 133) -> BELLCNTY8 ( 132) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 69 | 138 | Branch MVA | 75 | - | - | - | 120.2391 | 137.5278 | 117.8086 | -
TONCOR | NORTH | NORTH | NORTH, NORTH | BELLSN_T8 ( 1699) -> NORTHGATE_8 (12679) CKT 1 | L_001839STONCRK_8-012677HAGGRTY_8C1 | 138 | 138 | Branch Amp | 1312.0074 | - | - | - | 121.4185 | 130.3545 | 126.9158 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELTON1_8 ( 3610) -> BELTONSW1_8 (13610) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 111.2367 | - | 102.9505 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELTON1_8 ( 3610) -> BELTONSW1_8 (13610) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 119.4009 | - | 110.2988 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELTON1_8 ( 3610) -> BELTONSW1_8 (13610) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 106.0971 | 148.9773 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELTON1_8 ( 3610) -> NOLANVIL1_8 ( 3617) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 122.8289 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELTONSW1_8 (13610) -> WARRIORTRL_8 ( 3366) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1363.8853 | - | - | - | 105.5864 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BELTONSW1_8 (13610) -> WARRIORTRL_8 ( 3366) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1363.8853 | - | - | - | - | 133.9272 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENBRK_A_T5 ( 1869) -> BENBRSTR (500051) CKT 1 | 3WT_001870BENBRK_B_T5_018751BENBRK_SRB_8_011877BENBRK_B_3 C 2 | 345 | 1 | Branch MVA | 625 | - | - | - | 101.6167 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENBRK_A_T5 ( 1869) -> BENBRSTR (500051) CKT 1 | L_001875BENBRK_B_8-018751BENBRK_SRB_8C2 | 345 | 1 | Branch MVA | 625 | - | - | - | 101.6167 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENBRK_A_T5 ( 1869) -> BENBRSTR (500051) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV DCKT & EAGLE MOUNTAIN - WEATHERFORD 138 KV LINE | 345 | 1 | Branch MVA | 625 | - | - | - | 100.1176 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENDAVIS_8 ( 968) -> GOBLN_8 ( 2497) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 1363.8853 | - | - | - | - | 100.03 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENNETT_8 ( 1582) -> DECATUR_8 ( 1566) CKT 1 | BASECAMP - BENNETT RD SW 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.1251 | 100.8217 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENNETT_8 ( 1582) -> DECATUR_8 ( 1566) CKT 1 | BEPC_005_1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.0627 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENNETT_8 ( 1582) -> DECATUR_8 ( 1566) CKT 1 | BEPC_242 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.2694 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENNETT_8 ( 1582) -> DECATUR_8 ( 1566) CKT 1 | EAGLE MOUNTAIN - HICKS/BENNETT 138 KV (DOUBLE B TO B) A NEWLOAD | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.084 | 100.8336 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENNETT_8 ( 1582) -> DECATUR_8 ( 1566) CKT 1 | L_000541RENO-000595KEETERC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.2586 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENNETT_8 ( 1582) -> DECATUR_8 ( 1566) CKT 1 | L_000568PEDENROAD-001570RHOME_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.7426 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENNETT_8 ( 1582) -> DECATUR_8 ( 1566) CKT 1 | L_000579JCKCNTY8-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.2545 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENNETT_8 ( 1582) -> DECATUR_8 ( 1566) CKT 1 | L_000595KEETER-000596COTTONDALEC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.6195 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENNETT_8 ( 1582) -> DECATUR_8 ( 1566) CKT 1 | L_000596COTTONDALE-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.2567 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENNETT_8 ( 1582) -> DECATUR_8 ( 1566) CKT 1 | L_001570RHOME_8-001594DECATUR_T8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.167 | 100.8204 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENNETT_8 ( 1582) -> DECATUR_8 ( 1566) CKT 1 | L_001582BENNETT_8-001594DECATUR_T8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.1756 | 100.8311 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENNETT_8 ( 1582) -> DECATUR_8 ( 1566) CKT 1 | RAMHORN - HICKS & BASE CAMP - BENNET DC 345 &138 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.8379 | 100.4894 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENNETT_8 ( 1582) -> DECATUR_8 ( 1566) CKT 1 | RAMHORN - HICKS 345 AND BASE CAMP - BENNET 138 (DOUBLE B TO B) CKT 2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.6105 | 102.0878 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENNETT_8 ( 1582) -> DECATUR_8 ( 1566) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (COMMON TOWER) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 111.8301 | 104.6153 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENNETT_8 ( 1582) -> DECATUR_8 ( 1566) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.6105 | 102.0878 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BENNETT_8 ( 1582) -> DECATUR_8 ( 1566) CKT 1 | WISE COUNTY (BEC) - ALVORD/BRIDGEPORT(BEC) (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.9291 | - | -
TONCOR,TLSTR | EAST | NORTH_CE | EAST, NORTH_CE | BIGBRNE_5 ( 3380) -> NAVARRO (68091) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 105.2171 | - | 118.7956 | -
TONCOR,TLSTR | EAST | NORTH_CE | EAST, NORTH_CE | BIGBRNE_5 ( 3380) -> NAVARRO (68091) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 112.7242 | - | 129.2692 | -
TONCOR,TLSTR | EAST | NORTH_CE | EAST, NORTH_CE | BIGBRNE_5 ( 3380) -> NAVARRO (68091) CKT 1 | L_003134RICHLND1_5-003380BIGBRNE_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | - | 106.2184 | -
TONCOR,TLSTR | EAST | NORTH_CE | EAST, NORTH_CE | BIGBRNE_5 ( 3380) -> NAVARRO (68091) CKT 1 | L_003386OUTLAW_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | - | 101.0498 | -
TONCOR,TLSTR | EAST | NORTH_CE | EAST, NORTH_CE | BIGBRNE_5 ( 3380) -> NAVARRO (68091) CKT 1 | LIMESTONE - OUTLAW / NAVARRO_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 112.0143 | - | - | -
TONCOR,TLSTR | EAST | NORTH_CE | EAST, NORTH_CE | BIGBRNE_5 ( 3380) -> NAVARRO (68091) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 118.3107 | - | 129.0594 | -
TONCOR,TLSTR | EAST | NORTH_CE | EAST, NORTH_CE | BIGBRNE_5 ( 3380) -> NAVARRO (68091) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | - | 124.0723 | -
TONCOR,TLSTR | EAST | NORTH_CE | EAST, NORTH_CE | BIGBRNE_5 ( 3380) -> NAVARRO (68091) CKT 1 | RICH-BBROWN (DOUBLE B TO B)A | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | - | 106.3755 | -
TONCOR,TLSTR | EAST | NORTH_CE | EAST, NORTH_CE | BIGBRNE_5 ( 3380) -> NAVARRO (68091) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | - | 114.5431 | -
TONCOR,TLSTR | EAST | NORTH_CE | EAST, NORTH_CE | BIGBRNE_5 ( 3380) -> NAVARRO (68091) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 114.4228 | - | 129.5412 | -
TONCOR,TLSTR | EAST | NORTH_CE | EAST, NORTH_CE | BIGBRNE_5 ( 3380) -> NAVARRO (68091) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 108.6029 | - | 119.7958 | -
TONCOR,TLSTR | EAST | NORTH_CE | EAST, NORTH_CE | BIGBRNE_5 ( 3380) -> NAVARRO (68091) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 106.1509 | - | - | -
TONCOR | EAST | EAST | EAST, EAST | BIGBRNE_5 ( 3380) -> RICHLND1_5 ( 3134) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 106.9886 | - | - | -
TONCOR , TLSTR | EAST | NORTH_CE | EAST, NORTH_CE | BIGBRNE_5 (3380) -> NAVARRO (68091) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1999.8072 | - | - | - | - | 107.5083 | - | -
TONCOR,TLSTR | EAST | NORTH_CE | EAST, NORTH_CE | BIGBRNW_5 ( 3381) -> NAVARRO (68091) CKT 2 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 105.7034 | - | -
TONCOR,TLSTR | EAST | NORTH_CE | EAST, NORTH_CE | BIGBRNW_5 ( 3381) -> NAVARRO (68091) CKT 2 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 115.4383 | - | -
TONCOR,TLSTR | EAST | NORTH_CE | EAST, NORTH_CE | BIGBRNW_5 ( 3381) -> NAVARRO (68091) CKT 2 | P7-1_E1>LEG-OUTLAW_ERC | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 112.3773 | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BIGLAKE2A ( 6533) -> PHBL_TAP2A ( 6546) CKT 1 | L_006550FDRAN2A-006560OZONA2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 105.1145 | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BIGLAKE2A ( 6533) -> PHBL_TAP2A ( 6546) CKT 1 | L_060361SANTARIT4A-060414OWLS4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 136.6114 | 133.7082 | 133.7197 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BIGLAKE2A ( 6533) -> PHBL_TAP2A ( 6546) CKT 1 | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 136.7061 | 133.6805 | 133.556 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BIGLAKE2A ( 6533) -> PHBL_TAP2A ( 6546) CKT 1 | L_060723CROSSOVE4A-060728PALOUSE4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 146.272 | 144.4273 | 147.8065 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BIGLAKE2A ( 6533) -> PHBL_TAP2A ( 6546) CKT 1 | L_060723CROSSOVE4A-076032L_NORTMC8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 146.3211 | 144.4837 | 147.8681 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BIGLAKE2A ( 6533) -> PHBL_TAP2A ( 6546) CKT 1 | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 134.8671 | 133.1788 | 132.9423 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BIGLAKE2A ( 6533) -> PHBL_TAP2A ( 6546) CKT 1 | L2020944-A | 69 | 69 | Branch Amp | 317.961 | - | - | - | 136.708 | 133.6882 | 133.5557 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BIGLAKE2A ( 6533) -> PHBL_TAP2A ( 6546) CKT 1 | L2020944-B | 69 | 69 | Branch Amp | 317.961 | - | - | - | 146.2717 | 144.427 | 147.8059 | -
TAEPTN | WEST | FAR_WEST | WEST, FAR_WEST | BIGLAKE2B ( 6534) -> BARNHRT2A ( 6530) CKT 1 | L_006036YUCCA4A-006525ESMERALD4AC1 | 69 | 69 | Branch Amp | 317.961 | 149.3851 | - | 189.7084 | - | - | - | -
TAEPTN | WEST | FAR_WEST | WEST, FAR_WEST | BIGLAKE2B ( 6534) -> BARNHRT2A ( 6530) CKT 1 | L_006036YUCCA4A-060360CASSAVA4AC1 | 69 | 69 | Branch Amp | 317.961 | 115.2708 | - | 138.7167 | 170.0271 | 191.2573 | 196.0887 | -
TAEPTN | WEST | FAR_WEST | WEST, FAR_WEST | BIGLAKE2B ( 6534) -> BARNHRT2A ( 6530) CKT 1 | L_006530BARNHRT2A-060359CASSAVA2AC1 | 69 | 69 | Branch Amp | 317.961 | 106.7131 | - | 125.5422 | 141.6296 | 154.9654 | 156.9282 | -
TAEPTN | WEST | FAR_WEST | WEST, FAR_WEST | BIGLAKE2B ( 6534) -> BARNHRT2A ( 6530) CKT 1 | T_060359CASSAVA2A-060360CASSAVA4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 103.2828 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BIGLAKE4A ( 6535) -> BIGLAKE2A ( 6533) CKT 1 | L_006036YUCCA4A-060360CASSAVA4AC1 | 69 | 138 | Branch MVA | 50 | - | - | - | - | 105.2034 | 105.6392 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BIGLAKE4A ( 6535) -> BIGLAKE2A ( 6533) CKT 1 | T_006534BIGLAKE2B-006535BIGLAKE4AC1 | 69 | 138 | Branch MVA | 50 | - | - | - | - | 110.7392 | 105.9685 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BIGLAKE4A ( 6535) -> BIGLAKE2B ( 6534) CKT 1 | L_006036YUCCA4A-060360CASSAVA4AC1 | 69 | 138 | Branch MVA | 50 | - | - | - | - | 100.9731 | 101.394 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BIGLAKE4A ( 6535) -> BIGLAKE2B ( 6534) CKT 1 | T_006533BIGLAKE2A-006535BIGLAKE4AC1 | 69 | 138 | Branch MVA | 50 | - | - | - | - | 109.18 | 104.4922 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_001869BENBRK_A_T5_018741BENBRK_SRA_8_011876BENBRK_A_3 C 1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.017 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_001870BENBRK_B_T5_018751BENBRK_SRB_8_011877BENBRK_B_3 C 2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0047 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_001880ROCKYCRK_5_001881ROCKYCRK_8_011881ROCKYCRK_3 C 1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.071 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.8792 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_001918SHRYAUTO1_5_001920SHRY_B8_011920SHRY_B_3 C 1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4873 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_001926LIGGETT_1T5_001923LIGGETTA1_8_011926LIGGETTA1_3 C 1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1319 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_001927LIGGETT_2T5_001925LIGGETTA2_8_011927LIGGETTA2_3 C 2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1316 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_001934SHRYAUTO2_5_001919SHRY_A8_011921SHRY_A_3 C 2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2207 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_002359RNRDPL1_5_002358RNRDPL_1T8_016358RNRDPL1_3 C 1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1546 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_002361CRLTN_NW1_5_002360CRLTN_NW1_8_012360CRLTN_NW1_3 C 1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.038 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_002410NORWD_1T5_002404NORWD_1T8_012404NORWD_1T3 C 1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0517 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_002433SGVLSW1_5_002434SGVLSW1_8_012434SGVLSW1_3 C 2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1722 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_002453CNVLSW1_5_002450CNVLSW_E8_029872CNVIL1_3 C 1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0201 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_002514ALLENSW2_5_012513ALLENSWS2_8_012512ALLENSW2_3 C 2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0484 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_002522PL_TENNY_5_002523PL_TENNY_8_012523PL_TENNY1_3 C 1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0184 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_003522HILLBORO1_8_003523HILLBORO1_9_003519HILLBORO1_3 C 1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.105 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | AEN_LP-AU¦DL_2013 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1907 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | AEN_LY-FPP:CIS-HO | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1403 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | AEN_LY-FPP¦CIS | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2554 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | AEN_P7 FPP-LP.DC_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0083 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW - MONTICELLO 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.003 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3182 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4033 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6422 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4108 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6493 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4776 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7398 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5247 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8037 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4853 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7569 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5322 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8108 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1176 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1245 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN-MOSES 345-138 AUTO-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2699 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3015 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5768 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2998 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.563 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ASP_WRG_L1F1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4554 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ASP_WRG_P7F2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2055 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | B2-COD-1_B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2228 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BARRETT_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.136 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BAS_RANCH_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.2673 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 113.3216 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 111.996 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BENBROOK-PARKER*CARMICHAEL BEND 345 KV WITH BENBROOK AUTO (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0776 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.3089 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BEPC_015_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.5167 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BEPC_22 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1731 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BEPC_227-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1431 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BEPC_227-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1431 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BEPC_23_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1646 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BEPC_301_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3039 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BEPC_304_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.506 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BEPC_311_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0868 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BEPC_459 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BITTER CREEK SW (LCRA) - CATTLEMEN SW & BITTER CREEK SW (LCRA) - SWEETWATER EAST 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0391 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BLOOMDALE SW - ANNA SW 138 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.01 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BLUBIRD_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.3331 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 110.5718 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | BROWN SW - BLUFF CREEK SW & BROWN SW - CENTRAL BLUFF 345 KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0165 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | CARROLLTON NW-HACKBERRY-NORWOOD 345KV (SINGLE B TO B) HACKBERRY 345/138 TRANSFORMER | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.021 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | CARTWHEEL_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.364 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | CEDAR HILL - DESOTO/LOOP NINE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.3368 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 108.6527 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | CEDAR HILL SW - FISH CREEK 138 KV (SINGLE B TO B) FISH CREEK 138/69 TRANSFORMER | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1045 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 108.5085 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | CLEAR CROSSING - COODY CROSSING/THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5912 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | CLY_PHNT1P7F1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.9357 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | CLY_PHNT1P7F1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8386 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | CLY_PHNT2P7F1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5438 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | CLY_PHNT2P7F1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.448 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | COMANCHE PEAK-MITCHELL BEND*WOLF HOLLOW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0356 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | COODY CROSSING - TECUMSEH AND CLEAR CROSSING - THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7321 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | DERMOTT - KIRCHHOF CKT 1 & DERMOTT - KIRCHHOF CKT 2 345 KV (DOUBLE B TO B) C | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2162 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | DERMOTT - KIRCHHOF CKT 1 345 KV WIN 2023 - FUTURE (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1814 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | DES_WILL_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.0916 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | DRY_CREEK_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.7294 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | DUNE - WINK/YUKON 138 KV 2019 SUM - FUTURE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0167 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | DUNHAM - KRUMW/RNK DC 345 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1293 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.478 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | DVCPA1C21B_1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1995 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | DVCPA1C21B_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2555 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_ETCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.9873 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_FLCNS_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0053 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_FRNYPP_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.9137 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_FRNYPP_CC2_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.8914 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_JACKCNTY_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.9182 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_JCKCNTY2_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.973 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_KMCHI_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.3698 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_KMCHI_CC2_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.3794 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_LPCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.2232 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_LPCCS_CC2_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.1322 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_OECCS_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4834 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_OECCS_CC2_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.485 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_PANDA_S_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.7408 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_QALSW_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1154 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_QALSW_CC2_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.111 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_TEN_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2823 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_TGCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2747 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_TNSKA_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3948 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_WCPP_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.2803 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_WHCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.1458 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E_WHCCS2_CC2_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.8347 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E5DVA1C1_1_B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.4709 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | E5DVA1C1_1_B_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8002 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | EAGLE MTN-PARKER/HICKS 345 KV (DOUBLE B TO B) A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2106 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | EAST LEVEE - NORWOOD 138 KV & NORWOOD - WEST LEVEE 345 KV DCKT A LUPO | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.9201 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8048 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 127.5902 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.0888 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ENNIS - PEBBLE CREEK 138 KV SWITCH (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6627 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ERIKA_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.5341 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | FARMERSVILLE - ANNA SW 345 KV & FARMERSVILLE - VALLEY SOUTH 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0146 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.0669 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | FORNEY - SEAGOVILLE SW/TRI CORNER DCKT 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2089 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | FORNEY-EAST MESQUITE DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0013 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_000575JCKCNTY5UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.063 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_000579JCKCNTY8UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8396 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_000971PRUITT_8US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.187 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_001700TOCO_8US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.009 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_001729VAL_STH_5UB1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0113 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_001777PARIS_8US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.154 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_001877MITCHBND_5UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4291 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_003321REDLAND_5UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0349 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_006100OKLA7AUC0 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8468 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_006111RILEY7BUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1157 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_010012METEOR_5US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.406 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_023906AJSWOPE_5US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0326 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_023908DEAFSMITH_5US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1944 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_023909WALLABY_5US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3502 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_023912OGALLALA_5US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0325 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_023913KRESS_5US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0159 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_059904COTTONWOODUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0129 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_060700GAUSS7AUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.261 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_060716SGSA4AUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0428 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_079000GRAYUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5261 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_079000GRAYUW1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.13 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_120041MLSES_UNIT1UL1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4749 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_120042MLSES_UNIT2UL2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4899 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_120043MLSES_UNIT3UL3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5013 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_120142SCSES_UNIT2UN2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0295 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_120441BR_ARROW_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.091 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_120442BR_ARROW_S2US2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1891 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_120591STAM_SLR_S2US2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1781 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_120821HOPKINS_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1748 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_134953EUNICE_S2US2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0324 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_135501RDOSLR_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0016 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_136341TRBNT_PV_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0565 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_141607AEEC_5UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0803 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_141609ELK_G3UN6 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0515 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_143116SRNOVA2_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0033 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_143261CONGLI_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0783 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_143421PHOENIX_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0028 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_143572SAMSON_3_S2US2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0811 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_143701DELILA_1_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1242 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_143752DELILA_2_S2US2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.032 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_143961MISAE2_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4022 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_144011BRSFORK_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0644 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_144211HRNTSLR_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4282 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_144261EIFSLR_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2852 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_144311FRYE_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.053 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_144312FRYE_S2US2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.053 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_144511TROJAN_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1111 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_144561BAKE_SLR_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2817 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_144562BAKE_SLR_S2US2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2817 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_144721TWOFORKS_B1UB1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0189 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150021MCSES_UNIT6UN6 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3526 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150022MCSES_UNIT7UN7 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3708 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150023MCSES_UNIT8UN8 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.0075 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150041GRSES_UNIT1UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2015 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150042GRSES_UNIT2UN2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5051 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150051HLSES_UNIT3UN3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7208 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150052HLSES_UNIT4UN4 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.9195 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150053HLSES_UNIT5UN5 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8286 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150072SPNC_SPNCE_5UN5 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0086 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150082OLIN_OLING_2UN2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1753 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150083OLIN_OLING_3UN3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3624 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150084OLIN_OLING_4UN4 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1032 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150091LHSES_UNIT1UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.3613 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150092LH2SES_UNIT2UN2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.7937 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150111CPSES_UNIT1UU1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.026 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150112CPSES_UNIT2UU2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.0436 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150132MIL_MILLERG2UN2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0112 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150133MIL_MILLERG3UN3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1375 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150151MDANP_CT1UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.178 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150152MDANP_CT2UN2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1871 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150153MDANP_CT3UN3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1498 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150154MDANP_CT4UN4 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1487 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150155MDANP_CT5UN5 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1846 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_150156MDANP_CT6UN6 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1858 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_151191DEC_AGR_AUN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0063 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_151192DEC_AGR_BUN2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0052 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_151193DEC_AGR_CUN3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0051 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_151194DEC_AGR_DUN4 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0064 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_151371LILY_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0992 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_152081NOBLESLR_R1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0983 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_152082NOBLESLR_R2US2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0671 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_152281ELLISSLR_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0614 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_152581ESTONIAN_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0053 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_152582ESTONIAN_S2US2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0511 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_153141PORT_SLR_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.329 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_153532ELIZA_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.264 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_153911PNGT1_PV_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7614 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_154331CMPDREPV_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0821 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_154411ANOLEBES_B1UB1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1546 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_154421DESERTWL_B1UB1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.023 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_183172GALLOWAY_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0132 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_5920EASTDCTIE | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.3921 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_6103NORTHDCTIE | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1548 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888839BAS_RANCH_POIUC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.2519 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888845DRY_CREEK_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0626 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888848BARRETT_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1066 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888851TRIFECTA_POIUN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4015 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888854PINEFOREST_POIUB1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1713 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888854PINEFOREST_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5271 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888856HOLLY_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1699 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888856HOLLY_POIUS2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.044 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888865MALDIVES_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0023 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888866HANSON_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1429 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888874VIKING_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.309 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888878ERIKA_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3668 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888879BLUBIRD_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.28 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888881SOLAC_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2112 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888882BUZIOS_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0536 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888883QUANT_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0996 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G_888885GALAC_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2352 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | G8DVA1C1_B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.0316 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | GALAC_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2602 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | GRAHAM UNIT 2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5051 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | HANSON_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1952 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | HICKS - EAGLE MTN*PARKER 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4667 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | HICKS -ALLIANCE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3305 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | HIGHNOON_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.172 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | HOLLY_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3474 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | INDIGO_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.115 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | JEWETT - RANCHLAND (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0688 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | JEWETT-BALE*TWINOAK_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.0943 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | JEW-LONG_LAKE-PAL_S_8 (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0071 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | KEMP RANCH - SOAP CREEK / SARDIS 138 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3622 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1092 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | KINGS CREEK - KAUFMAN_8 (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1161 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.0608 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.12 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | KRUM WEST - RILEY A 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.442 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | KRUMW-WEST DENT/DUNHAM 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4341 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000032ROBERTSON-003707CANNON_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1008 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000064MILANO-003683MINERVA1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4412 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000064MILANO-003707CANNON_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.446 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000099BENHUR-000107PRAIRIEHILC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0608 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000107PRAIRIEHIL-000186NAVAROMILSC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0406 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000120TALBRTRIDG-003678ROCKDALE1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3657 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000120TALBRTRIDG-003683MINERVA1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3742 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000186NAVAROMILS-000190DAWSONC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0437 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000190DAWSON-000194PURDONC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0359 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.282 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.2976 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000203SARDIS8-002309WAX_NW_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0383 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000203SARDIS8-012317STERRETTL_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2126 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000220CEDARHILL-000223SAINTPAULC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0141 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000221TRUMBULL8-002229PEBBLCRK_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6248 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000221TRUMBULL8-012344GAMMA_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6509 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000223SAINTPAUL-000404JESSICAC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1435 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000237BLANTON-888875THRESLR_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0394 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000237BLANTON-888889MIDPOINT_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0301 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000240WHITNEY5-000246BOSQUESW5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0568 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000404JESSICA-000419LILLIAN8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1813 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000419LILLIAN8-000439HIGHPOINTC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1133 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000432CONLEY-000436GRANDVIEWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1372 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000432CONLEY-000439HIGHPOINTC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.122 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000436GRANDVIEW-000443SANDFLATSWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1511 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000443SANDFLATSW-000444COVINGTONC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2347 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000444COVINGTON-888859HIGHNOON_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2513 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000570WISECNTY-000571HIDEOUTC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0034 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000571HIDEOUT-000579JCKCNTY8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0791 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000612BLUHORSE-000680NRTHSANGERC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0067 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000612BLUHORSE-000684SPRINGC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0172 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000646LEWISVLSW5_1-002361CRLTN_NW1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0878 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000646LEWISVLSW5_1-021851DUNHAM_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3473 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000842GPL_KINGMTSW-000843GPL_KINGMTTPC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1589 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2394 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000844GPL_NEVILLSW-076000L_NORTMC5_1YC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2572 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000844GPL_NEVILLSW-076002L_BAKERS5_1YC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.056 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000860GPL_GIRVINSW-136341TRBNT_PV_S1C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0565 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000902POES31569-000981SPNCRINT69C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2228 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000970BENDAVIS_5-000973MCCREE_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0348 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000970BENDAVIS_5-002478ROYSE_S5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1823 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_000988W_DENT_5-001730W_KRUM_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0851 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2056 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001141HOLTSS_8-132313ECEC_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1588 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001421WILLOWCK_5-001443HENDRCH_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0394 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001421WILLOWCK_5-011418TECUMSEH_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2084 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001421WILLOWCK_5-011523THOMPRCE_5C2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1677 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001421WILLOWCK_5-031875RAMHORNH_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.302 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001421WILLOWCK_5-031875RAMHORNH_5C2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.302 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001429JACKSBRO_5-011736BIRDDOG_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0589 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001436PARKER_5-001859BASECAMP_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.224 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001436PARKER_5-002081HICKS_SW1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2811 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001444BROWN_5-151756RADN_TLINEC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0531 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001685FARMVLSW_5-001729VAL_STH_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0419 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001685FARMVLSW_5-002461ROYSE_N5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1475 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001685FARMVLSW_5-002478ROYSE_S5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1507 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001685FARMVLSW_5-011689CYCLONE_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1958 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001685FARMVLSW_5-011700SALTILLO_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0854 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001690VALLYSES1_5-001729VAL_STH_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0304 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001690VALLYSES1_5-011683PACIFICSW_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0158 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 103.0335 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001695MOSES_5-001697SULSP_SS1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1034 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.003 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2765 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001696MOSES1_T5-888854PINEFOREST_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.003 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001697SULSP_SS1_5-888847CARTWHEEL_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2626 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001730W_KRUM_5-006111RILEY7BC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0726 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001730W_KRUM_5-006111RILEY7BC2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0726 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001730W_KRUM_5-011736BIRDDOG_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2587 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001730W_KRUM_5-021851DUNHAM_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1023 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001730W_KRUM_5-152087NOBLESLR_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4385 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001739DENISND_T8-006949DENISDMA_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0209 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001757ALLA_HUB_P8-012351OUTERLOOP_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0007 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001757ALLA_HUB_P8-012468EPCO_P8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0081 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001839STONCRK_8-011757DORCHEST_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0105 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001839STONCRK_8-012677HAGGRTY_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0221 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.7408 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001841BURGRLK_T8-001852ROANOKE2_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0435 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001852ROANOKE2_8-002000SEVENTNLKS_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0798 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001873BENBRK_5-002285CARMICHL_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0196 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001874BENBRK_A_8-018741BENBRK_SRA_8C2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.017 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001875BENBRK_B_8-018751BENBRK_SRB_8C2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0047 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001880ROCKYCRK_5-888879BLUBIRD_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.066 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 104.3869 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 104.7687 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.0106 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001906VENUS_S5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.573 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 104.9619 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001906VENUS_S5-015201FORBESR2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.1781 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001906VENUS_S5-888857OYSTER_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 110.5085 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001906VENUS_S5-888880DES_WILL_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.0004 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4509 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.6818 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001907VENUS_N5-011885EVRMNTIE3_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1583 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001907VENUS_N5-011902BRITTNRD2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6499 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001907VENUS_N5-015200FORBESR1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.9024 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001907VENUS_N5-068091NAVARROC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 110.5471 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001911WEBB1_5-001929CENTURY1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4807 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001911WEBB1_5-011902BRITTNRD2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5639 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001918SHRYAUTO1_5-001929CENTURY1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3795 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001919SHRY_A8-002257PARKROW1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3093 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001920SHRY_B8-002258PARKROW2_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3938 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001921LIGGETTA1_5-002632MILLERRD_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.5765 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001922LIGGETT_N8-002124INT_AIR1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0645 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001928LIGGETT_3T5-002406NORWD1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.9491 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.0363 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.5007 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001951HANDLEYD_8-012110WHITETAP2_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.072 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001978WESTON1_8-002544CHAMBVLE_P8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0712 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001978WESTON1_8-002546MCKNY2_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0645 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001979WESTON2_8-002341TRINITYFL_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0633 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_001979WESTON2_8-002625BLOOMDALE_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0632 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002000SEVENTNLKS_8-002018WROANOKE1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0531 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002019KIMBALL1_8-002020STHLAKE1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0368 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002026CLYVIL1_T8-002027BEARCK1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0045 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002027BEARCK1_8-012043WPKELLR3_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0385 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002044WATAGAS_T8-002047HALTOM1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0254 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002047HALTOM1_8-002074DEENSW_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0254 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002114TRINITY3_8-002115HURSTN_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.038 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002114TRINITY3_8-012109WHITETAP1_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0464 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002124INT_AIR1_8-002128WATSON1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0308 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 127.5902 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002237STERTRD_8-002317STERRETT1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1551 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2615 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002257PARKROW1_8-002260POLY_AM1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.267 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002258PARKROW2_8-002259LTV1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3542 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002259LTV1_8-002262GRANDPR1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3218 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002260POLY_AM1_8-012492LAKECRST_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1235 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002262GRANDPR1_8-012491FSHCRK2_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2436 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002263GELLER_8-003079SSWWT2T_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.768 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002263GELLER_8-003083WILMER1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7497 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002279CLEBRNSW_8-002290CLEBRN_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1331 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002286PADERA_8-002310MDLTHTXI2_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.33 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002286PADERA_8-002311MDLTH_N_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2504 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002289SOAPCRK_8-002303KEMPRNCH_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2105 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002289SOAPCRK_8-002310MDLTHTXI2_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3297 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002290CLEBRN_8-002291CLEBRN_W_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1901 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002291CLEBRN_W_8-037810TNHILL_CO_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2333 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2604 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002305AIRPRD_T8-002307MDLTHTXI1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2347 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002307MDLTHTXI1_8-012307NEWBRCH_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1626 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002308MDLTH_S_8-002309WAX_NW_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0866 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002308MDLTH_S_8-012307NEWBRCH_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1435 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002313MDLTH_N_8-002314MDLTHBOX_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2033 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002314MDLTHBOX_8-003054CHCLRKRD1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1117 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002315WAX_PMP2_8-002319WAX_PMP1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1711 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002315WAX_PMP2_8-002320WAX_N_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1744 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002316MG_IND_T8-002319WAX_PMP1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1601 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002317STERRETT1_8-012317STERRETTL_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1073 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002320WAX_N_8-002321WAX_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2464 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2497 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.1035 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.0735 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002341TRINITYFL_T8-002374ANNASW_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0746 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002361CRLTN_NW1_5-002387HACKBRY1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0596 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002361CRLTN_NW1_5-033646LEWISVLSW5_2C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1141 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002372COLLINSS1_5-002373ANNASW_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2187 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002374ANNASW_8-002544CHAMBVLE_P8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0623 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002406NORWD1_5-012398TOPEKA1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8651 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002420CHILSW1_5-002431DESSW1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7278 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002420CHILSW1_5-002847LOOP9_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3039 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002421CHILSW_S8-002999DVIL1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.174 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002422CHILSW_N8-002491FSHCRK1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0712 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002422CHILSW_N8-003049EGLFD2_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0528 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 104.7986 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 104.7986 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 109.4447 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 108.5864 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002432TRICRN1_5-888878ERIKA_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.3011 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002434SGVLSW1_8-002732MARSHLL_P8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0065 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002434SGVLSW1_8-003076SGVL1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8869 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.9137 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.8914 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002445PARKDB2_8-002960PLGRV1T_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0388 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002450CNVLSW_E8-002916EZACH2_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0169 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002461ROYSE_N5-002464CASHSW_T5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2173 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002472ROYSE_N_8-012703FATE_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0092 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002478ROYSE_S5-002485POETRY_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6761 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002485POETRY_5-003103SHAMBRGR_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2272 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002491FSHCRK1_8-012492LAKECRST_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1234 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002512ALLENSW2_8-012513ALLENSWS2_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0484 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002529MCKNY1_8-002560MCKNY_TI_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0599 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002529MCKNY1_8-002625BLOOMDALE_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0633 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002530MCKNY_SW1_8-002554MCKNY_S1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0026 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002530MCKNY_SW1_8-002560MCKNY_TI_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0356 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002534CRGRNCH1_8-002554MCKNY_S1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0026 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002546MCKNY2_8-002561MCKNYWHT_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0337 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002547MCKNY_SW2_8-002561MCKNYWHT_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0058 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002724KAUFMN_8-002728KAUFMN_S_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1314 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002724KAUFMN_8-012715FORNEYS_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1739 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002726KEMP_S_8-002774KNGCRK_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5153 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002726KEMP_S_8-003264SEVENPTS_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5726 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002727CRANDALL1_8-002732MARSHLL_P8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0515 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002727CRANDALL1_8-012715FORNEYS_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1743 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002728KAUFMN_S_8-002774KNGCRK_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1527 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002993STHTN2_8-002994LVBRD1T_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0082 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_002994LVBRD1T_8-002999DVIL1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0453 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003049EGLFD2_8-003050SORCEY1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0326 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003051SORCEY2_8-003052DVILS1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0191 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003053CHILTPL_8-003054CHCLRKRD1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0603 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003058CHILTPL4_8-003059DESHPR1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0201 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003076SGVL1_8-003077KLEBRG1T_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.835 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003077KLEBRG1T_8-003079SSWWT2T_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7738 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003100MARTINLK_5-003102TYLERGND_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.2859 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003100MARTINLK_5-003116MTENTRPR_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1163 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.2929 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003110STRYKER_8-003112SMRFLDMT_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0271 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003110STRYKER_8-888855LUMBERJACK_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0332 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003112SMRFLDMT_8-003253JAXVLSW_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.016 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003118LUFKNSS_8-003349TMPLINLA_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0725 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 105.5491 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 108.6427 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003127TRINIDAD_8-003260NIPAKTAP_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6815 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003133RICHLND2_5-003381BIGBRNW_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.2693 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003134RICHLND1_5-003380BIGBRNE_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 104.0867 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003147TROUPSS_8-003156WALNUTGRV_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0114 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003156WALNUTGRV_8-003227WHITEHSE_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.005 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 125.7272 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003167ENTERPRI_8-003188WILLSPNT_9C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0347 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003174CANTNSW_8-003181EDGEWOOD_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2413 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003181EDGEWOOD_8-003188WILLSPNT_9C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1402 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003260NIPAKTAP_8-003265MANKIN_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6802 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003262CEDRCREK_8-003263CEDRCKPU_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6537 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003262CEDRCREK_8-003287WILL_WHT_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6407 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003263CEDRCKPU_8-003265MANKIN_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6651 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003264SEVENPTS_8-003287WILL_WHT_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6215 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003271PALSTNS_8-003272PALESTNE_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0052 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003306STEKLY_DAM_5-003404BELFALLS_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3737 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003306STEKLY_DAM_5-003409LAKE_CRK1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1642 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.4804 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003374FILESVALY_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8536 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003377LITTLEPOND_5-003687BELL_E_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 103.3207 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003377LITTLEPOND_5-003704HOGCREEK_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.5517 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003384STJOHNS_5-003409LAKE_CRK1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 103.1677 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003384STJOHNS_5-003711BALE_S5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.5911 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003388FOURBTHRS_5-003405THOUSE__5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0619 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003388FOURBTHRS_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2045 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003389FORTSMITH_5-152333FILESSLR_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0102 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003390JEWETT_S5-003711BALE_S5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.3278 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003390JEWETT_S5-046020LIMEST_POI_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4299 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003391JEWETT_N5-003396NUCOR_ST1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0498 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003391JEWETT_N5-046020LIMEST_POI_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0127 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003394JEWETTA_8-003501SEATEAG_T_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0576 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003400TWIN_OAK_N5-039950TNTNP_ONE_3C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6953 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003400TWIN_OAK_N5-039950TNTNP_ONE_3C2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6953 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003400TWIN_OAK_N5-888846TIDWELL_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2908 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003400TWIN_OAK_N5-888846TIDWELL_POIC2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2908 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003402LAKE_CRK2_5-003403LAKE_HALL_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.295 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003403LAKE_HALL_5-003405THOUSE__5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3434 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003404BELFALLS_8-003414TEMP_SS__5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4816 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003409LAKE_CRK1_5-013405THOUSE_A_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0673 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003410LAKE_CRK1_8-003702RIESEL_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1798 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.125 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.0159 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003495BLAIN_8-003501SEATEAG_T_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0303 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003518BLUMPUMP1_8-037810TNHILL_CO_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2439 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003522HILLBORO1_8-003546WHITNEY__8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0187 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003678ROCKDALE1_8-003740SLRPRTY_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2728 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003687BELL_E_5-003705BRANGUS_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 103.5988 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003704HOGCREEK_5-039950TNTNP_ONE_3C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.8385 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003705BRANGUS_5-003706GIBSON_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.8926 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003706GIBSON_5-039950TNTNP_ONE_3C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.9995 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003723OLYMPUS_SW-003454MONTFTSS__8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2101 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_003740SLRPRTY_8-003750VOSSLAKE_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1362 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5966 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3331 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4179 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2368 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_005380SHAULA-005915SO_TEX__345AC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2392 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1812 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_005915SO_TEX__345A-042400REFUGE_POI_5C27 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.193 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_005915SO_TEX__345A-042530JONCRK__B345C&1-MS | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0527 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.0098 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_006903BOZE-151372LILY_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1356 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_007077L_AMOSCR5_1Y-183171GALLOWAY_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0871 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_007270L_BELLSO8_1Y-046220PETERS__B138C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2745 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_007389L_PINNAC8_1Y-135019TI_SOLAR_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0568 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_008127LAN_CTY4A-008130LAN_CTY4BCS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1619 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_008715RADIANT7A-008728COBRA7AC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5611 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_008728COBRA7A-081003HABER7AC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6682 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1533 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_011084RIVERTON_5-888839BAS_RANCH_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0038 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_011270DOGHOUSE_5-023876CLEARFRK_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3597 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_011270DOGHOUSE_5-134805PROSPERO_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0937 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_011270DOGHOUSE_5-135183PRSPERO2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0429 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_011273NELSON_8-135503RDOSLR_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0016 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_011406CENTBLUF_5-182255HOLSTN_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0071 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_011418TECUMSEH_5-011419COODYCROSS_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0823 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_011419COODYCROSS_5-060514CLEARCRO7BC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0012 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_011523THOMPRCE_5-060515CLEARCRO7AC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2158 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_011684BRIGHTR_5-011689CYCLONE_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0828 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_011688THORNTRE_5-143625SAMSON_1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4541 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_011688THORNTRE_5-143705DELILA_1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.547 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_011757DORCHEST_8-012468EPCO_P8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0087 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_011809COPPERHD_8-143424PHOENIX_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0028 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_012329SHANKLSW_8-012344GAMMA_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6505 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_013401TIGERCK_5-013405THOUSE_A_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0671 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_013401TIGERCK_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2875 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.3277 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.6898 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_021851DUNHAM_5-033646LEWISVLSW5_2C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3269 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_023910WINDMILL_5-140753HRFDWIND_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0045 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_023920ABERNATH_5-141607AEEC_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3528 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_040240CENTER_POI_5-042000P_H_R___B345C97 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0731 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_042400REFUGE_POI_5-042440HAWKIN_POI_5C27 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0809 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_042500DOW____POI_5-043060SPEDWY_POI_5C18 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1667 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_044000W_A_P__POI5A-044160WOLF___POI_5C64 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1238 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_044000W_A_P__POI5A-088800HOUDINI7AC39 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2241 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_044040BAILEY_POI_5-044060BLUE___POI_5C72 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.3881 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_044040BAILEY_POI_5-044090CDRCRK_POI_5C72 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0666 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_044060BLUE___POI_5-044220JULIA__POI_5C72 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.64 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_044160WOLF___POI_5-044200HILLJE__B345C64 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4306 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_044200HILLJE__B345-044220JULIA__POI_5C72 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.8268 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_046510TOMBAL__B138-046511TOMBAL_T66_8C66 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0428 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_059906LONGDRAW_138-134145JUNO_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0865 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_059906LONGDRAW_138-134342LGDRAW_S8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0183 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_059909NOVA_138-059998NOVA8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4225 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_059909NOVA_138-143115NOVA1SLR_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2029 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_059911MHOS-183406JADE_HI_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1197 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_060011NEBULA7A-183525ANDMDSLR_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0815 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_060059PENUMBRA7A-060500EDITHCLA7AC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0323 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_060059PENUMBRA7A-060506AVOGADRO7AC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0097 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_060393PIGCREEK4A-134245TAYGETE_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0251 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_060464AZUREPOI7A-060514CLEARCRO7BC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0032 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_060504TESLA7B-060511SALVARE7AC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0089 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_060504TESLA7B-142815MISAE_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0784 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_060515CLEARCRO7A-068000WSHACKC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0485 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_060515CLEARCRO7A-068000WSHACKC2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0485 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_068000WSHACK-888867INDIGO_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0298 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_068001CLAYTON_345-068014OPENSKYC2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2545 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_068004PHNTMHL-068014OPENSKYC2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0391 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_068005SAMREACTR-068051REATAC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3185 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_068006NAVREACTR-068008LATIMERC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3802 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_068008LATIMER-068051REATAC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2827 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_068010ROMNEY1_W-068011ASPIREC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4565 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_068011ASPIRE-068051REATAC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.1094 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_068020ROMNEY1_E-068025WRANGLERC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.456 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_076002L_BAKERS5_1Y-135327REDBARN_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0135 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_143575SAMSON_3_5-143625SAMSON_1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1594 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_143705DELILA_1_5-143757DELILA_2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1631 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.7188 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_888846TIDWELL_POI-039950TNTNP_ONE_3C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3053 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_888846TIDWELL_POI-039950TNTNP_ONE_3C2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3053 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_888847CARTWHEEL_POI-002464CASHSW_T5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2937 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2765 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_888855LUMBERJACK_POI-003147TROUPSS_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0526 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_888857OYSTER_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 108.4982 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_888867INDIGO_POI-068001CLAYTON_345C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0897 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_888878ERIKA_POI-003105ELKTON_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8927 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_888880DES_WILL_POI-001916LIGGETTA2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.0616 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L_888889MIDPOINT_POI-003518BLUMPUMP1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2468 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L10012900 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1619 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L201000169 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3543 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | L20255426 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3543 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LAKE CREEK - LAKE HALL/TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.091 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LAKE CREEK - LAKE HALL_5 (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3613 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LAKE CREEK-RATTLESNAKE/RIESEL_5_8 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1796 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LAKE CREEK-RATTLESNAKE/ST JOHNS_5 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 103.1676 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LATIMER_REATA_P7F1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 103.791 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LCRA TSC_T21457 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0027 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LCRA TSC_T237_T389_1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0095 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LCRA TSC_T255_TAE3121_1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1387 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LCRA TSC_T389_T518 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0062 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LCRA TSC_T698_T217_A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2768 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.4636 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.5957 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.7329 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.7984 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.0952 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.0652 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 105.2988 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT-NORWOOD 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.4557 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 105.0016 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 105.0203 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 108.8851 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2626 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | LUMBERJACK_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0545 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MALDIVES_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0078 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MANKIN-KINGSCREEK_8 (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.527 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 104.9207 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 105.4314 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MB208402551425515 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0457 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MB210110210115 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0658 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MB210140210145-AAAAA | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6616 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MB210140210145-AAAAB | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7227 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MB210140210145-AAABA | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3307 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MB210140210145-AABA | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5925 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MB210140210145-AABB | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2639 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MB210140210145-ABAAA | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5469 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MB210140210145-ABAAB | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4867 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MB210140210145-ABABB | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3906 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MB210140210145-ABBA | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4195 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MB2551220811-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0045 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MB2551520840-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0457 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MB2551525514 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.9727 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MB255152551420840 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.9691 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MB2726627277 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1442 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MINERVA - CANNON_8 (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4461 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.1813 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.3339 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNIT 4 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4643 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7634 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 104.5754 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | MOSES-SULPHUR SPRINGS SW 345-138 KV AUTO SULPHUR SPRINGS SW 345-138 KV AUTO #1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1827 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1349 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1349 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1531 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | NEW-GRAHAM-PARKER 345 KV-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2418 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | NEW-HILLSBORO-CLEBURNE_SW_8 (SINGLE B TO B )-1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1531 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7199 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.3404 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | NORTHWEST CARROLLTON - LEWISVILLE SW (BEPC) 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6324 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | NORWOOD - LIGGETT/CEDAR HILL DCKT 345 KV (DOUBLE B TO B) NEW_LOAD | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3375 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | NORWOOD - WEST LEVEE 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.9792 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | NORWOOD-LIGGETT 345 & MOUNTAIN CREEK - LIGGETT 138 KV DCKT A BLUBONT | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.7864 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | ODESSA EHV - NORTH MCCAMEY 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1643 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | OYSTER_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 109.0524 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P1-2_(8130-43190-1) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1619 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7.1_CP8-CP9_CP8-CP9 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0395 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1/C5-CTT-14 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0272 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>JULIA | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.6191 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T0205B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0344 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T0303C | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0283 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T0692 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0545 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T0921A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0659 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T0921BX | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1821 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T0945A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2572 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T0976BX | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5542 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T1827BY | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3576 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T1827D | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6542 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T1827FX | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.54 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T1827GX_ERC | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6816 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T1827K | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6854 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T1839X1_ERC | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2586 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T1839X2_ERC | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2024 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T2222GX | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2695 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T2476A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.04 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T2525D | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1629 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T2573A_78RADIAL | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0957 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T2682EX1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0343 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T2682EX2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0382 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T2682GY1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0386 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T2682GY2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0387 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T3595X | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0004 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T3944Z_ERC | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.237 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T4848K | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4526 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T6472CX1A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 103.516 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T6472CX1B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 103.2495 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T6472E | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.8887 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T6472F | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8443 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T6472G | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4265 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T6472H | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0542 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T6681D | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0307 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T6781B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1349 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T6795A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1689 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T7381E | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.043 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T7498A_ERC | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8515 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T8181H | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2439 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T8686BX | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0386 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T8690B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1271 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>T0684B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0057 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>T4848A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0351 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>T5959A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2722 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>T5959B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3101 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>T7979G | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0751 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>T7979M | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0387 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>T8686A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0368 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1>>T2727L | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4935 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | PALESTINE - CROCKETT*PALESTINE SOUTH - ELKTON_8_9 (DOUBLE B TO B)_SUM2019 B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0065 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | PARIS NW-PARIS-PARIS SW138 KV (SINGLE B TO B) A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0963 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | PARIS SW-MOSES 345 KV-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1143 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | PARIS SW-PACIFIC SW/VALLEY S SW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1364 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | PARKER-COMANCHE PEAK 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0311 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.9439 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV DCKT & EAGLE MOUNTAIN - WEATHERFORD 138 KV LINE | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.871 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | PHNT_WSHACK_P7-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2366 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | PHNT_WSHACK_P7-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1314 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | PINEFOREST_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.9546 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | RAMHORN - DUNHAM DC 345 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2952 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | RAMHORN - HICKS 345 AND BASE CAMP - BENNET 138 (DOUBLE B TO B) CKT 2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2016 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (COMMON TOWER) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.0026 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2016 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | RAMHORN - WILLOW CREEK DC 345 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.1058 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | RANCHLAND - MEXIA_8 (SINGLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0167 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0171 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | REAT_SKYD_P7F2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8779 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | RENNER - NORTHWEST CARROLLTON 345 KV & RENNER - ALLEN SW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1673 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | RENNER DPL 345-138 KV AUTO #1 (SINGLE AUTO) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1536 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | RICH-BBROWN (DOUBLE B TO B)A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 106.6894 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | RILEY - TESLA & TESLA - SALVARE | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1566 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | RYBRN_P1-2_CANTON TAP-CANTON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2518 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | RYBRN_P1-2_VINSON-LORING_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0483 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | S_001924LIGGETT_S81 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0344 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | S_002074DEENSW_81 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0114 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | S_002303KEMPRNCH_81 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0312 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | S_002370COLLINSS1_81 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0134 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | S_002399WLEVEE_E81 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0251 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | S_002411MTCK_W81 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0101 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | S_002421CHILSW_S81 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0127 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | S_002422CHILSW_N81 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0126 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | S_002523PL_TENNY_81 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0384 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | S_002578CRLTNE_81 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1009 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | S_002782MRSN_E81 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0009 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | S_002783MRSN_W81 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0009 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | S_003106ELKTON_81 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0094 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5124 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.7228 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.3953 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 103.6711 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | SAND LAKE - SOLSTICE 345 KV DCKT LINE (DOUBLE B TO B) WIN 2027 - FUTURE | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2354 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | SCUR_CLY_P7 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.0249 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | SEAGOVILLE SW - FORNEY/TRICORNER DCKT 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.174 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | SEAGOVILLE SW-KAUFMAN-TERRELL SW (SINGLE B TO B) A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5444 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | SHAMBURGER - POETRY_5(SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2272 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | SHAMBURGER-BLACKFORK/POETRY_8_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1463 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | SHERRY - FISH CREEK 138 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0269 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | SHERRY-TIMBERVIEW*VENUS 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8539 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | SHERRY-VENUS 345 KV (SINGLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2903 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | SOAP CREEK - CEDAR HILL / SARDIS 138 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0868 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | SOLACE_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1671 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | STERRETT 5410-SARDIS (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0404 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | STONE CREEK SW-BONHAM SW 69 KV & VALLEY -COMMERCE 138 KV LINE A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.023 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | T_000981SPNCRINT69-000982DN_STEAM_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2228 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | T_003103SHAMBRGR_5-003104SHAMBRGR_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1788 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | T_059908NOVA_345-059998NOVA8CT1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4225 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2847 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TEMPLE - BELFALLS_5 (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4816 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TEMPLE PECAN CREEK/BELFALLS - TEMPLE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6121 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TEMPLE PECAN CREEK/BELFALLS - TRADINGHOUSE/STEAKLEYDAM_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7725 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TEMPLE PECAN CREEK/STEAKLEYDAM - TRADINGHOUSE/LAKE CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5796 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3377 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | THOUSE-LCRK*PCNCRK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1746 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | THRESLR_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0573 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.7477 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.0883 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TIMBERVIEW-VENUS 345 KV DOUBLE-CIRCUIT LINE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.031 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 107.5158 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8444 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8555 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TRICORNER - TYLER GRANDE (single B TO B) new_load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8958 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.5074 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.9624 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.4864 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 123.4937 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TRIFECTA_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4022 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TRINIDAD - MANKIN (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6804 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TRIN-MANKIN*EUSTACE SOUTHEAST(DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7264 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TRIN-NIP*MA (DOUBLE B TO B)B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.6273 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 117.1682 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 104.1402 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 104.6564 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 120.6611 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TULECANYON-TESLA (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0505 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 105.9524 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 105.9249 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 106.1084 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VALLEY S-ANNA SW 345 KV & VALLEY S-FARMERSVILLE 345 KV | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2308 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VALLEY S-VALLEY SW 345 KV & VALLEY S-PARIS SW 345 KV | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2038 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VALLEY SW-COMMERCE SW 138 KV BONHAM SW 138-69KV AUTO #1 A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.037 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3241 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 105.7377 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 103.7452 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS - WEBB 345KV (SINGLE B TO B) BRITTONRD2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5621 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 106.642 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 126.3822 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 123.9714 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.4382 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 104.3767 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 104.8545 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-FORT SMITH SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.2911 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.6466 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.5785 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.4796 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.6138 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.9458 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.8021 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-SAM SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.9969 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | VIKING_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3578 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | Voss Lake - Minerva 138 kV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3826 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | WAP - HOUDINI & STP - SHAULA | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.564 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 105.0652 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 105.5154 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | WILLOW CREEK - CLEAR CROSSING (THOMAS PRICE) & COODY CROSSING - TECUMSEH 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV SUM 2026 - FUTURE (TRIPLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5983 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | WILLOW CREEK - HENDERSON RANCH 345 KV & WILLOW CREEK - JACKSBORO 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1764 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | WILLOW CREEK - TECUMSEH/THOMAS PRICE 345 KV DCKT WIN 2023 - FUTURE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7858 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | WILLOW CREEK - THOMAS PRICE\TECUMSEH CREEK 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV WIN 2023 - FUTURE (TRIPLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.75 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.2805 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | WINDMILL - AJSWOPE (SINGLE B TO B) SUM 2028 - FUTURE | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3498 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7608 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C2_345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2353 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | WSHACK_LATIMER_L1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3754 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | WSHACK_LATIMER_P7 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 104.185 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | WSHACK_REATA_L2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3138 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-ENNSTRAC_8-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5102 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-ENNSTRAC_8-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2458 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-GRHAMSES1_8-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2015 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-HANDLEYC_8-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7208 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-HANDLEYC_8-3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.8286 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-HANDLEYD_8-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.9195 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-LKHB_1T8-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.3613 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-LKHB_2T8-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.7937 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MARTINLK_5-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4749 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MARTINLK_5-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4899 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MARTINLK_5-3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.5013 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MDLTHELP_5-5 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1846 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MDLTHELP_5-6 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1858 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MDLTHELP_N5-3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1498 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MDLTHELP_N5-4 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1487 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MDLTHELP_S5-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.178 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MDLTHELP_S5-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.1871 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MTCK_6T8-6 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3526 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MTCK_7T8-7 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.3708 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MTCK_8T8-8 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 102.0075 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MTENTRPR_5G-4 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0342 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-STRYKER_8-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0295 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-TENASKA_8-1_REVA (UNIT1) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0239 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-TENASKA_8-1_REVA (UNIT2) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0239 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-TENASKA_8-1_REVA (UNIT3) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0308 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-WHCCS2_4-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.4643 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-WHCCS2_5-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 101.2077 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-WLFHMDPT_5-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.7609 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 ( 2466) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-WLFHOSTR-3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.2353 | -
TLSTR , TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BIGONION_5 (2466) -> GLASGOW_POI (888877) CKT 1 | Pre-contingency | 345 | 345 | Amps | 2729.4439 | - | - | - | - | 116.3704 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BIGSPRIG_8 ( 1322) -> COSDEN_8 ( 1332) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 1200.7211 | - | 107.2829 | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BIGSPRIG_8 ( 1322) -> STEER_8 (10044) CKT 1 | L_011325HOWD2599_8-011331BEALSCRK_8C1 | 138 | 138 | Branch Amp | 1648.3767 | 100.8811 | - | 100.2965 | 100.2251 | 100.9678 | 101.4803 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BIGSPRIG_8 ( 1322) -> STEER_8 (10044) CKT 1 | L_011325HOWD2599_8-023836NATDAM_8C1 | 138 | 138 | Branch Amp | 1648.3767 | 104.8687 | - | 104.7644 | 105.149 | 106.2448 | 106.8054 | -
TCNPE | COAST | COAST | COAST, COAST | BIPORT_X82B8 (42190) -> CAVERN_X82T8 (43330) CKT 82 | Pre-contingency | 138 | 138 | Amps | 874.3927 | - | - | - | - | 111.1042 | 116.1302 | -
TCNPE | COAST | COAST | COAST, COAST | BIPORT_X82B8 (42190) -> OYSCRK_C82_8 (43336) CKT 82 | L_042050CLUTE___B138-043240SINTEK_X26B8C26 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | 104.6077 | 109.7665 | -
TCNPE | COAST | COAST | COAST, COAST | BIPORT_X82B8 (42190) -> OYSCRK_C82_8 (43336) CKT 82 | L_043240SINTEK_X26B8-043365CAMDEN_X26B8C26 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 103.4514 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BLANTON ( 237) -> MIDPOINT_POI (888889) CKT 1 | G_154011MIDPOINT_S1US1 | 138 | 138 | Branch Amp | 779.8411 | - | - | - | - | 101.5364 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BLANTON ( 237) -> MIDPOINT_POI (888889) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 779.8411 | - | - | - | - | 108.3733 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BLANTON ( 237) -> MIDPOINT_POI (888889) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 779.8411 | - | - | - | - | 105.2418 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BLANTON ( 237) -> MIDPOINT_POI (888889) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 779.8411 | - | - | - | - | 101.0033 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING2A ( 8119) -> MDFLDTP2A ( 8552) CKT 1 | L_008102EL_CAMPO4A-008679ARROZ4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 107.3959 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING2A ( 8119) -> MDFLDTP2A ( 8552) CKT 1 | L_008104LANCTYPM4A-008127LAN_CTY4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 100.5282 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING2A ( 8119) -> MDFLDTP2A ( 8552) CKT 1 | L_008104LANCTYPM4A-008679ARROZ4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 100.2489 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING2A ( 8119) -> MDFLDTP2A ( 8552) CKT 1 | L10006-1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 106.3557 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING2A ( 8119) -> MDFLDTP2A ( 8552) CKT 1 | L10010006-1B | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 100.2876 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 108.6469 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 104.3066 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 102.6562 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 100.4864 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | DVCPA1C21B_1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 104.8433 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | DVCPA1C21B_2 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 105.3506 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | E_B_DAVIS_CC1_TRAIN | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 103.9741 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | E_NEDIN_CC1_TRAIN | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 101.0016 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | E_NUECES_B_CC1_TRAIN | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 104.0165 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | E_VICTORIA_CC1_TRAIN | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 102.5256 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | G_120261TREB_SLR_S1US1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 104.2889 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 112.0971 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 129.2501 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 110.9783 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 114.9166 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 106.1334 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_005380SHAULA-005915SO_TEX__345AC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 106.2822 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 130.4236 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 115.7163 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_008102EL_CAMPO4A-008679ARROZ4AC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 103.2116 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_008104LANCTYPM4A-008127LAN_CTY4AC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 101.1802 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_008104LANCTYPM4A-008679ARROZ4AC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 101.1093 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_008117GANADO4A-008118EDNA4AC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 101.638 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_008117GANADO4A-008192PULSAR4AC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 101.8807 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_008118EDNA4A-008172VICTORIA4AC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 100.7153 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_008140JOSLIN4A-120263TREB_SLR_8C1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 104.2873 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 113.4418 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 104.3325 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L10006-1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 101.8375 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | L10010006-1B | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 101.1591 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | M10000271115801 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 101.3386 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | MB100002711580 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 101.3386 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | P7-1_E1>>T1839X1_ERC | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 105.1293 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | P7-1_E1>>T1839X2_ERC | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 104.6327 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | P7-1_E1>>T2764Y_ERCa | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 108.1058 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | P7-1_E1>>T3944Z_ERC | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 129.1101 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | SAN_PAT_CON | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 100.5274 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | STP - HOUDINI & STP - SHAULA | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 107.8956 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | T100002 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 103.0929 | - | -
TAEPTC | COAST | COAST | COAST, COAST | BLESSING4A ( 8121) -> LOLITA4A ( 8125) CKT 1 | WAP - HOUDINI & STP - SHAULA | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 104.7653 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BLUMPUMP1_8 (3518) -> TNHILL_CO_8 (37810) CKT 1 | Pre-contingency | 138 | 138 | Amps | 861.8416 | - | - | - | 103.3538 | 115.843 | 106.8498 | -
RSHELL | COAST | COAST | COAST, COAST | BOGGYSTR (500254) -> BOG_T2T (110960) CKT 2 | P1-2_(110952-110962-1) | 12.47 | 1 | Branch MVA | 62.5 | 100.2759 | - | - | - | - | - | -
RSHELL | COAST | COAST | COAST, COAST | BOGGYSTR (500255) -> BOG_T4T (110962) CKT 4 | P1-2_(110953-110960-1) | 12.47 | 1 | Branch MVA | 62.5 | 100.3116 | - | - | - | - | - | -
RSHELL | COAST | COAST | COAST, COAST | BOGGYSTR (500258) -> BOG_T2T (110960) CKT 2 | P1-2_(110952-110962-1) | 12.47 | 1 | Branch MVA | 62.5 | - | 100.3644 | - | - | - | - | -
RSHELL | COAST | COAST | COAST, COAST | BOGGYSTR (500259) -> BOG_T2T (110960) CKT 2 | P1-2_(110952-110962-1) | 12.47 | 1 | Branch MVA | 62.5 | - | - | 100.2776 | 100.2855 | 100.2817 | 100.2824 | -
RSHELL | COAST | COAST | COAST, COAST | BOGGYSTR (500259) -> BOG_T4T (110962) CKT 4 | P1-2_(110953-110960-1) | 12.47 | 1 | Branch MVA | 62.5 | - | 100.4009 | - | - | - | - | -
RSHELL | COAST | COAST | COAST, COAST | BOGGYSTR (500260) -> BOG_T4T (110962) CKT 4 | P1-2_(110953-110960-1) | 12.47 | 1 | Branch MVA | 62.5 | - | - | 100.3136 | 100.3213 | 100.3178 | 100.3182 | -
TONCOR | NORTH | NORTH | NORTH, NORTH | BOISPUMP_T8 ( 1835) -> BONHAM_P8 ( 1593) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 958.0667 | - | - | - | - | 110.2512 | 101.6123 | -
TONCOR | NORTH | NORTH | NORTH, NORTH | BONHAM_8 ( 1808) -> BONHMSS1_8 ( 1760) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.8326 | - | -
TONCOR | NORTH | NORTH | NORTH, NORTH | BONHAM_P8 ( 1593) -> VALLYSES1_8 ( 1691) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 958.0667 | - | - | - | - | 106.3354 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | BONILLA7A ( 8573) -> RIOHONDO7A ( 8318) CKT 1 | L_008601CEBOLLA7A-008902RIOHONDO7CC1 | 345 | 345 | Branch Amp | 1989.7664 | - | - | - | 110.8819 | 110.7794 | 109.4029 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | BONILLA7A ( 8573) -> RIOHONDO7A ( 8318) CKT 1 | L1000097 | 345 | 345 | Branch Amp | 1989.7664 | - | - | - | 110.8819 | 110.7794 | 109.4029 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | BONILLA7A ( 8573) -> RIOHONDO7A ( 8318) CKT 1 | M10000841000093-1A | 345 | 345 | Branch Amp | 1989.7664 | - | - | - | - | - | 118.0064 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | BONILLA7A ( 8573) -> RIOHONDO7A ( 8318) CKT 1 | P7/C5-SHRY-3 | 345 | 345 | Branch Amp | 1989.7664 | - | - | - | - | - | 116.5276 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | BONILLA7A ( 8573) -> RIOHONDO7A ( 8318) CKT 1 | T100001 | 345 | 345 | Branch Amp | 1989.7664 | - | - | - | - | - | 101.6051 | -
ERCOT | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BRA_AVR1_CT2 (170135) -> VON_ROSE ( 5475) CKT T2 | E5T5A1C1_B | 345 | 18 | Branch MVA | 193 | - | - | - | 100.08 | - | - | -
ERCOT | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BRA_AVR1_CT2 (170135) -> VON_ROSE ( 5475) CKT T2 | G_170126CALAVER_JKS2UL2 | 345 | 18 | Branch MVA | 193 | - | - | - | 100.6654 | - | - | -
ERCOT | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BRA_AVR1_CT2 (170135) -> VON_ROSE ( 5475) CKT T2 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | 18 | Branch MVA | 193 | - | - | - | 102.9525 | - | - | -
ERCOT | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BRA_AVR1_CT2 (170135) -> VON_ROSE ( 5475) CKT T2 | N5GSU2_B | 345 | 18 | Branch MVA | 193 | - | - | - | 100.6654 | - | - | -
ERCOT | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BRA_AVR1_CT2 (170135) -> VON_ROSE ( 5475) CKT T2 | N5U3A1C1_1_B | 345 | 18 | Branch MVA | 193 | - | 100.0551 | - | 100.3159 | - | - | -
ERCOT | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BRA_AVR1_CT2 (170135) -> VON_ROSE ( 5475) CKT T2 | S2SM1_B_1 | 345 | 18 | Branch MVA | 193 | - | - | - | 101.5378 | - | - | -
TONCOR | WEST | WEST | WEST, WEST | BRAND_8 ( 1315) -> GOLDENSW_8 ( 1067) CKT 1 | SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 1 & SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 105.4061 | - | -
TONCOR | WEST | WEST | WEST, WEST | BRAND_8 ( 1315) -> GOLDENSW_8 ( 1067) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 111.9157 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRANGUS_5 ( 3705) -> BELL_E_5 ( 3687) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | - | 103.5166 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRANGUS_5 ( 3705) -> BELL_E_5 ( 3687) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | - | 101.838 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRANGUS_5 ( 3705) -> BELL_E_5 ( 3687) CKT 1 | L_003377LITTLEPOND_5-003687BELL_E_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | 100.1832 | 120.6151 | 133.2911 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRANGUS_5 ( 3705) -> BELL_E_5 ( 3687) CKT 1 | L_003377LITTLEPOND_5-003704HOGCREEK_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 112.4574 | 124.2711 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRANGUS_5 ( 3705) -> BELL_E_5 ( 3687) CKT 1 | L_003384STJOHNS_5-003409LAKE_CRK1_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | - | 100.5991 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRANGUS_5 ( 3705) -> BELL_E_5 ( 3687) CKT 1 | L_003704HOGCREEK_5-039950TNTNP_ONE_3C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.6998 | 115.7454 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRANGUS_5 ( 3705) -> BELL_E_5 ( 3687) CKT 1 | LAKE CREEK-RATTLESNAKE/ST JOHNS_5 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | - | 100.5998 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRANGUS_5 ( 3705) -> BELL_E_5 ( 3687) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | - | 107.0182 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRANGUS_5 ( 3705) -> BELL_E_5 ( 3687) CKT 1 | P7-1_E1>>T6472CX1A | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | - | 100.7527 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRANGUS_5 ( 3705) -> BELL_E_5 ( 3687) CKT 1 | P7-1_E1>>T6472CX1B | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | - | 100.1726 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRANGUS_5 ( 3705) -> BELL_E_5 ( 3687) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | - | 105.3517 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRANGUS_5 ( 3705) -> BELL_E_5 ( 3687) CKT 1 | TEMPLE PECAN CREEK/BELFALLS - TRADINGHOUSE/STEAKLEYDAM_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | - | 101.9756 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRANGUS_5 ( 3705) -> BELL_E_5 ( 3687) CKT 1 | TEMPLE PECAN CREEK/STEAKLEYDAM - TRADINGHOUSE/LAKE CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | - | 100.0814 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRANGUS_5 ( 3705) -> BELL_E_5 ( 3687) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | - | 100.3511 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRANGUS_5 ( 3705) -> BELL_E_5 ( 3687) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | - | 100.0515 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | BAS_RANCH_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.1429 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.0062 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | BLUBIRD_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.969 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | CLUTCH_CITY_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.394 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | E_DDPEC_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.6595 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | E_FRNYPP_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9962 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | E_FRNYPP_CC2_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.022 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | E_FTR_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.5018 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | E_JCKCNTY2_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.364 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | E_KMCHI_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0559 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | E_KMCHI_CC2_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0868 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | E_PANDA_S_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9887 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | E_PANDA_T1_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9686 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | E_PANDA_T2_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0104 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | E_TGCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.6341 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | E_WCPP_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.7426 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | E_WHCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3429 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | E_WHCCS2_CC2_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.3631 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_000575JCKCNTY5UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7294 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_000579JCKCNTY8UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2746 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_006100OKLA7AUC0 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7688 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_110351STP_STP_G1UU1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4136 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_110352STP_STP_G2UU2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3613 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_120041MLSES_UNIT1UL1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2691 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_120042MLSES_UNIT2UL2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3193 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_120043MLSES_UNIT3UL3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3343 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_120131OGSES_UNIT1AUL1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9948 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_120132OGSES_UNIT2UL2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9944 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_150023MCSES_UNIT8UN8 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4393 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_150101LEG_LEG_G1UL1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.7988 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_150102LEG_LEG_G2UL2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8955 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_150111CPSES_UNIT1UU1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.2166 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_150112CPSES_UNIT2UU2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.194 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_150741SCES_UNIT1UL1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.314 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_170126CALAVER_JKS2UL2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7482 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_888839BAS_RANCH_POIUC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.144 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_888879BLUBIRD_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.658 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | G_RIO_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6753 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | J5LCA1C1_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.678 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.0675 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_001839STONCRK_8-140002SHER1_TLC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9773 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.5147 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.0184 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.011 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9924 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_007270L_BELLSO8_1Y-046220PETERS__B138C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6731 | 101.5631 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_008102EL_CAMPO4A-008679ARROZ4AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.2365 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_008127LAN_CTY4A-008130LAN_CTY4BCS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 113.7652 | 113.3503 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_042100HUDSON_POI_8-888849CLUTCH_CITY_POIC04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.5212 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_042150BASF___POI_8-042210BRZPRT_S02_8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.419 | 107.2178 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_042150BASF___POI_8-042810HOFMAN_X02B8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.3194 | 109.0774 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_042210BRZPRT_S02_8-042215COPPER_X02B8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.037 | 105.8562 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_042215COPPER_X02B8-042540JONCRK__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8351 | 104.4136 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_042810HOFMAN_X02B8-042880LKJACK_S02_8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.4437 | 109.1991 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_042880LKJACK_S02_8-043170RETREV__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.202 | 110.9092 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_042940MONSAN_POI_8-043070PETSON_X04B8C04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.019 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_042960MUSTNG_S04_8-043500WEBSTR_B138AC&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9522 | 102.2281 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_042985DYANN__POI_8-043190S_LANE__B138C60 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4822 | 104.4083 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_043070PETSON_X04B8-044890SNUG___POI_8C04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.1294 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044010W_A_P__POI8A-044342IMPERL05T3_8C05 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.3735 | 105.8441 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044010W_A_P__POI8A-044652SIENNA05T1_8C05 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.5708 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044015W_A_P__POI8B-044020ALIEF__S09_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 108.2242 | 108.4723 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044015W_A_P__POI8B-044180DEWALT_S02_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.576 | 105.6906 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044020ALIEF__S09_8-044310HAYES___09B8C09 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.8358 | 104.1236 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044120BRITMR__B138-044310HAYES___09B8C09 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8989 | 102.1965 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044180DEWALT_S02_8-047150H_O_C___B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.2498 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044190E_BERN__B138-044740WALLIS_S65_8C65 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 127.6195 | 124.4219 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044200HILLJE__B345-044220JULIA__POI_5C72 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.3077 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044230FLEWLN__B138-044280FTBEND__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | 118.7006 | - | 102.8043 | - | 151.1304 | 153.3772 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044230FLEWLN__B138-044510OBRIEN_B138AC&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.504 | 102.7256 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044260FRANZ___09B8-044910ZENITH__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1558 | 102.7046 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044342IMPERL05T3_8-044670STAFRD_S05_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.3139 | 103.7952 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044450MASON__S25_8-044510OBRIEN_B138AC25 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5387 | 102.2149 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044590ROARK__S25_8-047310JENETA__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.3584 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044640SEALY__S65_8-044700GEBHRT_X65B8C65 | 138 | 138 | Branch Amp | 1137.9656 | 113.6689 | - | - | - | 145.505 | 149.7875 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044640SEALY__S65_8-046220PETERS__B138C65 | 138 | 138 | Branch Amp | 1137.9656 | 109.5174 | - | - | - | 140.6789 | 145.0354 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044670STAFRD_S05_8-044760WCHASE_S05_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5233 | 101.0123 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_044700GEBHRT_X65B8-888872SKYSLY_POIC65 | 138 | 138 | Branch Amp | 1137.9656 | 115.1299 | - | - | - | 147.0792 | 151.3393 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_046510TOMBAL__B138-046511TOMBAL_T66_8C66 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.1651 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_047170H_O_C__POI_8-048262SOWYCK26TP_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.7403 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_047175H_O_C__SB138-047660GARROT__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.9344 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_888849CLUTCH_CITY_POI-042960MUSTNG_S04_8C04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1451 | 102.4113 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L_888872SKYSLY_POI-044740WALLIS_S65_8C65 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 127.0545 | 123.8671 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | L10012900 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 113.7651 | 113.3503 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | LAKE CREEK - RATTLE SNAKE 345 KV WITH SANDY UNIT (SINGLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.314 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | LCRA TSC_T698_T217_A | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6342 | 101.542 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | MB210140210145-AAAAB | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1584 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.5346 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9694 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | N5GSU2_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7482 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P1-2_(33.1X_SODG_44342) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.8579 | 103.3349 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P1-2_(40600-120095-1) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.5018 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P1-2_(46020-49208-GL) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.7988 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P1-2_(46020-49209-GL) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8955 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P1-2_(8130-43190-1) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 113.7651 | 113.3503 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P1-2_HOC_BUS_REACTOR | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.6187 | 107.9171 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7.1_CP8-CP9_CP8-CP9 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 101.3417 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>JULIA | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.0461 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T0202C | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.4264 | 109.204 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T0202E | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.4661 | 107.2786 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T0202H | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8334 | 104.4129 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T0205A | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5544 | 101.9532 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T0205B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 113.0998 | 113.5448 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T0226 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.5575 | 106.861 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T0405 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1415 | 102.5099 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T0463 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0023 | 102.274 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T0493 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8201 | 102.0733 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T0924B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.5133 | 104.5935 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T0924C | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.686 | 101.7771 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T0945A | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.498 | 102.0432 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T0990A | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.7736 | 102.7093 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T0990B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0395 | 101.9791 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T1827D | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.0607 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T1827H | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5482 | 100.5814 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T1899X | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7161 | 101.6634 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T2525C | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.0957 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T2573B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 111.4622 | 105.8149 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T2682EX1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.9203 | 107.9883 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T2682EX2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.2666 | 108.3206 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T2682GY1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.3015 | 108.355 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T2682GY2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.3017 | 108.3552 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T3790A | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.9597 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T3790B_90RADIAL | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.8087 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T7475C | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.2867 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T9797B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5088 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>>T9899A | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 115.7687 | 110.2759 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>T0202GX | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.0374 | 107.0126 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>T0205CX | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 115.57 | 115.2598 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>T0524AY | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.0901 | 103.5077 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | P7-1_E1>T2682DX | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.4405 | 105.5326 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | Pre-contingency | 138 | 138 | Amps | 874.3927 | - | - | - | - | 124.0249 | 126.0358 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | RAT_SNAKE-SNDY_CREEK_5 (SINGLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.314 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | SKYSLY_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 131.8725 | 128.6608 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | T100002 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.2091 | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | TWIN_OAK_BKR_8995_345_OAK_GROVE_SINGLE_B_T0_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9943 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | TWIN_OAK_BKR_9000_345_OAK_GROVE_SINGLE_B_T0_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9948 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.8478 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.7427 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | XFMR-MARTINLK_5-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2691 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | XFMR-MARTINLK_5-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3193 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | XFMR-MARTINLK_5-3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3343 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | XFMR-MTCK_8T8-8 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4393 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | XFMR-SANDYCRK_5-01 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.314 | - | -
TCNPE | COAST | COAST | COAST, COAST | BRAZOS_S09_8 (44100) -> FLEWLN__B138 (44230) CKT 09 | XFMR-WHCCS2_5-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.665 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | 3WT_000988W_DENT_5_000986W_DENT_8_000972W_DENT_T2 C 2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1333 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | 3WT_000988W_DENT_5_000986W_DENT_8_000984W_DENT_T1 C 1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1333 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | 3WT_001859BASECAMP_5_001860BASECAMP_8_011861BASECAMP1_3 C 1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3704 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | 3WT_001859BASECAMP_5_001860BASECAMP_8_011866BASECAMP2_3 C 2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2741 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0078 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | 3WT_013125TDADTMOD_5_003127TRINIDAD_8_120151TRSES_UNIT6 C 1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8417 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | AEN_LP-AU¦DL_2013 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2304 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | AEN_LY-FPP¦CIS | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.165 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | AEN_P1-1_GEN_SH5A+5C | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.2555 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | AEN_P2HLJ345_RB_570_610_1(94OF224): | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4418 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.5577 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW - MONTICELLO 345 KV (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0812 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW - PLANO TENNYSON 345 KV & ALLEN SW - RENNER 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1121 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW 345-138 KV AUTO #1 (SINGLE AUTO) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1008 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6262 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5729 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3237 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5734 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3195 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7264 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.536 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7996 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.6513 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.729 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.5335 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8024 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.6499 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0204 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.8564 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0216 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.8459 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN-MOSES 345-138 AUTO-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.084 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLEN-MOSES 345-138 AUTO-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6638 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7558 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.6707 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7665 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.5989 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALVORD - WISE COUNTY 138 KV & BENNETT RD - CHICO WEST 69 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 108.4569 | 100.8171 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ALVORD-WFS 138 KV A | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.8379 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ARGENTA_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.7944 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | B2-COD-1_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6773 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BARRETT_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0782 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BAS_RANCH_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.7909 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.438 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2355 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BENBROOK-CALMONT 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0358 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BENBROOK-CARMICHAEL BEND*BENBROOK SYCAMORE CRK 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2594 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BENBROOK-PARKER*CARMICHAEL BEND 345 KV WITH BENBROOK AUTO (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7165 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.1546 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_004_1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1028 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_005_1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | 103.8291 | 108.1146 | 132.4758 | 122.7447 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_006 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 111.6454 | 104.5952 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_014_2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.7788 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_015_2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.2199 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_114 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 113.4583 | 106.2148 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_130 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2879 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_20 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.4646 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_21 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.5353 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_211 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.141 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_22 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4052 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_223 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.64 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_23_2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2415 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_240 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0726 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_241 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.7255 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_242 | 138 | 138 | Branch Amp | 1200.7211 | - | - | 105.1719 | 112.8274 | 135.7762 | 127.0379 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_243 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 106.0186 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_244_2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1051 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_245 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 108.4938 | 100.8528 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_246 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 112.5222 | 105.396 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_2541 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 112.6001 | 105.3871 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_255 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.847 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_256 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.031 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_2661_2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3967 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_2681_1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6356 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_271 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3273 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_281 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3567 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_304_2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0025 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_307_2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.8233 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_311_2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2663 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_414 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3273 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_432 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.8403 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BEPC_458 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 109.7806 | 102.841 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.9023 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BIGBRN__5-JEWETT_S5 & BIGBRN__5-JEWETT_N5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1822 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2916 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BITTER CREEK SW (LCRA) - CATTLEMEN SW & BITTER CREEK SW (LCRA) - SWEETWATER EAST 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4208 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | BLUBIRD_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.1037 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | CACTUS_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6164 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | CARLSON - STEGER (LCRA)_8 (SINGLE B TO B ) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.045 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | CARMICHAEL BEND-TIMBERVIEW 345 KV*DECORDOVA-CLEBURNE 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6789 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | CARTWHEEL_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.008 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.1231 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8486 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | CLUTCH_CITY_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2147 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | COODY CROSSING - TECUMSEH AND CLEAR CROSSING - THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4404 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | DERMOTT - COTTONWOOD/MHOS (WETT) CKT 1 345 KV (SINGLE B TO B) C | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2252 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | DERMOTT - KIRCHHOF CKT 1 & DERMOTT - KIRCHHOF CKT 2 345 KV (DOUBLE B TO B) C | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0948 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | DERMOTT - KIRCHHOF CKT 1 345 KV WIN 2023 - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.2149 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | DES_WILL_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4156 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | DRY_CREEK_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.5525 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | DUNE - WINK/YUKON 138 KV 2019 SUM - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3552 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.928 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | DVCPA1C21B_1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1341 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_AMOCOOIL_CC2_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.1413 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_AMOCOOIL_CC2_TRAIN_NSO | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.5803 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_B_DAVIS_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.9219 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_BASTEN_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.2026 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_BOSQUESW_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5134 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_BOSQUESW_CC2_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.252 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_BRAUNIG_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.1132 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_BTE_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.8069 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_BVE_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.3292 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_BYU_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0262 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_CAL_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3109 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_CBEC_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4205 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_CBEC_CC2_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5131 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_CBECII_CC3_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.1047 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_CBY4_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.0462 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_CCEC_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.294 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_CHE_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.9307 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_CVC_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.9041 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_DDPEC_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.1522 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_DIB_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9144 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_DUKE_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.7411 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_ETCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.94 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_FERGCC_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.9301 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_FLCNS_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2065 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_FREC_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.3245 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_FREC_CC2_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.5434 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_FRNYPP_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.2676 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_FRNYPP_CC2_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.2843 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_FTR_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.2359 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_GUADG_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.6056 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_GUADG_CC2_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.5768 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_INGLCOSW_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.1274 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_JCKCNTY2_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.7875 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_KMCHI_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.9218 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_KMCHI_CC2_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.9543 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_LGE_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.1102 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_LOSTPI_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.7683 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_LPCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.419 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_LPCCS_CC2_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.0844 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_NEDIN_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.9224 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_NUECES_B_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.9114 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_OECCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.8003 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_OECCS_CC2_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.8115 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_PANDA_S_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.7545 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_PANDA_T1_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.0399 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_PANDA_T2_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.0396 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_PSA_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.9313 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_PSG_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.0563 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_QALSW_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8438 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_QALSW_CC2_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8182 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_RAYBURN_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4305 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_TEN_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.665 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_TGCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.644 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_THW_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0542 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_THW_CC2_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0543 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_TNSKA_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9395 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_TXCTY_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.2326 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_VICTORIA_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1489 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_WCPP_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.485 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_WHCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.2284 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | E_WHCCS2_CC2_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.2163 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | EAGLE MOUNTAIN - HICKS/WEATHERFORD 138 KV (DOUBLE B TO B) NEWLOAD | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.0818 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | EAGLE MTN-PARKER/HICKS 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.5849 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | EAGLE MTN-WEATHERFORD 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.7137 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ELMAX_POI_Con | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.1925 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ELPATR_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0694 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.685 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ERIKA_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0564 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0513 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_000099BENHURUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1221 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_000575JCKCNTY5UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.1895 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_000971PRUITT_8US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2399 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_001777PARIS_8US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2406 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_001877MITCHBND_5UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3518 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_003134RICHLND1_5UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7225 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_003134RICHLND1_5UN2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7225 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_003306STEKLY_DAM_5US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.522 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_003321REDLAND_5UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.329 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_003391JEWETT_N5US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0556 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_003420TEMP_PEC__8US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2306 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_003478NAVARRO1_8US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3046 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_003706GIBSON_5US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2129 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_003707CANNON_8US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2512 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_003717TORTOISE_5US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2797 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_003717TORTOISE_5US2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0097 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_005506FURHMANSW8US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0718 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_006100OKLA7AUC0 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.954 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_006111RILEY7BUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2384 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_007041L_JOHNDU5_1YUN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5628 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_007044L_MARION5_1YUN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.3693 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_007048L_GARFIE5_1YUN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.5028 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_008249ANGSTRM7AUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7062 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_008573BONILLA7AUW1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6686 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_008707DRYFRIOUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1594 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_010012METEOR_5US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.3405 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_023906AJSWOPE_5US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1609 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_023908DEAFSMITH_5US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8835 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_023909WALLABY_5US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3654 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_023912OGALLALA_5US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1656 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_023913KRESS_5US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0937 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_040000CEDARP_B345AUC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.192 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_040700GRNBYU__B345UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.8024 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_040710GRNBYU_POI8AUN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.7935 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_042199BSTCM12_36_8US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5065 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_042400REFUGE_POI_5UW1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0596 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_042440HAWKIN_POI_5US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.266 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_043060SPEDWY_POI_5US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1822 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_043060SPEDWY_POI_5US2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3342 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_043060SPEDWY_POI_5US4 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.3771 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_043340GLFTIE_POI_8UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.2807 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_043990ELMATO_POI_5US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1034 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_043990ELMATO_POI_5US2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.5335 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_044040BAILEY_POI_5US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0936 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_045500T_H_W__POI_5UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.8413 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_045515T_H_W__POI_8UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.8349 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_047170H_O_C__POI_8UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0559 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_048262SOWYCK26TP_8UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8538 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_059904COTTONWOODUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1381 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_060700GAUSS7AUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.2513 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_060716SGSA4AUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7973 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_068004PHNTMHLUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1953 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_068014OPENSKYUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1476 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_068025WRANGLERUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2654 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_068051REATAUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.2532 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_079000GRAYUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.1939 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_079000GRAYUW1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5267 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_079007YELLOWWOLFUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3031 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_080039LUCERO7AUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0394 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_080039LUCERO7AUS2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7448 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_080219LOBO7AUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8714 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_080219LOBO7AUS2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3065 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_080355DELSOL7AUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3493 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_085000N_SHARPE7AUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0886 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110013WAP_WAP_G3UN3 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5353 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110014WAP_WAP_G4UN4 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.1101 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110015WAP_WAP_G5UL5 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.8841 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110016WAP_WAP_G6UL6 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.9796 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110017WAP_WAP_G7UL7 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.472 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110018WAP_WAP_G8UL8 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.6288 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110071CBY_CBY_G1UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.466 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110072CBY_CBY_G2UN2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.5037 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110146DOW_DOW_GT96UP1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1843 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110280AMO_AMOCO_G1UPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0773 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110281AMO_AMOCO_G2UPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0775 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110282AMO_AMOCO_G3UPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0773 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110351STP_STP_G1UU1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.0295 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110352STP_STP_G2UU2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.0323 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110662CHE_CHEST1UPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2102 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110701LHM_CVC_G4UPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1829 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110731BTE_BTE_G1UPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3358 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110732BTE_BTE_G2UPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0692 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110733BTE_BTE_G3UPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0693 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_110734BTE_BTE_G4UPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0693 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_111861BCK_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1556 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_111862BCK_S2US2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1706 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_112261SPACECI_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3683 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_112351OLDHCKRY_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2898 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_112491JAY_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0167 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_112612ROW_S2US2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0895 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_113051GARCITAS_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3266 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_113111LUNIS_CK_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.0084 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_113341TNGLWDPV_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3162 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_113751CASCADE_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3068 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_113921PARLIMNT_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3585 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_120041MLSES_UNIT1UL1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.6371 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_120042MLSES_UNIT2UL2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.6451 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_120043MLSES_UNIT3UL3 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.6531 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_120071TNP__TNP_O_1UL1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2052 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_120072TNP__TNP_O_2UL2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2052 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_120131OGSES_UNIT1AUL1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.2383 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_120132OGSES_UNIT2UL2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.2387 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_120141SCSES_UNIT1AUN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3382 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_120142SCSES_UNIT2UN2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.5301 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_120151TRSES_UNIT6UN6 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8417 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_120261TREB_SLR_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0939 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_120441BR_ARROW_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0149 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_120442BR_ARROW_S2US2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2984 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_120591STAM_SLR_S2US2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.295 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_120821HOPKINS_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2861 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_120871AZALEA_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.15 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_132311ECEC_G1UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1971 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_132312ECEC_G2UN2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1971 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_132481RIGGINS_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0669 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_132781CASLGP_UNIT1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1596 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_132941SPTX12B_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0532 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_133841WAYMARK_W1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1607 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_134091OBERON_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1488 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_134141JUNO_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.018 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_134751FOWLR_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0328 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_134801PROSPERO_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.009 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_134951EUNICE_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1757 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_134953EUNICE_S2US2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3913 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_135111ARAGORN_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2106 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_135321REDBARN_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3459 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_135501RDOSLR_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2216 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_136341TRBNT_PV_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7884 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_136441SWIFTAIR_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0069 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_141607AEEC_5UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4135 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_141609ELK_G3UN6 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3119 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_143116SRNOVA2_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1636 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_143701DELILA_1_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1154 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_143702DELILA_1_S2US2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1154 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_143961MISAE2_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.4391 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_144011BRSFORK_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5911 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_144064INERTIA_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1808 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_144161NOVA2SLR_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1402 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_144211HRNTSLR_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.7926 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_144261EIFSLR_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6055 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_144311FRYE_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2674 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_144312FRYE_S2US2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2674 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_144511TROJAN_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2512 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_144561BAKE_SLR_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5989 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_144562BAKE_SLR_S2US2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5989 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150021MCSES_UNIT6UN6 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3632 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150022MCSES_UNIT7UN7 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3273 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150023MCSES_UNIT8UN8 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.392 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150042GRSES_UNIT2UN2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.5777 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150051HLSES_UNIT3UN3 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.4989 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150052HLSES_UNIT4UN4 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.074 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150053HLSES_UNIT5UN5 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.0772 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150082OLIN_OLING_2UN2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1815 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150083OLIN_OLING_3UN3 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5131 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150091LHSES_UNIT1UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.6367 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150092LH2SES_UNIT2UN2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.9006 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150101LEG_LEG_G1UL1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.3144 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150102LEG_LEG_G2UL2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.3177 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150111CPSES_UNIT1UU1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.172 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150112CPSES_UNIT2UU2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.294 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150151MDANP_CT1UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0166 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150152MDANP_CT2UN2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1298 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150153MDANP_CT3UN3 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0974 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150154MDANP_CT4UN4 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.096 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150155MDANP_CT5UN5 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1016 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150156MDANP_CT6UN6 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1152 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_150741SCES_UNIT1UL1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.099 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_151371LILY_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1616 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_151421STRATEGC_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.11 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_151551VISION_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0023 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_151752RADN_SLR_S2US2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0169 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_152081NOBLESLR_R1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2167 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_152082NOBLESLR_R2US2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.087 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_152181SUNVASLR_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0553 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_152331FILESSLR_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0774 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_152431MERCURY_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2833 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_153141PORT_SLR_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.81 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_153381FIVEWLLS_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1701 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_153532ELIZA_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2524 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_153631DORADO_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1617 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_153781JAGUARSP_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6972 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_153861TOKIO_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0969 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_153911PNGT1_PV_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.75 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_153961GAIA_SOL_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0793 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_154061DIVER_PV_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0014 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_154161LANGER_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.45 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_154221ASHCRKSL_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3487 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_154281CLINGHAM_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9134 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_154331CMPDREPV_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.47 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_160101B_D_B_DAVIG1UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.4922 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_160131SAN_SANMIGG1UL1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.9924 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_160151INGLCOS_CTG1UPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4266 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_160152INGLCOS_CTG2UPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4266 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_160153INGLCOSW_STGUPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.401 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_160201LGE_LGE_GT1UPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3483 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_160202LGE_LGE_GT2UPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3445 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_160261CCEC_GT1UPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1963 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_160262CCEC_GT2UPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1963 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_160263CCEC_ST1UPE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2849 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_160391PAP1_PAP1UW1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0626 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_160392COTTON_PAP2UW1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1683 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_160741LV1_LV1AUW1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1567 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_160742LV1_LV1BUW2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1603 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_160982CAMWIND_G1UW1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0112 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_161651PATWND_UNIT1UW1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2734 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_161951STELLA_W1UW1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1364 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_162251CHALUPA_W1UW1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0421 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_162541MCLNSLR_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2672 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_162791HRZN_SLR_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2532 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_163021NEBULA_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0556 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_163071ALGODON_W1UW1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0231 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_163221CORAZON_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2965 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_163321SPARTA_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0362 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_163521PEREGRN_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9828 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_163641CHARGER_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.5992 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_163691REDONDA_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6218 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_163881TULSITA_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6411 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_163931OUTPOST_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.9696 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_170071GID_GIDEONG1UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1479 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_170072GID_GIDEONG2UN2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1716 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_170073GID_GIDEONG3UN3 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.5288 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_170101FPPYD_FPP_G1UL1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.1255 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_170102FPPYD_FPP_G2UL2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.0975 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_170103FPPYD_FPP_G3UL3 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.02 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_170126CALAVER_JKS2UL2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.8539 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_170191HAY_HAYSENG1UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7019 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_170192HAY_HAYSENG2UN2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8234 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_170193HAY_HAYSENG3UN3 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8169 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_170194HAY_HAYSENG4UN4 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7212 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_170521E_BLACK_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0409 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_170671CACHENA_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.3367 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_170821EBELLSLR_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3632 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_170901SHLA_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2166 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_170951SHLA_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2166 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_171021AURE_SLR_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2058 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_171091MPP_N1UN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5128 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_171111MANDORLA_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4299 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_171161SYPBRNCH_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5857 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_182501RAMBLR_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2078 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_183172GALLOWAY_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4226 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_183351RATLIFF_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0046 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_183402JADE_S2US2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0069 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_183451CROWDEDS_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2675 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_183522ANDMDSLR_S2US2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0133 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_183571SUNRAY_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2707 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_183621ZIER_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0861 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_183781ANG_PV_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1881 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_5920EASTDCTIE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.8416 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_6103NORTHDCTIE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3738 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888839BAS_RANCH_POIUC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.79 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888841ELMAX_POIUN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.1611 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888845DRY_CREEK_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.317 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888848BARRETT_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0519 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888849CLUTCH_CITY_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0642 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888851TRIFECTA_POIUN1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.2253 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888854PINEFOREST_POIUB1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0515 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888854PINEFOREST_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.167 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888856HOLLY_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1529 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888856HOLLY_POIUS2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4355 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888857OYSTER_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5435 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888858ARGENTA_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0473 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888859HIGHNOON_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0582 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888861LEON_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2542 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888865MALDIVES_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2336 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888866HANSON_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1231 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888870BTTM_GRSS_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.4748 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888871ELPATR_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0649 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888872SKYSLY_POIUN2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.09 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888874VIKING_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8807 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888877GLASGOW_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4535 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888878ERIKA_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5039 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888879BLUBIRD_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.4305 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888881SOLAC_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.969 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888882BUZIOS_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3241 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888883QUANT_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9362 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888885GALAC_POIUS1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3322 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888887CONNOLLY_B1UB1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5905 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_888888FEWELL_S1US1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0761 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | G_RIO_TRAIN | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.8895 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | GLASGOW_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.8709 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | GRAHAM UNIT 2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.5777 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | HANSON_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.2356 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | HIGHNOON_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0307 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | HOLLY_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.0529 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | J5CT1_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3375 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | J5CT2_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3368 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | J5CT3_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3374 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | J5GSU1_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3375 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | J5GSU2_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3368 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | J5GSU3_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3374 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | J5GSU4_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3136 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | J5LCA1C1_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.8891 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | J5ST1_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3136 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | JACKSBORO SW-BOWMAN SW 345 KV A | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0773 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | JW-CROCKETT (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0487 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | JW-CROCKETT (SINGLE B TO B)-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0487 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | KRUM WEST - RILEY A 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0726 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | KRUMW-WEST DENT/DUNHAM 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.9572 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000295STEPHENVIL8-000324HANNIBALC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9081 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000306BUNKER-000312LONGC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2483 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000312LONG-000331RWMILLERC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3203 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000320JAYBIRD-000324HANNIBALC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0657 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000320JAYBIRD-000331RWMILLERC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7516 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000501HILLTOP8-000508RIKERC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 101.1717 | 122.6117 | 114.7453 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000501HILLTOP8-000534VEALJNCTNC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6492 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000508RIKER-000516ZIONHILLC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 101.1699 | 122.6093 | 114.7431 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000511AGNESSWTCH-000534VEALJNCTNC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.8522 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000511AGNESSWTCH-001592WTHFRDSS_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.1942 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000516ZIONHILL-000543SWIMMERC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 102.5389 | 124.0096 | 116.0755 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000520ALEDOSW-000529LGVESSC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3501 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000526DICEY-000529LGVESSC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3517 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000537CNTERPOINT-000541RENOC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3026 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000537CNTERPOINT-000545BRIARC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9667 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000541RENO-000572AURORAC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.0244 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000541RENO-000595KEETERC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | 103.3556 | 111.0784 | 134.1102 | 125.2978 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000543SWIMMER-000588WILLOWC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 103.1291 | 124.6279 | 116.6707 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000545BRIAR-000548BOYDC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7128 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000548BOYD-000573NEWARKC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5729 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000570WISECNTY-001564CHCOGHLL1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 108.1389 | 100.4863 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000572AURORA-000576RHOMEC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.9293 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000573NEWARK-000576RHOMEC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4483 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000576RHOME-000585CHISOLMC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.258 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000576RHOME-000598ELNAC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3315 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000579JCKCNTY8-000580WSTBROOKC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 103.4479 | 124.9681 | 116.9978 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000579JCKCNTY8-000600BRIDGEPORTC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.2157 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000579JCKCNTY8-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | 105.0014 | 112.663 | 135.7606 | 126.8836 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000580WSTBROOK-000588WILLOWC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 103.2483 | 124.7459 | 116.7846 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000583DECATUR-011551DE_EMGCY1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0598 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000584WOODIE-000598ELNAC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2377 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000584WOODIE-011551DE_EMGCY1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0623 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000585CHISOLM-000637ROSEMARYC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.3933 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000590PERCHHILL-000600BRIDGEPORTC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.7169 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000590PERCHHILL-000608CRAFTONC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.5502 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000595KEETER-000596COTTONDALEC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | 103.9411 | 111.6508 | 134.7081 | 125.8746 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000596COTTONDALE-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | 105.0037 | 112.6646 | 135.7624 | 126.8848 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000602AVONDALE-000637ROSEMARYC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.8523 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000602AVONDALE-000640ROANOKEC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.5655 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000608CRAFTON-000620BOWIE8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.4053 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000610PATTSNST-001469SUNSETSW_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2854 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000612BLUHORSE-000680NRTHSANGERC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.703 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000612BLUHORSE-000684SPRINGC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.9077 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000616CARTER-001469SUNSETSW_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9669 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000616CARTER-001470NEWPRT_P8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6191 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000618LONESTAR-001559ALVORD_T8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.6329 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000618LONESTAR-001561ALVORD1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.4282 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000620BOWIE8-000741DYEMOUNDC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 112.8863 | 105.7142 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000621BOWIE9-000632JOHNSONSWC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.033 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000640ROANOKE-001854ROANOKE1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.812 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000672RECTORROAD-000680NRTHSANGERC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7305 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000684SPRING-000691VALLEYVIEWC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 114.1315 | 106.9555 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000684SPRING-011989MASCH_BR1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.291 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000690MYRA-000691VALLEYVIEWC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 114.7942 | 107.6046 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000690MYRA-000695MUENSTERC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 111.5761 | 104.4835 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000695MUENSTER-000730WOLFRIDGEC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 112.3328 | 105.2265 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000730WOLFRIDGE-000746STJO8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 109.2799 | 102.2005 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000741DYEMOUND-000762HARDYSWC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 112.4618 | 105.3356 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000746STJO8-000762HARDYSWC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 112.207 | 105.1146 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000842GPL_KINGMTSW-000843GPL_KINGMTTPC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.2831 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.1 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000860GPL_GIRVINSW-136341TRBNT_PV_S1C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7884 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000902POES31569-000981SPNCRINT69C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6773 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000917POCKRUS138-001985CORINTH1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1116 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_000988W_DENT_5-001730W_KRUM_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8077 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.5803 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001141HOLTSS_8-132313ECEC_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1379 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001421WILLOWCK_5-001443HENDRCH_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4436 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001421WILLOWCK_5-031875RAMHORNH_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5414 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001421WILLOWCK_5-031875RAMHORNH_5C2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5414 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001436PARKER_5-001859BASECAMP_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.2905 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001436PARKER_5-002081HICKS_SW1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8208 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001444BROWN_5-151756RADN_TLINEC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7457 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001464WFALLS_S_8-001467NORTHSTR_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1939 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001467NORTHSTR_8-001468LKAROWHD_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4111 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001468LKAROWHD_8-001470NEWPRT_P8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5268 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001469SUNSETSW_8-001559ALVORD_T8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.6099 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001561ALVORD1_8-001562CHCOWEST_T8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.4271 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001562CHCOWEST_T8-001563CHCOWEST_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3068 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001562CHCOWEST_T8-001564CHCOGHLL1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 106.6309 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001592WTHFRDSS_8-015015FLAT_RCK_T8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 106.2281 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.6433 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0813 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6517 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001696MOSES1_T5-888854PINEFOREST_POIC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0813 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001730W_KRUM_5-006111RILEY7BC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0487 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001730W_KRUM_5-006111RILEY7BC2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0487 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001730W_KRUM_5-011736BIRDDOG_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3212 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001730W_KRUM_5-152087NOBLESLR_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1787 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.7298 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001860BASECAMP_8-002062AZLE1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.7425 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001873BENBRK_5-002285CARMICHL_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1776 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001880ROCKYCRK_5-888879BLUBIRD_POIC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6134 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001902JHNSONSW_P5-015106LILLIAN1C_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5304 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2928 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4037 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.9073 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4657 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001906VENUS_S5-015201FORBESR2_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7499 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001906VENUS_S5-888880DES_WILL_POIC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0863 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.1122 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8011 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001907VENUS_N5-015106LILLIAN1C_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0125 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001907VENUS_N5-015200FORBESR1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2213 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001921LIGGETTA1_5-002632MILLERRD_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2394 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001928LIGGETT_3T5-002406NORWD1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0048 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3236 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5147 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_001986KRUM_T8-011989MASCH_BR1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.6309 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_002062AZLE1_8-015015FLAT_RCK_T8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 106.2222 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.9023 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.685 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_002281GODLEY_8-002283AIRLIQD_P8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0576 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_002281GODLEY_8-002888CARMICHL_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0597 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_002285CARMICHL_5-011886TIMBERVW_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0774 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_002372COLLINSS1_5-002373ANNASW_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8871 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0549 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.5639 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.2809 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.2736 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_002461ROYSE_N5-002513ALLENSW1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1038 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.6672 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2209 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8507 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_003133RICHLND2_5-003199CALFRESTN_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.5163 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_003134RICHLND1_5-003186CALPFREST_5C2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.3284 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.5163 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1192 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_003374FILESVALY_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4995 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_003386OUTLAW_5-046020LIMEST_POI_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2561 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_003386OUTLAW_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5733 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_003389FORTSMITH_5-152333FILESSLR_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0961 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.6525 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_003490LNGPRAIRIE_8-152736FENCESLR_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5461 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_003702RIESEL_8-153195CORAL_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0565 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_003711BALE_S5-153733TNS_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3605 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.7104 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2799 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5318 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_005502RAYBURN8-005513RAYBURNPLNT8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4305 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_005761PAREDESSW8-160981CAMWIND_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0363 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_005779REDSWTAP8-005784REDGATESW8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8756 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_005779REDSWTAP8-161031REDGATE_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8756 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_005895PEARSALLSUB8-005896MORROWSW8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2519 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_005895PEARSALLSUB8-005897HORIZONSW8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2533 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_005895PEARSALLSUB8-058959PEARSALLSCB8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6298 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_005897HORIZONSW8-162793HRZN_SLR_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2533 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_006015MADDUX4A-183353RATLIFF_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0046 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_006630FTST4A-132482RIGGINS_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0685 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_006903BOZE-151372LILY_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2543 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.2027 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_007077L_AMOSCR5_1Y-183171GALLOWAY_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9485 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_007126L_FERGUS8_1Y-180015FERGGT1_1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.431 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_007126L_FERGUS8_1Y-180016FERGGT2_2_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.431 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_007126L_FERGUS8_1Y-180017FERGST1_1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5157 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_007279L_MULDOO8_1Y-1707737RNCHSLR_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4135 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_007337L_KIMBRO8_1Y-170523E_BLACK_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0409 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_007389L_PINNAC8_1Y-135019TI_SOLAR_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6127 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_007389L_PINNAC8_1Y-135113ARAGORN_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2106 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008140JOSLIN4A-120263TREB_SLR_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0939 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008172VICTORIA4A-110883VIC_SU5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0809 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008172VICTORIA4A-110884VIC_SU6C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2828 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008209SHAKEPOI4A-162543MCLNSLR_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2671 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008318RIOHONDO7A-162745LMJDSW_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5347 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008319RIOHONDO4A-160750LV1_AB_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0936 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008380NEDIN4A-160234NEDIN_1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8239 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008380NEDIN4A-160235NEDIN_2_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8239 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.7208 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.469 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008458B_DAVIS4A-160105B_DAVIS_1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.4922 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008458B_DAVIS4A-160106B_DAVIS_2_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.7112 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008458B_DAVIS4A-160107B_DAVIS_3_9C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4272 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008458B_DAVIS4A-160108B_DAVIS_4_9C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4272 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008579KATOEN7A-008606GODDARD7AC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1084 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008640KELVIN4A-088640CHLPAPOI4AC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1519 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008663ELSUZPOI7A-163415ELSAUZ_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6246 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008963HEC4A-008981HECGT14AC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3129 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008963HEC4A-008983HECST14AC3 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4659 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008980FRONTERA4A-160180FRONT_EC_C1TC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5663 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008980FRONTERA4A-160181FRONT_EC_C2TC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5662 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_008980FRONTERA4A-160182FRONT_EC_STTC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6184 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3205 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_011270DOGHOUSE_5-023876CLEARFRK_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.9913 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_011270DOGHOUSE_5-134805PROSPERO_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6889 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_011270DOGHOUSE_5-135183PRSPERO2_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4586 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_011273NELSON_8-135503RDOSLR_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2216 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_011406CENTBLUF_5-182255HOLSTN_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2051 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_011688THORNTRE_5-143625SAMSON_1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.3263 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_011688THORNTRE_5-143705DELILA_1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.7839 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7562 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3918 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_023910WINDMILL_5-140753HRFDWIND_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0384 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_023920ABERNATH_5-141607AEEC_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.5234 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_023924FARMLAND_5-133641TAHOKAW_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1024 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_038745TNATTWATER1-111971TOPAZ_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.6692 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_040000CEDARP_B345A-110076CBY4_1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.0462 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_040010CEDARP_B138A-049201GENGBY2_02_8CGL | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.5037 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_040715GRNBYU_POI8B-049211GENGBY7_08_8CGL | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.057 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_041000LYDELL_POI_8-110665CHE_2_8C04 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2102 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_042010P_H_R___B138-111131BAC_8C92 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0386 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_042110ANGLTN_POI_8-111535MYR_8C01 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5385 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_042110ANGLTN_POI_8-112597BCH_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9964 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_042215COPPER_X02B8-042540JONCRK__B138C&1-MS | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5309 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_042420BEASLY_POI_8-112433TAV_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2425 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_042570ARCHER_POI_8-112969BTM_8C01 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0847 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_043110SANBER_POI_8-112215DAG_8C01 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0377 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_044000W_A_P__POI5A-049205GENWAP6_06_5CGL | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.9796 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_044000W_A_P__POI5A-049206GENWAP7_07_5CGL | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.472 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_044005W_A_P__POI5B-049207GENWAP8_08_5CGL | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.6288 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_044015W_A_P__POI8B-049212GENWAP3_03_8CGL | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5353 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_044060BLUE___POI_5-112043HOL_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2672 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_044070WHALEY_POI_5-112615ROW_5C01 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4848 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_044200HILLJE__B345-111637DANISH_5C01 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4259 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_044200HILLJE__B345-112147PLN_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.192 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_044650SMTHRS_POI_5-112419RABBS_5C01 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1883 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_044880WATERH_POI_5-112878GSTAR_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.256 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_044890SNUG___POI_8-113435COTBAYOU_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6065 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_045500T_H_W__POI_5-049204GENTHW5X05_5CGL | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.124 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_045515T_H_W__POI_8-049202GENTHW3X03_8CGL | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0542 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_045515T_H_W__POI_8-049203GENTHW4X04_8CGL | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0543 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_046020LIMEST_POI_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3012 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_047170H_O_C__POI_8-111800PRO_8C01 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1747 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_059906LONGDRAW_138-134145JUNO_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6445 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_059906LONGDRAW_138-134342LGDRAW_S8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3057 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_059909NOVA_138-059998NOVA8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.2108 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_059909NOVA_138-143115NOVA1SLR_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.2807 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_059909NOVA_138-144163NOVA2SLR_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1402 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_059911MHOS-183406JADE_HI_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8666 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_060011NEBULA7A-183525ANDMDSLR_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.694 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_060383LINTERNA4A-132331REROCK_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0562 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_060393PIGCREEK4A-134245TAYGETE_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5619 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_060393PIGCREEK4A-134705TYGTEII_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3141 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_060464AZUREPOI7A-060514CLEARCRO7BC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4004 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_060504TESLA7B-142815MISAE_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2442 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_068090SAMSW-068092LIBERTYC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.2039 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_068092LIBERTY-152433MERCURY_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.723 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_076002L_BAKERS5_1Y-133843WAYMARK_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1608 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_076002L_BAKERS5_1Y-135327REDBARN_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4764 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_076005L_SCHNDR5_1Y-132632SANTRITA_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1232 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_076015L_CEDACA5_1Y-134512HILO_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1228 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_076040L_CASTIL8_1Y-132783CASL_GAP_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1721 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_076040L_CASTIL8_1Y-132943SPTX12B_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0852 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_076090L_DIVIDE5_1Y-180759CAPRIDG4_1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1228 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_078255L_PINTCR8_1Y-183623ZIER_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1396 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_080071ZORILLO7A-080076AJO7AC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.3509 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_080071ZORILLO7A-080171SARITA7AC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.9503 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_080072STELPOI7A-080076AJO7AC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1371 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_080072STELPOI7A-161953STELLA_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1367 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_080171SARITA7A-160299BAFFIN_2_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.95 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_080219LOBO7A-163223CORAZON_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6176 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_080259PELICAN4A-160394COTTON_1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1683 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_080259PELICAN4A-160395PAP1_1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0626 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_080260GILA4A-160095NUECES_B_2_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4319 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_080260GILA4A-160096NUECES_B_3_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.43 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_080309LASPULGA4A-160694REDFISH_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1764 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_080503SANTASW4A-085001N_SHARPE4AC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3715 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_080503SANTASW4A-161455CHAWIND_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3714 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_080509LADKPOI7A-161753BBREEZE_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2589 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_085008PATPOI7A-161653PATWIND_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2773 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_088173JCKSLPOI4A-163575JACKALOPE_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1448 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_088573ERAYPOI7A-162151EASTRAY_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1226 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_088574WRAYPOI7A-162695ELTRUENO_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3189 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_088606JRVKPOI7A-162005KNKWA1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1635 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_088640CHLPAPOI4A-162253CHALUPA_138C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1519 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_088656ASTRSPOI4A-163023NEBULA_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0558 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_088670BLACKPOI7A-162915BLACKJAK_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3234 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_131753PC_SOUTH_1_5-131755PC2_SWYD_1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0528 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_143575SAMSON_3_5-143625SAMSON_1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6779 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_143705DELILA_1_5-143757DELILA_2_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0016 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_160298BAFFIN_5-160299BAFFIN_2_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1345 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_160750LV1_AB_8-160751LV1_A_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1567 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_160750LV1_AB_8-160752LV1_B_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1603 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_180754DIVIDE_1_8-180757CAPRIDGE_3_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0683 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5899 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6517 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_888856HOLLY_POI-059900LONG_DRAWC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2216 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_888874VIKING_POI-011886TIMBERVW_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1175 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3293 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L_888880DES_WILL_POI-001916LIGGETTA2_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1624 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L1000027 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1371 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L1000032 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1227 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L10010116 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0952 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L10010434_MODIFIED_BY_MZ | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.275 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L10010717 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3129 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L10011226 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0112 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L10011585 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.9503 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L10011690 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.53 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L10011910-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4934 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L10012087 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2773 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L10012091 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1635 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L10012100 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0809 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L10012105 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2828 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L10012915 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3715 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L11000047 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3189 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L11000090 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6201 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L11000095 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2589 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L11000105 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1541 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L11000171 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1519 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L201000169 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.4531 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | L20255426 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.4531 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | LAKE CREEK - RATTLE SNAKE 345 KV WITH SANDY UNIT (SINGLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.099 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | LCRA TSC_T21451 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0683 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | LCRA TSC_T21457 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1526 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | LCRA TSC_T255_TAE3121_1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1849 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | LEON_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2601 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4167 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1635 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.9679 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8288 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7545 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0757 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | M10000271115801 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.9275 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | M105311105321 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.1104 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | M115851115803 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.3509 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | M128152129153 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5384 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MALDIVES_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2344 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.8855 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB100002711580 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.9275 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB1000710005-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0447 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB1101411110-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8352 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB1158011585 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.3509 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB1291512815a | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5267 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB210140210145-AAAAA | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.3429 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB210140210145-AAAAB | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.5972 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB210140210145-AAABA | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.9347 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB210140210145-AABA | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.0638 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB210140210145-AABB | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.6694 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB210140210145-ABAAA | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.8737 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB210140210145-ABAAB | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.6338 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB210140210145-ABABB | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.1733 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB210140210145-ABBA | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3667 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB210140210145-BAAA-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5263 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB210140210145-BAAA-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9549 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB210140210145-BAAB-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2734 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB210140210145-BAAB-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7095 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB210140210145-BABA | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2086 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB210140210145-BBAB-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3729 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MB2726627277 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3922 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.8025 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.1038 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNIT 4 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.54 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.8598 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | MOSS - HOLT/YUCCA 138 KV/MIDLAND COUNTY NW SW 345 KV (DOUBLE B TO B) SUM 2025- FUTURE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0132 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | N5GSU2_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.8539 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.772 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | NEW-GRAHAM-PARKER 345 KV-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6758 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ODESSA EHV - NORTH MCCAMEY 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.37 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | OLD LAKE SW - HOPEWELL SW 69 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2609 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | OYSTER_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0634 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_BTE_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1092 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_BTE_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1092 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_BTE_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1092 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_BVE_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.4765 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_BVE_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.4744 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_CBE_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0449 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_CBE_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0255 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_CBE_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1311 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_CBE_4_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1062 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_CBT_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.7357 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_CBT_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.771 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_CBY_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1023 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_CBY_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1022 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_CHE_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.879 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_CHE_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.126 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_CHE_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1812 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_CVC_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9739 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_CVC_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9507 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_CVC_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9507 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_CVC_4_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9529 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_DIB_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1456 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_DIB_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1455 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_DIB_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1848 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_DPEC_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.7536 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_DPEC_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.8096 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_DPEC_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.7539 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_DPEC_4_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.8096 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_DPEC_5_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.665 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_FTR_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.584 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_FTR_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.584 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_FTR_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.5845 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_BLY-CBT_C0_111143 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.8287 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_BLY-CBT_C1_111141 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9944 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_BLY-CBT_C2_111142 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0468 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_CBY-CBY_C0_110075 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2386 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_CBY-CBY_C1_110073 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1596 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_CBY-CBY_C2_110074 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1596 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_CTR-DPEC_C0_110755 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7952 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_CTR-DPEC_C1_110751 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1961 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_CTR-DPEC_C2_110752 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.248 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_CTR-DPEC_C3_110753 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1964 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_CTR-DPEC_C4_110754 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2481 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_CTR-DPEC_C6_110761 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1138 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_DPW-CHE_C2_110663 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.212 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_DPW-CHE_C3_110668 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2665 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_JFS-PSG_C0_110623 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2068 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_JFS-PSG_C2_110621 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1754 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_JFS-PSG_C3_110622 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1754 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_RNS-FTR_C0_120094 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.5763 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_RNS-FTR_C1_120091 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2006 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_RNS-FTR_C2_120092 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2006 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_RNS-FTR_C3_120093 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2009 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_SDN-CVC_C0_110824 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0693 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_SDN-CVC_C1_110821 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2029 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_SDN-CVC_C2_110822 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1801 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_SDN-CVC_C3_110823 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1801 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_SMR-BVE_C0_110773 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6507 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_SMR-BVE_C1_110771 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0838 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_GEN_SMR-BVE_C2_110772 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0819 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_PSA_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2317 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_PSA_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.237 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_PSA_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2422 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_PSA_4_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2448 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_PSA_5_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2387 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_PSA_6_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2329 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_PSG_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0892 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_PSG_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0892 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_THW_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1806 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_THW_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1806 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_THW_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1806 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_THW_4_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1806 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_THW_5_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1806 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_THW_6_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1806 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_THW_7_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1806 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-1_THW_8_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1806 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(110666-110667-BC) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2665 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(40015-49200-GL) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.466 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(40070-110975-1) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0709 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(40240-110756-01) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7952 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(40240-110757-02) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1961 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(40240-110758-03) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.248 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(40240-110759-04) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1964 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(40240-110760-05) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2481 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(40240-110762-01) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1138 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(40450-110666-02) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1831 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(40600-120095-1) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.2359 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(40890-113219-01) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.4947 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(41240-110624-02) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1754 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(41240-110625-03) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1754 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(41240-110626-02) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2068 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(41430-110825-03) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9739 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(41430-110826-02) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1801 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(41430-110827-01) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1801 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(42985-110797-60) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.2054 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(43020-113341-1) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3162 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(44015-49215-GL) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.1101 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(44090-111865-1) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0292 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(44160-112495-1) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7036 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(44200-112261-1) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3683 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(44650-110774-1) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0838 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(44650-110775-2) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0819 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(44650-110776-1) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6507 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(46020-49208-GL) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.3144 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_(46020-49209-GL) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.3177 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P1-2_11.1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8892 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>>T0202H | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5306 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>>T0202K-1-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2076 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>>T0202K-2-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2313 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>>T0202K-2-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7042 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>>T0226 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.541 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>>T0404YYY | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7963 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>>T0526 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.733 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>>T0726 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4415 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>>T1839X2_ERC | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1202 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>>T2764Y_ERCa | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0839 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>>T6060B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3725 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>>T7475B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.9049 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>>T9797B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.1504 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.1897 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>T0202F-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3093 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>T0202GX | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1243 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | P7-1_E1>T6060F | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.2398 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | PARIS NW-PARIS-PARIS SW138 KV (SINGLE B TO B) A | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0512 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | PARIS SW-MOSES 345 KV-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.333 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | PARIS SW-PACIFIC SW/VALLEY S SW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2348 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | PARKER-COMANCHE PEAK 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6496 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.5632 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV DCKT & EAGLE MOUNTAIN - WEATHERFORD 138 KV LINE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 111.9367 | 103.9113 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | PINEFOREST_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.9522 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | QUANT_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3186 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | R4U2A5C1_1_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.1183 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | RAMHORN - HICKS DC 345 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0181 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | RAMHORN - WILLOW CREEK DC 345 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.2074 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | RAT_SNAKE-SNDY_CREEK_5 (SINGLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.099 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | ROANOKE - RHOME 138 KV & ROANOKE - GRAPEVINE SW 138 KV (DOUBLE B TO B) F FLOWERMOUND WEST | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.1598 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | RUBICONALPHA_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0532 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6499 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3497 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0059 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | SAM_NAV_P7F1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.446 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | SAN_PAT_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.9183 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | SKYSLY_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6132 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | SOLACE_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0059 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | STECL_10247 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0485 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | STECL_10248 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0485 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | STECL_10262 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.9924 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | STECL_10288 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0363 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | STP - HOUDINI & STP - SHAULA | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0697 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | STPHNVIL-JAYBIRD 138 KV (SINGLE B TO B) B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0457 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | T_000621BOWIE9-000620BOWIE8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0328 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | T_000646LEWISVLSW5_1-000645LEWISVLSW8_1C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9534 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | T_000750STJO9-000746STJO8C2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2879 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | T_000981SPNCRINT69-000982DN_STEAM_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6773 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | T_059908NOVA_345-059998NOVA8CT1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.2108 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | T_180760DIVIDE_SC1-180754DIVIDE_1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0683 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3355 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | TIMBERVIEW-COMANCHE PEAK*CARMICHAEL BEND 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9446 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | TIMBERVIEW-COMANCHE PEAK*DECORDOVA 345 KV (SINGLE B TO B)-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.2464 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0697 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6189 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | TRIFECTA_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.2265 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.0955 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | TRIN-SK*ME (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3463 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | TWIN_OAK_BKR_8995_345_OAK_GROVE_SINGLE_B_T0_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.2387 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | TWIN_OAK_BKR_9000_345_OAK_GROVE_SINGLE_B_T0_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.2383 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | U3CT1_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3674 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | U3GSU1_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.7244 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | U3GSU2_B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5765 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8215 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7012 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.8732 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4459 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2707 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.1992 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | VENUS-FORT SMITH SW 345 KV (SINGLE B TO B) new load | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1556 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | VENUS-JOHNSON 345KV/DECORDOVA-CLEBURNE 138KV (DOUBLE B TO B) new load | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7171 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | VIKING_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.5219 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0672 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.5896 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6312 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | WHITERIVER-COTTONWOOD (DOUBLE B TO B)-3 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8358 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | WILLOW CREEK - CLEAR CROSSING (THOMAS PRICE) & COODY CROSSING - TECUMSEH 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV SUM 2026 - FUTURE (TRIPLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1688 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | WILLOW CREEK - HENDERSON RANCH 345 KV & WILLOW CREEK - JACKSBORO 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.0595 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | WILLOW CREEK - TECUMSEH/THOMAS PRICE 345 KV DCKT WIN 2023 - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1873 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | WILLOW CREEK - THOMAS PRICE\TECUMSEH CREEK 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV WIN 2023 - FUTURE (TRIPLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4151 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.4852 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | WINDMILL - AJSWOPE (SINGLE B TO B) SUM 2028 - FUTURE | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3665 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | WISE COUNTY - ALVORD TAP 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 108.7299 | 101.0904 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | WISE COUNTY (BEC) - ALVORD/BRIDGEPORT(BEC) (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1200.7211 | - | - | 103.7709 | 108.0592 | 132.4195 | 122.6917 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.8241 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C2_345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8259 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-CALFRESTN_5-4 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2911 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-CALFRESTN_5-5 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2891 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-CALFRESTN_5-6 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4412 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-CALPFREST_5-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2217 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-CALPFREST_5-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2216 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-CALPFREST_5-3 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3544 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-ENNSTRAC_8-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9081 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-ENNSTRAC_8-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2392 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-HANDLEYC_8-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.4989 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-HANDLEYC_8-3 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.0772 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-HANDLEYD_8-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.0739 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-LKHB_1T8-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.6367 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-LKHB_2T8-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.9006 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-MARTINLK_5-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.6371 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-MARTINLK_5-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.6451 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-MARTINLK_5-3 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.6531 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-MDLTHELP_5-5 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1016 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-MDLTHELP_5-6 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1152 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-MDLTHELP_N5-3 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0974 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-MDLTHELP_N5-4 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.096 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-MDLTHELP_S5-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.0166 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-MDLTHELP_S5-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.1298 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-MTCK_6T8-6 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3632 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-MTCK_7T8-7 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3273 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-MTCK_8T8-8 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.392 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-MTENTRPR_5G-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2727 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-MTENTRPR_5G-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1418 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-MTENTRPR_5G-3 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.254 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-MTENTRPR_5G-4 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.8391 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-SANDYCRK_5-01 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.099 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-STRYKER_8-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.5301 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-STRYKERND_8-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.3382 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-WHCCS2_4-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.54 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-WHCCS2_5-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.2161 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-WLFHMDPT_5-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.8241 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | XFMR-WLFHOSTR-3 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8259 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_8 ( 1565) -> BRDGPORT_T8 ( 1590) CKT 1 | YELLOW_WOLF_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.3813 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | BEPC_005_1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 121.073 | 112.1796 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | BEPC_006 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 102.0335 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | BEPC_114 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 103.6888 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | BEPC_242 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 103.1166 | 124.0892 | 116.1039 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | BEPC_246 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 102.8357 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | BEPC_2541 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 102.908 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | BEPC_458 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.3288 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000501HILLTOP8-000508RIKERC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 112.0567 | 104.8685 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000508RIKER-000516ZIONHILLC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 112.0544 | 104.8665 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000516ZIONHILL-000543SWIMMERC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 113.3343 | 106.0843 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000541RENO-000595KEETERC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 101.518 | 122.5665 | 114.5135 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000543SWIMMER-000588WILLOWC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 113.8995 | 106.6283 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000579JCKCNTY8-000580WSTBROOKC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 114.2104 | 106.9272 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000579JCKCNTY8-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 102.9663 | 124.075 | 115.9629 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000580WSTBROOK-000588WILLOWC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 114.0073 | 106.7324 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000595KEETER-000596COTTONDALEC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 102.0412 | 123.113 | 115.0406 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000596COTTONDALE-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 102.9678 | 124.0766 | 115.964 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000620BOWIE8-000741DYEMOUNDC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 103.1685 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000684SPRING-000691VALLEYVIEWC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 104.308 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000690MYRA-000691VALLEYVIEWC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 104.9137 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000690MYRA-000695MUENSTERC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 101.972 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000695MUENSTER-000730WOLFRIDGEC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 102.6637 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000741DYEMOUND-000762HARDYSWC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 102.7814 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | L_000746STJO8-000762HARDYSWC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 102.5486 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV DCKT & EAGLE MOUNTAIN - WEATHERFORD 138 KV LINE | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 102.3029 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRDGPORT_T8 ( 1590) -> BENNETT_8 ( 1582) CKT 1 | WISE COUNTY (BEC) - ALVORD/BRIDGEPORT(BEC) (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 121.0216 | 112.1312 | -
1 | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | BRELYN_8 (11332) -> ONC900057_TAP (901396) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 110.3963 | - | -
TONCOR | EAST | EAST | EAST, EAST | BRINKER_A8 (11797) -> SULSP_E_T8 ( 1797) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 110.4227 | 127.5214 | 110.831 | -
TONCOR | EAST | EAST | EAST, EAST | BRINKER_A8 (11797) -> SULSP_E_T8 ( 1797) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 119.7709 | 137.487 | 119.2085 | -
TONCOR | EAST | EAST | EAST, EAST | BRINKER_A8 (11797) -> SULSP_E_T8 ( 1797) CKT 1 | L_001695MOSES_5-001697SULSP_SS1_5C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 101.0497 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 113.3044 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 107.7587 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | - | 104.4974 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | DES_WILL_CON | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 101.3698 | 112.0946 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | - | 103.3936 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | GLASGOW_CON | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | - | 103.4398 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | L_001906VENUS_S5-888880DES_WILL_POIC1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 101.0252 | 111.5937 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | L_001928LIGGETT_3T5-002406NORWD1_5C1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | - | 102.706 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 101.2413 | 111.3945 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 104.1581 | 114.6047 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | - | 104.4974 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | - | 103.3936 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | - | 103.4681 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | - | 102.6018 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | - | 101.8491 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | L_888880DES_WILL_POI-001916LIGGETTA2_5C1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 101.9131 | 112.6742 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 100.0695 | 110.8643 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 100.9379 | 111.6511 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 100.9973 | 111.6058 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 101.8751 | 112.4508 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 101.3848 | 112.1108 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 101.928 | 112.6903 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 109.8509 | 120.9126 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | LIGGETT-NORWOOD 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | - | 101.8467 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 109.7277 | 120.9303 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 110.2378 | 121.4167 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | NORWOOD-LIGGETT 345 & MOUNTAIN CREEK - LIGGETT 138 KV DCKT A BLUBONT | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | - | 102.2186 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 101.7236 | 111.7344 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 105.7968 | 115.9341 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | - | 103.2176 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 112.3011 | 124.8205 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 100.4087 | 111.1052 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 100.8716 | 111.6203 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 100.4285 | 111.1443 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-2 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 101.2974 | 112.0535 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 101.4059 | 112.0018 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 101.8905 | 112.4668 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BRITNRD1_5 (11901) -> WEBB3_5 ( 1904) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 3000.0457 | - | - | - | 102.0866 | - | - | -
TONCOR | NORTH | NORTH | NORTH, NORTH | BRKSTN_T8 ( 1833) -> BOISPUMP_T8 ( 1835) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 958.0667 | - | - | - | - | 110.2635 | 101.6295 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_ATK138 (32862) -> BRYN_LENRDRD (32851) CKT 1 | L_032780BRYN_RELLIS-032852BRYN_STEELE_C1 | 138 | 138 | Branch Amp | 1091.9449 | - | - | 135.2261 | 135.4248 | 202.2325 | 200.6894 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_ATK138 (32862) -> BRYN_LENRDRD (32851) CKT 1 | L_032852BRYN_STEELE_-032857BRYN_SNOO138C1 | 138 | 138 | Branch Amp | 1091.9449 | - | - | 139.6558 | 140.0666 | 210.3373 | 208.4306 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_ATK138 (32862) -> BRYN_LENRDRD (32851) CKT 1 | L_032857BRYN_SNOO138-032860BRYN_KOPPEC1 | 138 | 138 | Branch Amp | 1091.9449 | - | - | - | - | 119.2865 | 118.8054 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_ATK138 (32862) -> BRYN_LENRDRD (32851) CKT 1 | L_032857BRYN_SNOO138-032867BRYN_BRUSCKC1 | 138 | 138 | Branch Amp | 1091.9449 | - | - | - | - | 113.613 | 113.264 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_ATK138 (32862) -> BRYN_LENRDRD (32851) CKT 1 | L_032860BRYN_KOPPE-032895BRYN_WBRN138C1 | 138 | 138 | Branch Amp | 1091.9449 | - | - | - | - | 123.2231 | 122.5689 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_ATK138 (32862) -> BRYN_LENRDRD (32851) CKT 1 | L_032863BRYN_THMP_CK-032867BRYN_BRUSCKC1 | 138 | 138 | Branch Amp | 1091.9449 | - | - | - | - | 116.7786 | 116.4096 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_ATK138 (32862) -> BRYN_LENRDRD (32851) CKT 1 | L_032863BRYN_THMP_CK-032897BRYN_DSBY138C1 | 138 | 138 | Branch Amp | 1091.9449 | - | - | - | - | 119.6586 | 119.2694 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_ATK138 (32862) -> BRYN_LENRDRD (32851) CKT 1 | L_032878BRYN_GRNPRAI-032895BRYN_WBRN138C1 | 138 | 138 | Branch Amp | 1091.9449 | - | - | - | - | 127.6071 | 126.9127 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_BRUSCK (32867) -> BRYN_SNOO138 (32857) CKT 1 | L_032780BRYN_RELLIS-032853BRYN_SMETANAC1 | 138 | 138 | Branch Amp | 1091.9449 | - | - | - | - | 103.8985 | 105.1982 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_BRUSCK (32867) -> BRYN_SNOO138 (32857) CKT 1 | L_032851BRYN_LENRDRD-032853BRYN_SMETANAC1 | 138 | 138 | Branch Amp | 1091.9449 | - | - | - | - | 109.0645 | 106.8206 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_DSBY138 (32897) -> BRYN_THMP_CK (32863) CKT 1 | L_032780BRYN_RELLIS-032853BRYN_SMETANAC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 118.942 | 120.3908 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_DSBY138 (32897) -> BRYN_THMP_CK (32863) CKT 1 | L_032851BRYN_LENRDRD-032853BRYN_SMETANAC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 124.3908 | 121.9985 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_GRNPRAI (32878) -> CSGR (32007) CKT 1 | L_032000CSST-032001CSPTC2 | 138 | 138 | Branch Amp | 882.7601 | - | - | 101.1719 | 112.311 | 129.9384 | 128.6535 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_GRNPRAI (32878) -> CSGR (32007) CKT 1 | L_032001CSPT-032002CSSVC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 105.5668 | 104.5245 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_HOLLEMN (32892) -> DOWLNGRD (32005) CKT 1 | BRYN_1088 DC | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 101.6869 | - | -
TBTU | EAST | EAST | EAST, EAST | BRYN_HOLLEMN (32892) -> DOWLNGRD (32005) CKT 1 | BRYN_1093 DC | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 103.0008 | 101.173 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_HOLLEMN (32892) -> DOWLNGRD (32005) CKT 1 | L_032780BRYN_RELLIS-032852BRYN_STEELE_C1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 126.8235 | 125.5864 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_HOLLEMN (32892) -> DOWLNGRD (32005) CKT 1 | L_032852BRYN_STEELE_-032857BRYN_SNOO138C1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 130.2455 | 128.8751 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_HOLLEMN (32892) -> DOWLNGRD (32005) CKT 1 | L_032854BRYN_TRI_PK-032881BRYN_KURTENC1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 100.3581 | - | -
TBTU | EAST | EAST | EAST, EAST | BRYN_HOLLEMN (32892) -> DOWLNGRD (32005) CKT 1 | L_032857BRYN_SNOO138-032860BRYN_KOPPEC1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 113.16 | 112.219 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_HOLLEMN (32892) -> DOWLNGRD (32005) CKT 1 | L_032859BRYN_JK_CRK-032881BRYN_KURTENC1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 101.6254 | - | -
TBTU | EAST | EAST | EAST, EAST | BRYN_HOLLEMN (32892) -> DOWLNGRD (32005) CKT 1 | L_032860BRYN_KOPPE-032895BRYN_WBRN138C1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 117.7636 | 116.5029 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_HOLLEMN (32892) -> DOWLNGRD (32005) CKT 1 | L_032862BRYN_ATK138-032897BRYN_DSBY138C5 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 102.6608 | 102.0855 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_HOLLEMN (32892) -> DOWLNGRD (32005) CKT 1 | L_032878BRYN_GRNPRAI-032895BRYN_WBRN138C1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 122.6509 | 121.3648 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_KOPPE (32860) -> BRYN_SNOO138 (32857) CKT 1 | L_032780BRYN_RELLIS-032853BRYN_SMETANAC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 114.6537 | 116.1244 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_KOPPE (32860) -> BRYN_SNOO138 (32857) CKT 1 | L_032851BRYN_LENRDRD-032853BRYN_SMETANAC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 119.9124 | 117.2259 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SNOO138 (32857) -> BRYN_STEELE_ (32852) CKT 1 | L_032780BRYN_RELLIS-032853BRYN_SMETANAC1 | 138 | 138 | Branch Amp | 2104.3997 | - | - | - | - | 109.6238 | 111.0451 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SNOO138 (32857) -> BRYN_STEELE_ (32852) CKT 1 | L_032851BRYN_LENRDRD-032853BRYN_SMETANAC1 | 138 | 138 | Branch Amp | 2104.3997 | - | - | - | - | 114.9058 | 112.4355 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SOUTH (32880) -> BRYN_SWTCH (32893) CKT 1 | L_032000CSST-032001CSPTC2 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 115.1228 | 113.888 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_STEELE_ (32852) -> BRYN_RELLIS (32780) CKT 1 | L_032780BRYN_RELLIS-032853BRYN_SMETANAC1 | 138 | 138 | Branch Amp | 2179.7063 | - | - | - | - | 103.6271 | 104.9751 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_STEELE_ (32852) -> BRYN_RELLIS (32780) CKT 1 | L_032851BRYN_LENRDRD-032853BRYN_SMETANAC1 | 138 | 138 | Branch Amp | 2179.7063 | - | - | - | - | 108.6697 | 106.3255 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SWTCH (32893) -> BRYN_HOLLEMN (32892) CKT 1 | 3WT_000975JKCREEK1_032859BRYN_JK_CRK_000978JKCREEK3 C 1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 101.6046 | - | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SWTCH (32893) -> BRYN_HOLLEMN (32892) CKT 1 | BRYN_1087 DC | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 103.9103 | 102.1081 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SWTCH (32893) -> BRYN_HOLLEMN (32892) CKT 1 | BRYN_1088 DC | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 108.056 | 106.217 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SWTCH (32893) -> BRYN_HOLLEMN (32892) CKT 1 | BRYN_1093 DC | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 109.3728 | 107.5239 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SWTCH (32893) -> BRYN_HOLLEMN (32892) CKT 1 | L_032780BRYN_RELLIS-032852BRYN_STEELE_C1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 133.1239 | 131.8606 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SWTCH (32893) -> BRYN_HOLLEMN (32892) CKT 1 | L_032852BRYN_STEELE_-032857BRYN_SNOO138C1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 136.5427 | 135.145 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SWTCH (32893) -> BRYN_HOLLEMN (32892) CKT 1 | L_032854BRYN_TRI_PK-032881BRYN_KURTENC1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 106.6968 | 104.9055 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SWTCH (32893) -> BRYN_HOLLEMN (32892) CKT 1 | L_032854BRYN_TRI_PK-032897BRYN_DSBY138C1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 103.9647 | 102.162 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SWTCH (32893) -> BRYN_HOLLEMN (32892) CKT 1 | L_032857BRYN_SNOO138-032860BRYN_KOPPEC1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 119.4656 | 118.5023 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SWTCH (32893) -> BRYN_HOLLEMN (32892) CKT 1 | L_032859BRYN_JK_CRK-032881BRYN_KURTENC1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 107.966 | 106.1667 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SWTCH (32893) -> BRYN_HOLLEMN (32892) CKT 1 | L_032860BRYN_KOPPE-032895BRYN_WBRN138C1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 124.0745 | 122.7898 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SWTCH (32893) -> BRYN_HOLLEMN (32892) CKT 1 | L_032862BRYN_ATK138-032897BRYN_DSBY138C5 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 108.9878 | 108.3904 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SWTCH (32893) -> BRYN_HOLLEMN (32892) CKT 1 | L_032878BRYN_GRNPRAI-032895BRYN_WBRN138C1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 128.9691 | 127.6585 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_SWTCH (32893) -> BRYN_HOLLEMN (32892) CKT 1 | T_032874BRYN_EAST69-032896BRYN_EAST138C1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | - | 105.3699 | 104.1755 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_TAMU_A (32798) -> BRYN_ATK138 (32862) CKT 6 | L_032852BRYN_STEELE_-032857BRYN_SNOO138C1 | 138 | 138 | Branch Amp | 912.046 | - | - | - | - | 103.0761 | 101.3974 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_THMP_CK (32863) -> BRYN_BRUSCK (32867) CKT 1 | L_032780BRYN_RELLIS-032853BRYN_SMETANAC1 | 138 | 138 | Branch Amp | 1091.9449 | - | - | - | - | 109.5638 | 110.9171 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_THMP_CK (32863) -> BRYN_BRUSCK (32867) CKT 1 | L_032851BRYN_LENRDRD-032853BRYN_SMETANAC1 | 138 | 138 | Branch Amp | 1091.9449 | - | - | - | - | 114.7757 | 112.4992 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_WBRN138 (32895) -> BRYN_KOPPE (32860) CKT 1 | L_032780BRYN_RELLIS-032853BRYN_SMETANAC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 121.3573 | 122.8133 | -
TBTU | EAST | EAST | EAST, EAST | BRYN_WBRN138 (32895) -> BRYN_KOPPE (32860) CKT 1 | L_032851BRYN_LENRDRD-032853BRYN_SMETANAC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 126.6086 | 123.8866 | -
TAEN,TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BTTM_GRSS_POI (888870) -> HOLMAN ( 9073) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | 102.7585 | - | - | -
TAEN,TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BTTM_GRSS_POI (888870) -> HOLMAN ( 9073) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | 100.5984 | - | - | -
TAEN,TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BTTM_GRSS_POI (888870) -> HOLMAN ( 9073) CKT 1 | DVCPA1C21B_1 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | 101.9624 | - | - | -
TAEN,TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BTTM_GRSS_POI (888870) -> HOLMAN ( 9073) CKT 1 | E5DVA1C1_1_B | 345 | 345 | Branch Amp | 2008.1747 | - | - | 106.7454 | 132.4007 | - | 103.246 | -
TAEN,TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BTTM_GRSS_POI (888870) -> HOLMAN ( 9073) CKT 1 | E5DVA1C1_1_B_1 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | 122.2423 | - | - | -
TAEN,TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BTTM_GRSS_POI (888870) -> HOLMAN ( 9073) CKT 1 | E5DVA1C1_1_B_2 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | 115.7796 | - | - | -
TAEN,TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BTTM_GRSS_POI (888870) -> HOLMAN ( 9073) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | 107.3504 | - | - | -
TAEN,TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BTTM_GRSS_POI (888870) -> HOLMAN ( 9073) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | 102.2116 | - | - | -
TAEN,TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BTTM_GRSS_POI (888870) -> HOLMAN ( 9073) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | 108.3759 | - | - | -
TAEN,TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BTTM_GRSS_POI (888870) -> HOLMAN ( 9073) CKT 1 | L_008715RADIANT7A-008728COBRA7AC1 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | 104.3094 | - | - | -
TAEN,TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BTTM_GRSS_POI (888870) -> HOLMAN ( 9073) CKT 1 | L_008728COBRA7A-081003HABER7AC1 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | 106.6805 | - | - | -
TAEN,TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BTTM_GRSS_POI (888870) -> HOLMAN ( 9073) CKT 1 | P7-1_E1>>T1827GX_ERC | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | 112.3859 | - | - | -
TAEN,TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | BTTM_GRSS_POI (888870) -> HOLMAN ( 9073) CKT 1 | P7-1_E1>>T1839X2_ERC | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | 102.0126 | - | - | -
TONCOR | EAST | EAST | EAST, EAST | BULLARD_8 (13253) -> BULLARD_ON_8 ( 3237) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 109.8616 | 118.2642 | 109.2977 | -
TONCOR | EAST | EAST | EAST, EAST | BULLARD_8 (13253) -> BULLARD_ON_8 ( 3237) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 113.5754 | - | 113.8427 | -
TONCOR | EAST | EAST | EAST, EAST | BULLARD_ON_8 ( 3237) -> FLINTSUB_8 ( 3251) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 108.2913 | 116.6193 | 107.6964 | -
TONCOR | EAST | EAST | EAST, EAST | BULLARD_ON_8 ( 3237) -> FLINTSUB_8 ( 3251) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 111.9897 | - | 112.2553 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | BUNTIN2_8 ( 2985) -> SMPST2T_8 ( 2986) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 124.9488 | 163.5877 | 126.1648 | -
TCPSE , RBECR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CACHENA (5068) -> ELMCREEK (5133) CKT 2 | Pre-contingency | 345 | 345 | Amps | 1815.7246 | - | - | - | 110.1546 | 134.3789 | 102.3276 | -
TCPSE , RBECR | SOUTH_CE | COAST | SOUTH_CE, COAST | CACHENA (5068) -> OLD_HCKRY_5 (5323) CKT 2 | Pre-contingency | 345 | 345 | Amps | 1701.928 | - | - | - | - | 102.4593 | - | -
TCPSE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CAGAUTO1 ( 5057) -> CAGNOSTR (500133) CKT 1 | New_L_005444TO005805TO005808 | 13.8 | 1 | Branch MVA | 29 | - | 100.0976 | - | - | - | - | -
TCPSE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CAGAUTO1 ( 5057) -> CAGNOSTR (500133) CKT 1 | R4LCA1C1_B_1 | 13.8 | 1 | Branch MVA | 29 | - | 100.1283 | - | - | - | - | -
TBREC | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CALVERTSW (73) -> CALVERT (77) CKT 1 | Pre-contingency | 69 | 69 | Amps | 117.1435 | - | 102.2399 | - | - | - | - | -
TAEPTN | WEST | FAR_WEST | WEST, FAR_WEST | CAMPELIZ2A ( 6641) -> KINNEBREW_9 (11352) CKT 1 | XFMR-RANGER_5 | 69 | 69 | Branch Amp | 317.961 | - | 100.5411 | - | - | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CANNON_8 ( 3707) -> MILANO ( 64) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 114.8767 | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CANNON_8 ( 3707) -> MILANO ( 64) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 110.0868 | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CANNON_8 ( 3707) -> MILANO ( 64) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 104.8641 | - | - | -
TONCOR | EAST | EAST | EAST, EAST | CANTNSW_8 ( 3174) -> EDGEWOOD_8 ( 3181) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 124.278 | 101.4269 | -
TONCOR | EAST | EAST | EAST, EAST | CANTNSW_8 ( 3174) -> EDGEWOOD_8 ( 3181) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 109.4874 | - | -
TONCOR | EAST | EAST | EAST, EAST | CANTNSW_8 ( 3174) -> EDGEWOOD_8 ( 3181) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 102.1082 | 128.5017 | 104.9556 | -
TONCOR | EAST | EAST | EAST, EAST | CANTNSW_8 ( 3174) -> EDGEWOOD_8 ( 3181) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 119.2417 | 103.6008 | -
TONCOR | EAST | EAST | EAST, EAST | CANTNSW_8 ( 3174) -> EDGEWOOD_8 ( 3181) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 115.4276 | 100.6742 | -
TONCOR | EAST | EAST | EAST, EAST | CANTNSW_8 ( 3174) -> EDGEWOOD_8 ( 3181) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 110.1681 | - | -
TONCOR | EAST | EAST | EAST, EAST | CANTNSW_8 ( 3174) -> EDGEWOOD_8 ( 3181) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 115.0399 | - | -
TONCOR | EAST | EAST | EAST, EAST | CANTNSW_8 ( 3174) -> EDGEWOOD_8 ( 3181) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 114.5022 | - | 114.8838 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CARMICHL_5 ( 2285) -> BENBRK_5 ( 1873) CKT 1 | PARKER-COMANCHE PEAK 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | 100.4111 | - | 101.0955 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CARMICHL_5 ( 2285) -> BENBRK_5 ( 1873) CKT 1 | TIMBERVIEW-COMANCHE PEAK*CARMICHAEL BEND 345 KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.6807 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CARMICHL_5 ( 2285) -> BENBRK_5 ( 1873) CKT 1 | TIMBERVIEW-COMANCHE PEAK*DECORDOVA 345 KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.6835 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CARMICHL_5 ( 2285) -> TIMBERVW_5 (11886) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.0674 | 100.6981 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CARMICHL_8 ( 2888) -> GODLEY_8 ( 2281) CKT 1 | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | 102.6839 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CARMICHL_8 ( 2888) -> GODLEY_8 ( 2281) CKT 1 | L_000442RAILPORT-001908VENUSC1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | 103.6419 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | CARTVLRNCH_8 (10018) -> CARTRVL_8 (23851) CKT 1 | L_001328QUARTZSAND_8-010029LILDEWEY_8C1 | 138 | 138 | Branch Amp | 1146.333 | 102.6536 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | CARTVLRNCH_8 (10018) -> CARTRVL_8 (23851) CKT 1 | L_001333MCDONALD_8-001334GLASSCNTYN_8C1 | 138 | 138 | Branch Amp | 1146.333 | - | - | - | - | 101.6375 | 100.9257 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | CARTVLRNCH_8 (10018) -> CARTRVL_8 (23851) CKT 1 | L_010029LILDEWEY_8-011350WRGRN_P8C1 | 138 | 138 | Branch Amp | 1146.333 | 102.6078 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | CARTVLRNCH_8 (10018) -> CARTRVL_8 (23851) CKT 1 | L_011337POLECAT1_8-011350WRGRN_P8C1 | 138 | 138 | Branch Amp | 1146.333 | 100.4767 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | CARTVLRNCH_8 (10018) -> CARTRVL_8 (23851) CKT 1 | QUARTZ SAND - POLECAT CREEK 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 1146.333 | 100.4704 | - | - | - | - | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | ALLEN SW - MONTICELLO 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 106.9149 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 114.792 | 100.0422 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.9886 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 110.7831 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.1482 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 110.9624 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | ALLEN-MOSES 345-138 AUTO-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 106.768 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | ALLEN-MOSES 345-138 AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 114.4661 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 114.0509 | 129.8825 | 112.9667 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | L_001685FARMVLSW_5-011689CYCLONE_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.7097 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | L_001685FARMVLSW_5-011700SALTILLO_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 106.3323 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 106.9149 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 114.638 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | L_001696MOSES1_T5-888854PINEFOREST_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 106.9149 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | L_011684BRIGHTR_5-011688THORNTRE_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3995 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | L_011684BRIGHTR_5-011689CYCLONE_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.5847 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | L_011688THORNTRE_5-011700SALTILLO_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6512 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 114.638 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | PARIS SW-PACIFIC SW/VALLEY S SW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 112.5208 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | PINEFOREST_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.5764 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 121.6267 | 143.6887 | 122.6474 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 115.1635 | 136.8339 | 116.3508 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | VALLEY S-VALLEY SW 345 KV & VALLEY S-PARIS SW 345 KV | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.0628 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | CARTWHEEL_POI (888847) -> CASHSW_T5 ( 2464) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.9259 | 120.591 | 105.4435 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CASHSW_T5 ( 2464) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.8143 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CASHSW_T5 ( 2464) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN-MOSES 345-138 AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.376 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CASHSW_T5 ( 2464) -> ROYSE_N5 ( 2461) CKT 1 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 106.4728 | 121.3737 | 104.8006 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CASHSW_T5 ( 2464) -> ROYSE_N5 ( 2461) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.7277 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CASHSW_T5 ( 2464) -> ROYSE_N5 ( 2461) CKT 1 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.7277 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CASHSW_T5 ( 2464) -> ROYSE_N5 ( 2461) CKT 1 | PARIS SW-PACIFIC SW/VALLEY S SW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.9005 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CASHSW_T5 ( 2464) -> ROYSE_N5 ( 2461) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 110.7645 | 130.9594 | 111.5883 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CASHSW_T5 ( 2464) -> ROYSE_N5 ( 2461) CKT 1 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.7896 | 124.6366 | 105.6808 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CASHSW_T5 ( 2464) -> ROYSE_N5 ( 2461) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 110.2513 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | CAVAZOS4A (80229) -> MILITARY4A ( 8339) CKT 1 | P7/C5-SHRY-1 | 138 | 138 | Branch Amp | 978.9851 | - | - | - | 124.7626 | 126.1732 | 125.4155 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | CLUTCH_CITY_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3673 | 105.3357 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_042050CLUTE___B138-043240SINTEK_X26B8C26 | 138 | 138 | Branch Amp | 1137.9656 | 110.2747 | - | 100.8416 | 115.7579 | 174.0228 | 182.0027 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_042100HUDSON_POI_8-042940MONSAN_POI_8C04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 102.1986 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_042100HUDSON_POI_8-888849CLUTCH_CITY_POIC04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.82 | 105.4276 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_042150BASF___POI_8-042210BRZPRT_S02_8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 102.9635 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_042150BASF___POI_8-042810HOFMAN_X02B8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 105.4959 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_042210BRZPRT_S02_8-042215COPPER_X02B8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 101.1242 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_042215COPPER_X02B8-042540JONCRK__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 102.1017 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_042570ARCHER_POI_8-044430MANVEL_S26_8C26 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7427 | 104.418 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_042810HOFMAN_X02B8-042880LKJACK_S02_8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 105.6616 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_042880LKJACK_S02_8-043170RETREV__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2793 | 107.9844 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_042940MONSAN_POI_8-043070PETSON_X04B8C04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 103.2007 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_042960MUSTNG_S04_8-043500WEBSTR_B138AC&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 109.5827 | 112.9445 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_043070PETSON_X04B8-044890SNUG___POI_8C04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0781 | 103.6893 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_043240SINTEK_X26B8-043365CAMDEN_X26B8C26 | 138 | 138 | Branch Amp | 1137.9656 | 101.2579 | - | - | 106.4213 | 164.4346 | 172.3351 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_043360VLASCO__B138-043365CAMDEN_X26B8C26 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 148.5884 | 156.3408 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_044410KARSTN_C26_8-048173ALVIN_26TP_8C26 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 101.7139 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_044430MANVEL_S26_8-048173ALVIN_26TP_8C26 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 102.0832 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | L_888849CLUTCH_CITY_POI-042960MUSTNG_S04_8C04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 110.3695 | 113.7102 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | P1-2_ALVIN_CKT05 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 102.0769 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | P7-1_E1>>T0202C | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 105.6159 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | P7-1_E1>>T0202E | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 102.4697 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | P7-1_E1>>T0202H | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 102.0986 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | P7-1_E1>>T0405 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 109.6011 | 113.0553 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | P7-1_E1>>T0463 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 109.6245 | 112.9822 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | P7-1_E1>>T0493 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 109.456 | 112.8064 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | P7-1_E1>>T1827FX | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.7326 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | P7-1_E1>>T1827K | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 103.0262 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | P7-1_E1>>T2626D | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8153 | 104.5677 | -
TCNPE | COAST | COAST | COAST, COAST | CAVERN_X82T8 (43330) -> BIPORT_X82B8 (42190) CKT 82 | P7-1_E1>T0202GX | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 104.5634 | -
RNAVWH | COAST | COAST | COAST, COAST | CBEC_1_8 (110797) -> CBEC_STG1 (110793) CKT G1 | Pre-contingency | 138 | 13.8 | MVA | 84 | 107.0171 | - | - | - | - | 123.7692 | -
RNAVWH | COAST | COAST | COAST, COAST | CBEC_1_8 (110797) -> CBEC_STG2 (110796) CKT G1 | Pre-contingency | 138 | 13.8 | MVA | 90 | 106.9159 | - | - | - | - | 119.6416 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CCRST_1T8 ( 2495) -> CCRST_8 ( 2486) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1648.3767 | - | - | - | - | 100.1929 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CCRST_8 ( 2486) -> BUNTIN2_8 ( 2985) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 126.2169 | 163.7755 | 127.3676 | -
TAEPTN | WEST | WEST | WEST, WEST | CEDH2A ( 6423) -> SILVRTP2 ( 6431) CKT 1 | L_060411BURMA2A-061017GOLOID2AC1 | 69 | 69 | Branch Amp | 476.9415 | - | - | 101.0692 | - | 105.3879 | - | -
TAEPTN | WEST | WEST | WEST, WEST | CEDH2A ( 6423) -> SILVRTP2 ( 6431) CKT 1 | L_061016MAGNOX2A-061017GOLOID2AC1 | 69 | 69 | Branch Amp | 476.9415 | - | - | - | - | 102.9099 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCKPU_8 ( 3263) -> CEDRCREK_8 ( 3262) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 107.4484 | - | 102.4798 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCKPU_8 ( 3263) -> CEDRCREK_8 ( 3262) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 103.4706 | - | 100.918 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCKPU_8 ( 3263) -> CEDRCREK_8 ( 3262) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 102.3209 | - | 103.514 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCKPU_8 ( 3263) -> CEDRCREK_8 ( 3262) CKT 1 | G_151371LILY_S1US1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 101.7815 | - | 102.9011 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCKPU_8 ( 3263) -> CEDRCREK_8 ( 3262) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 102.3207 | - | 103.3886 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCKPU_8 ( 3263) -> CEDRCREK_8 ( 3262) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 102.4763 | - | 103.5342 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCKPU_8 ( 3263) -> CEDRCREK_8 ( 3262) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 101.2533 | - | 102.482 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCKPU_8 ( 3263) -> CEDRCREK_8 ( 3262) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 100.9585 | - | 102.2072 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCKPU_8 ( 3263) -> CEDRCREK_8 ( 3262) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 119.6317 | - | 120.4399 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCKPU_8 ( 3263) -> CEDRCREK_8 ( 3262) CKT 1 | L_006903BOZE-151372LILY_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 102.5969 | - | 103.7374 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCKPU_8 ( 3263) -> CEDRCREK_8 ( 3262) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 100.4063 | - | 101.784 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCKPU_8 ( 3263) -> CEDRCREK_8 ( 3262) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 106.1591 | - | 107.1664 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCKPU_8 ( 3263) -> CEDRCREK_8 ( 3262) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 100.3757 | - | 100.6462 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCKPU_8 ( 3263) -> CEDRCREK_8 ( 3262) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 133.2201 | - | 130.7961 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCREK_8 ( 3262) -> WILL_WHT_8 ( 3287) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 105.9058 | - | 100.9757 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCREK_8 ( 3262) -> WILL_WHT_8 ( 3287) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 101.9332 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCREK_8 ( 3262) -> WILL_WHT_8 ( 3287) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 100.7879 | - | 102.0091 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCREK_8 ( 3262) -> WILL_WHT_8 ( 3287) CKT 1 | G_151371LILY_S1US1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 100.2497 | - | 101.3974 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCREK_8 ( 3262) -> WILL_WHT_8 ( 3287) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 100.7876 | - | 101.8847 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCREK_8 ( 3262) -> WILL_WHT_8 ( 3287) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 100.943 | - | 102.0301 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCREK_8 ( 3262) -> WILL_WHT_8 ( 3287) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | - | 100.9776 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCREK_8 ( 3262) -> WILL_WHT_8 ( 3287) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | - | 100.703 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCREK_8 ( 3262) -> WILL_WHT_8 ( 3287) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 118.0903 | - | 118.9289 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCREK_8 ( 3262) -> WILL_WHT_8 ( 3287) CKT 1 | L_006903BOZE-151372LILY_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 101.0501 | - | 102.2202 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCREK_8 ( 3262) -> WILL_WHT_8 ( 3287) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | - | 100.2802 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCREK_8 ( 3262) -> WILL_WHT_8 ( 3287) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 104.6233 | - | 105.66 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCREK_8 ( 3262) -> WILL_WHT_8 ( 3287) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 131.6686 | - | 129.2784 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCREK_8 (3262) -> CEDRCKPU_8 (3263) CKT 1 | Pre-contingency | 138 | 138 | Amps | 1008.271 | - | - | - | - | 101.9906 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CEDRCREK_8 (3262) -> WILL_WHT_8 (3287) CKT 1 | Pre-contingency | 138 | 138 | Amps | 1008.271 | - | - | - | - | 100.4859 | - | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CENTRVIL ( 810) -> MILLER ( 824) CKT 1 | L_000830SHILOH-000834MCCREE8C1 | 138 | 138 | Branch Amp | 999.9037 | - | - | 100.2545 | - | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | CHALYBE4A ( 8735) -> POMPANO4A ( 8535) CKT 1 | L_008535POMPANO4A-079601STILLMANC1 | 138 | 138 | Branch Amp | 1163.0677 | - | - | 158.4341 | - | - | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CHATFIELD ( 200) -> MONTFTSS__8 ( 3454) CKT 1 | L_003723OLYMPUS_SW-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 1004.0873 | - | - | - | 106.7307 | 127.1145 | 109.0166 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CHILSW_S8 ( 2421) -> FSHCRK2_8 (12491) CKT 1 | L_001920SHRY_B8-002258PARKROW2_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 136.3757 | 136.5171 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CHILSW_S8 ( 2421) -> FSHCRK2_8 (12491) CKT 1 | L_002258PARKROW2_8-002259LTV1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 128.141 | 128.3157 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CHILSW_S8 ( 2421) -> FSHCRK2_8 (12491) CKT 1 | L_002259LTV1_8-002262GRANDPR1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 121.2884 | 121.4858 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CHILSW_S8 ( 2421) -> FSHCRK2_8 (12491) CKT 1 | L_002262GRANDPR1_8-012491FSHCRK2_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.8635 | 104.9887 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CHILSW1_5 ( 2420) -> LOOP9_5 ( 2847) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.7865 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CHILSW1_5 ( 2420) -> LOOP9_5 ( 2847) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 111.151 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CHILSW1_5 ( 2420) -> MRRFLD_RD1_5 (15204) CKT 1 | CEDAR HILL - DESOTO/LOOP NINE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 100.5406 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CHILSW1_5 ( 2420) -> MRRFLD_RD1_5 (15204) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 107.0049 | 102.0318 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CHILTPL4_8 ( 3058) -> DESHPR1_8 ( 3059) CKT 1 | L_002429WATMLL_8-003065REINDEER_8C1 | 138 | 138 | Branch Amp | 1648.3767 | - | - | - | - | 112.829 | 108.3764 | -
TONCOR | WEST | WEST | WEST, WEST | CHINAGRV_8 ( 1318) -> CHINAGRVX1_8 (19521) CKT 2 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 899.4949 | - | 104.8677 | - | - | - | - | -
TONCOR | WEST | WEST | WEST, WEST | CHINAGRVX1_8 (19521) -> CP SOUTH (900126) CKT 1 | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 100.1244 | - | -
TONCOR | WEST | WEST | WEST, WEST | CHINAGRVX1_8 (19521) -> CP SOUTH (900126) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 748.8818 | - | 125.9603 | - | - | - | - | -
TONCOR | WEST | WEST | WEST, WEST | CHINAGRVX2_8 (19520) -> BARBER_LK1_8 ( 1189) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 748.8818 | - | 110.0885 | - | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | CHLD4A ( 6030) -> CHLD2A ( 6028) CKT 1 | L_006048PAUL2A-006051QUAN2AC1 | 69 | 138 | Branch MVA | 50 | 120.0312 | - | 119.9011 | 119.4677 | 119.1619 | 119.0538 | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | CHLD4A ( 6030) -> CHLD2A ( 6028) CKT 1 | MB2002820034 | 69 | 138 | Branch MVA | 50 | 120.0298 | - | 119.9553 | 119.4664 | 119.1636 | 119.0531 | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 103.3611 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | BAS_RANCH_CON | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 103.2898 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 101.3683 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.7211 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | DVCPA1C21B_1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.8403 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | DVCPA1C21B_2 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 101.0612 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | E_B_DAVIS_CC1_TRAIN | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 102.1115 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | E_INGLCOSW_CC1_TRAIN | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.6985 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | E_NEDIN_CC1_TRAIN | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 101.5452 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | E_NUECES_B_CC1_TRAIN | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 102.9025 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | E_VICTORIA_CC1_TRAIN | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 107.3355 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | G_150111CPSES_UNIT1UU1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.457 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | G_150112CPSES_UNIT2UU2 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.4633 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | G_170126CALAVER_JKS2UL2 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 102.0953 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | G_888839BAS_RANCH_POIUC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 103.2838 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | G_RIO_TRAIN | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.5307 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | J5LCA1C1_B | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.5293 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.2093 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 106.2935 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 110.876 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 103.2043 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 104.5906 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 101.339 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_005380SHAULA-005915SO_TEX__345AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 101.365 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_005502RAYBURN8-005506FURHMANSW8C1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 102.346 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_005502RAYBURN8-005680LOOP463SUB8C1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 101.1433 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_005680LOOP463SUB8-008172VICTORIA4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.5074 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 107.9202 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 102.7367 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_008117GANADO4A-008118EDNA4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 101.9024 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_008117GANADO4A-008192PULSAR4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 102.0122 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_008118EDNA4A-008172VICTORIA4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 101.4698 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_008125LOLITA4A-008172VICTORIA4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 124.5205 | 102.6639 | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_008144SEADRFTC4A-008189TUNGSTEN4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 100.7841 | 125.9948 | 103.8297 | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_008144SEADRFTC4A-080065MELNCRK4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 100.7646 | 125.9741 | 103.8106 | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_008146BIGTRE4A-008911BLKBYU4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 105.4474 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_008154VISTRON4B-008189TUNGSTEN4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 105.1345 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_008155SANDCRAB4A-008723CANGREJO4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 101.8489 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_008172VICTORIA4A-110883VIC_SU5C1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.1482 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_008172VICTORIA4A-110884VIC_SU6C1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.9952 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_008189TUNGSTEN4A-008723CANGREJO4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 105.157 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_008189TUNGSTEN4A-008723CANGREJO4AC2 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 105.1933 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_008437RINCON4B-080065MELNCRK4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 112.1235 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 103.8026 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_080071ZORILLO7A-080076AJO7AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.1242 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_110471FORFPC_1_8-110473FORFPC_2_8C1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 104.334 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.5015 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L10005-2B | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.9286 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L10010056 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 101.2577 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L10012100 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.1482 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L10012105 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.9952 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L10012964 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 103.4012 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | L10012977 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 102.6571 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | M10000271115801 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 101.5202 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | M100052100072 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 104.6411 | 134.6736 | 108.6015 | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | M115851115803 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.1242 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | MB100002711580 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 101.5202 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | MB1000510007-2 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 103.395 | - | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | MB1000710005-2 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 133.8389 | 107.3733 | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | MB1158011585 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.1242 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | MB1291012930 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 125.9689 | 103.8137 | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | MB1293012910 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 100.7617 | - | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | N5GSU2_B | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 102.0953 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | P7-1_E1>>T1839X1_ERC | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.9808 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | P7-1_E1>>T1839X2_ERC | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.7643 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | P7-1_E1>>T2764Y_ERCa | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 102.0473 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | P7-1_E1>>T3944Z_ERC | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 107.4847 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | STP - HOUDINI & STP - SHAULA | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 101.9669 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 101.9587 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CHOCBAYU4A (80064) -> V_DUPSW4A ( 8143) CKT 1 | WAP - HOUDINI & STP - SHAULA | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 100.8512 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CISTERN ( 9043) -> LYTTON5 ( 9074) CKT 1 | AEN_FPP-HO¦LY | 345 | 345 | Branch Amp | 1924.5007 | - | - | - | - | 127.1649 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CISTERN ( 9043) -> LYTTON5 ( 9074) CKT 1 | AEN_LP-AU¦DL_2013 | 345 | 345 | Branch Amp | 1924.5007 | - | - | - | 104.0685 | 128.7131 | 103.0993 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CISTERN ( 9043) -> LYTTON5 ( 9074) CKT 1 | AEN_P7 FPP-LP.DC_1 | 345 | 345 | Branch Amp | 1924.5007 | - | - | - | - | 122.1169 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CISTERN ( 9043) -> LYTTON5 ( 9074) CKT 1 | AEN_P7 FPP-LP.DC_2 | 345 | 345 | Branch Amp | 1924.5007 | - | - | - | - | 116.6737 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CISTERN ( 9043) -> LYTTON5 ( 9074) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1924.5007 | - | - | - | - | 105.2422 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CISTERN ( 9043) -> LYTTON5 ( 9074) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 345 | 345 | Branch Amp | 1924.5007 | - | - | - | - | 106.9042 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CISTERN ( 9043) -> LYTTON5 ( 9074) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 345 | 345 | Branch Amp | 1924.5007 | - | - | - | - | 101.0507 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CISTERN ( 9043) -> LYTTON5 ( 9074) CKT 1 | L_007055L_FPPYD25_1Y-009073HOLMANC1 | 345 | 345 | Branch Amp | 1924.5007 | - | - | - | - | 123.972 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CISTERN ( 9043) -> LYTTON5 ( 9074) CKT 1 | L_007055L_FPPYD25_1Y-009074LYTTON5C1 | 345 | 345 | Branch Amp | 1924.5007 | - | - | - | - | 109.3464 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | CISTERN (9043) -> LYTTON5 (9074) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1732.0507 | - | - | - | - | 100.2383 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_8 ( 2290) -> CLEBRNSW_8 ( 2279) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.0277 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_8 ( 2290) -> CLEBRNSW_8 ( 2279) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0933 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 112.3099 | 101.9418 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | 3WT_003522HILLBORO1_8_003523HILLBORO1_9_003519HILLBORO1_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 100.5215 | 114.4061 | 103.9252 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.514 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.506 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | BARDWELL LAKE-HILLSBORO_9 (SINGLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.2821 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | BARDWELL LAKE-ITALY-WAX_9 (SINGLE B TO B ) B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.2844 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | BARDWELL-HILLSBORO CKT2 69 KV (SINGLE B TO B ) A | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.2795 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | BAS_RANCH_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5011 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.394 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | BEPC_227-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.8568 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | BEPC_227-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.8568 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | BEPC_282_1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0735 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | BEPC_459 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0211 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0663 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | BIGBRN__5-JEWETT_S5 & BIGBRN__5-JEWETT_N5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2261 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.8061 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | BLUBIRD_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.1337 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | CARMICHAEL BEND-TIMBERVIEW 345 KV*DECORDOVA-CLEBURNE 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 110.0784 | 100.4337 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | CLEBURNE-DECORDOVA 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 109.6179 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | CLEBURNE-DECORDOVA/BURLESON 138 KV (DOUBLE B TO B) B WILSHIRE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0159 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | COMANCHE PEAK-STEPHENVILLE*STEPHENVILLE-WHITNEY 138 KV (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7097 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | DRY_CREEK_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.127 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | E_FRNYPP_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5456 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | E_FRNYPP_CC2_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.6137 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | E_JACKCNTY_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2612 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | E_JCKCNTY2_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3866 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | E_PANDA_S_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4999 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | E_WCPP_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3774 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | E_WHCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.1004 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | E_WHCCS2_CC2_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.6559 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | EL M MOTT - MCLANE/PEPPERVINE_8 (DOUBLE B TO B) D | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1005 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.587 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.9301 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | G_000575JCKCNTY5UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5322 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | G_000579JCKCNTY8UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4662 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | G_150023MCSES_UNIT8UN8 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9289 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | G_150051HLSES_UNIT3UN3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5243 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | G_150052HLSES_UNIT4UN4 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9119 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | G_150053HLSES_UNIT5UN5 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0963 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | G_150092LH2SES_UNIT2UN2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0177 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | G_150111CPSES_UNIT1UU1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.7684 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | G_150112CPSES_UNIT2UU2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.811 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | G_888839BAS_RANCH_POIUC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5085 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | G_888879BLUBIRD_POIUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.5799 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | GLASGOW_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0477 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | HIGHNOON_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.654 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | HILLS-ALVARADO_9 (SINGLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.8079 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000137MOODY-000138JUDITHC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2352 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000137MOODY-000141MOFFATC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1375 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000138JUDITH-000161MCGREGORC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2349 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000161MCGREGOR-000165WINDSORSWC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3189 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000165WINDSORSW-000173CRAWFORDC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6995 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000173CRAWFORD-000177BOSQUEC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8584 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.2055 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.2565 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000213HANEY-888876P_BTTLECRK_POIC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0239 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000221TRUMBULL8-002229PEBBLCRK_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2382 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000232LAMPOSTSW-000241WHITNEY8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8651 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000232LAMPOSTSW-000445YATESC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5211 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000246BOSQUESW5-003406ELM_MOTT__5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.0621 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000432CONLEY-000439HIGHPOINTC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0085 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000436GRANDVIEW-000443SANDFLATSWC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.6761 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000443SANDFLATSW-000444COVINGTONC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.9509 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_000444COVINGTON-888859HIGHNOON_POIC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.2703 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_001639SELDEN_8-001643ANTLERHLW_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.533 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_001639SELDEN_8-001645JOHNSNVL_P8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9644 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_001645JOHNSNVL_P8-001646WALNUTSP_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1565 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_001646WALNUTSP_8-001648POWELLDM_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4615 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_001648POWELLDM_8-003546WHITNEY__8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4739 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.9815 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4578 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_001883EVRMAN_A8-001933KENNEDALE_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8214 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_001895MITCHBND2_5-002285CARMICHL_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.2035 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.438 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_001906VENUS_S5-015201FORBESR2_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.3794 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5559 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_001907VENUS_N5-015200FORBESR1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.221 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_001907VENUS_N5-068091NAVARROC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4761 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_001969MARRS_8-002198GARDNACR_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.1652 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002198GARDNACR_8-002209BURLESON_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.6652 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0663 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.587 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002279CLEBRNSW_8-002280CLEBRN_N_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 109.8062 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002280CLEBRN_N_8-002283AIRLIQD_P8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.7816 | 113.7826 | 103.4133 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002281GODLEY_8-002283AIRLIQD_P8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 103.2791 | 114.6182 | 104.8968 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002281GODLEY_8-002888CARMICHL_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 103.323 | 114.6632 | 104.9407 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002295BARDWELL_9-002336FORESTON_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3131 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002298ALVARADO1_9-003537GRANDVEW1_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3093 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7668 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.6473 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002336FORESTON_9-002337ITALY_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7732 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002337ITALY_9-002338MILFRDEXN_T9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.2847 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002338MILFRDEXN_T9-003523HILLBORO1_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.287 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1312 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1312 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4607 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.9563 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5888 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5626 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5947 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.6278 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.0024 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_003374FILESVALY_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.4329 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2976 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_003381BIGBRNW_5-003391JEWETT_N5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2018 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_003386OUTLAW_5-046020LIMEST_POI_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7372 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_003386OUTLAW_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7014 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_003388FOURBTHRS_5-003405THOUSE__5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.0503 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_003388FOURBTHRS_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.1939 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_003405THOUSE__5-003406ELM_MOTT__5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0989 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_003409LAKE_CRK1_5-013405THOUSE_A_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0198 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.8507 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_003523HILLBORO1_9-003532ITASCA_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.9651 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_003532ITASCA_9-003533FILE_SIN1_T9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.367 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_003533FILE_SIN1_T9-003537GRANDVEW1_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.7745 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_013401TIGERCK_5-013405THOUSE_A_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0199 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_013401TIGERCK_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4039 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.7716 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.3158 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_046020LIMEST_POI_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9124 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_888859HIGHNOON_POI-000445YATESC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4262 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2797 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | LATIMER_REATA_P7F1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2044 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0562 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 109.8114 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.3894 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.1314 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6043 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5259 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.7385 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | NAV-CORS_W-MONTFORT_8 (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8207 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.6372 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.1108 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | OYSTER_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4557 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.8122 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 103.9669 | 121.849 | 101.9607 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 103.2822 | 118.9092 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 106.5931 | - | 109.4437 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | STPHNVIL-WALNUTSP - WHITNEY 138 KV (SINGLE B TO B)_C | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0735 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | T_002298ALVARADO1_9-002297ALVARADO1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.308 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6719 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | TEMPLE PECAN CREEK/BELFALLS - TRADINGHOUSE/STEAKLEYDAM_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1595 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | THOUSE-LCRK*PCNCRK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.477 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.6262 | 115.0837 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.6896 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2565 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | TRIN-MANKIN*EUSTACE SOUTHEAST(DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2239 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | TRIN-NIP*MA (DOUBLE B TO B)B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0908 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8142 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0761 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 107.7946 | - | 110.9283 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.8927 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.215 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.9406 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | VENUS-FORT SMITH SW 345 KV (SINGLE B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.012 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | VENUS-JOHNSON 345KV/DECORDOVA-CLEBURNE 138KV (DOUBLE B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 103.28 | 113.5675 | 103.7093 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | VENUS-SAM SW 345 KV (SINGLE B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.9671 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | WAXAHACHI-WAXAHACHI OFC 69KV/ENNIS-STERRETT 138KV (DOUBLE B TO B) A REAGOR | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4816 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.378 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5082 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | WSHACK_LATIMER_P7 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5762 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | XFMR-HANDLEYC_8-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5243 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | XFMR-HANDLEYC_8-3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0963 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | XFMR-HANDLEYD_8-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9119 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | XFMR-LKHB_2T8-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0177 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | XFMR-MTCK_8T8-8 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9289 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | XFMR-WHCCS2_5-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4165 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 ( 2291) -> CLEBRN_8 ( 2290) CKT 1 | XFMR-WLFHMDPT_5-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5063 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRN_W_8 (2291) -> TNHILL_CO_8 (37810) CKT 1 | Pre-contingency | 138 | 138 | Amps | 861.8416 | - | - | - | 100.0137 | 112.5377 | 103.5498 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> JOSHUA_8 ( 2210) CKT 1 | CLEBURNE-KEMP RANCH 138 KV WITH RAILPORT (SINGLE B TO B) A | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5495 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> JOSHUA_8 ( 2210) CKT 1 | KEMP RANCH - CLEBURNE 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5495 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> JOSHUA_8 ( 2210) CKT 1 | KEMP RANCH-ALVARADO-CLEBURNE 138 KV (SINGLE B TO B) A ALVARDO 138/69 TRANSFORMER | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5495 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> JOSHUA_8 ( 2210) CKT 1 | L_002279CLEBRNSW_8-002294KEENE_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8719 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> JOSHUA_8 ( 2210) CKT 1 | Venus Switch- Cleburne 138 kV Line (SINGLE B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5495 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> KEENE_8 ( 2294) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | 122.9808 | 119.7549 | 158.6793 | 193.0965 | 203.9491 | 175.9663 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> KEENE_8 ( 2294) CKT 1 | 3WT_003522HILLBORO1_8_003523HILLBORO1_9_003519HILLBORO1_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 105.3477 | 109.3372 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> KEENE_8 ( 2294) CKT 1 | BEPC_306 | 138 | 138 | Branch Amp | 861.8416 | 165.9793 | 187.307 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> KEENE_8 ( 2294) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3435 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> KEENE_8 ( 2294) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1278 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> KEENE_8 ( 2294) CKT 1 | CLEBURNE-BURLESON 138 KV (SINGLE B TO B) B WILSHIRE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 109.104 | 113.9634 | 102.0995 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> KEENE_8 ( 2294) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1312 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> KEENE_8 ( 2294) CKT 1 | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | 138 | Branch Amp | 861.8416 | 140.5046 | 179.7765 | 214.7527 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> KEENE_8 ( 2294) CKT 1 | L_000442RAILPORT-001908VENUSC1 | 138 | 138 | Branch Amp | 861.8416 | 142.6143 | 180.0201 | 218.8126 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> KEENE_8 ( 2294) CKT 1 | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | 138 | Branch Amp | 861.8416 | 165.7864 | 187.3991 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> KEENE_8 ( 2294) CKT 1 | L_002203MNTVALLY_P8-002210JOSHUA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 107.5542 | 112.4456 | 100.5591 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> KEENE_8 ( 2294) CKT 1 | L_002210JOSHUA_8-002279CLEBRNSW_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 109.1896 | 114.0708 | 102.1618 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> KEENE_8 ( 2294) CKT 1 | L_003523HILLBORO1_9-003532ITASCA_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.1104 | 104.976 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> KEENE_8 ( 2294) CKT 1 | L_003532ITASCA_9-003533FILE_SIN1_T9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.7986 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> KEENE_8 ( 2294) CKT 1 | L_003533FILE_SIN1_T9-003537GRANDVEW1_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7802 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CLEBRNSW_8 ( 2279) -> KEENE_8 ( 2294) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3979 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CLMVLTP2A ( 8556) -> EL_CAMPO2A ( 8100) CKT 1 | L_008102EL_CAMPO4A-008679ARROZ4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 103.1952 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | CLMVLTP2A ( 8556) -> EL_CAMPO2A ( 8100) CKT 1 | L10006-1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 102.1538 | - | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> CAVERN_X82T8 (43330) CKT 82 | L_042050CLUTE___B138-043240SINTEK_X26B8C26 | 138 | 138 | Branch Amp | 1213.2722 | 103.498 | - | - | 108.6819 | 163.3546 | 170.8404 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> CAVERN_X82T8 (43330) CKT 82 | L_042880LKJACK_S02_8-043170RETREV__B138C&1-MS | 138 | 138 | Branch Amp | 1213.2722 | - | - | - | - | - | 101.4117 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> CAVERN_X82T8 (43330) CKT 82 | L_042960MUSTNG_S04_8-043500WEBSTR_B138AC&1-MS | 138 | 138 | Branch Amp | 1213.2722 | - | - | - | - | 102.91 | 106.0643 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> CAVERN_X82T8 (43330) CKT 82 | L_043240SINTEK_X26B8-043365CAMDEN_X26B8C26 | 138 | 138 | Branch Amp | 1213.2722 | - | - | - | - | 154.3607 | 161.7723 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> CAVERN_X82T8 (43330) CKT 82 | L_043360VLASCO__B138-043365CAMDEN_X26B8C26 | 138 | 138 | Branch Amp | 1213.2722 | - | - | - | - | 139.4965 | 146.7693 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> CAVERN_X82T8 (43330) CKT 82 | L_888849CLUTCH_CITY_POI-042960MUSTNG_S04_8C04 | 138 | 138 | Branch Amp | 1213.2722 | - | - | - | - | 103.648 | 106.7825 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> CAVERN_X82T8 (43330) CKT 82 | P7-1_E1>>T0405 | 138 | 138 | Branch Amp | 1213.2722 | - | - | - | - | 102.9273 | 106.1683 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> CAVERN_X82T8 (43330) CKT 82 | P7-1_E1>>T0463 | 138 | 138 | Branch Amp | 1213.2722 | - | - | - | - | 102.9493 | 106.0997 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> CAVERN_X82T8 (43330) CKT 82 | P7-1_E1>>T0493 | 138 | 138 | Branch Amp | 1213.2722 | - | - | - | - | 102.7912 | 105.9348 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> CAVERN_X82T8 (43330) CKT 82 | Pre-contingency | 138 | 138 | Amps | 949.6992 | - | - | - | - | 102.4589 | 107.0876 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> RIWOOD_X82B8 (43150) CKT 82 | Pre-contingency | 138 | 138 | Amps | 949.6992 | - | - | - | - | 135.0839 | 141.3654 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> SINTEK_X26B8 (43240) CKT 26 | CLUTCH_CITY_CON | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 100.557 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> SINTEK_X26B8 (43240) CKT 26 | L_042050CLUTE___B138-042190BIPORT_X82B8C&1-MS | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 116.5686 | 122.1261 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> SINTEK_X26B8 (43240) CKT 26 | L_042100HUDSON_POI_8-888849CLUTCH_CITY_POIC04 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 100.6588 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> SINTEK_X26B8 (43240) CKT 26 | L_042150BASF___POI_8-042810HOFMAN_X02B8C02 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 100.905 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> SINTEK_X26B8 (43240) CKT 26 | L_042190BIPORT_X82B8-043335OYSCRK_POI_8C&1-MS | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 109.5018 | 115.0003 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> SINTEK_X26B8 (43240) CKT 26 | L_042810HOFMAN_X02B8-042880LKJACK_S02_8C02 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 101.0932 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> SINTEK_X26B8 (43240) CKT 26 | L_042880LKJACK_S02_8-043170RETREV__B138C&1-MS | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 103.7489 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> SINTEK_X26B8 (43240) CKT 26 | L_042960MUSTNG_S04_8-043500WEBSTR_B138AC&1-MS | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 106.0338 | 109.4011 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> SINTEK_X26B8 (43240) CKT 26 | L_043335OYSCRK_POI_8-043345GLOBAL_X82B8C&1-MS | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 103.6337 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> SINTEK_X26B8 (43240) CKT 26 | L_888849CLUTCH_CITY_POI-042960MUSTNG_S04_8C04 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 106.9316 | 110.2965 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> SINTEK_X26B8 (43240) CKT 26 | P7-1_E1>>T0202C | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 101.0424 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> SINTEK_X26B8 (43240) CKT 26 | P7-1_E1>>T0405 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 106.0543 | 109.5309 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> SINTEK_X26B8 (43240) CKT 26 | P7-1_E1>>T0463 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 106.0812 | 109.4453 | -
TCNPE | COAST | COAST | COAST, COAST | CLUTE___B138 (42050) -> SINTEK_X26B8 (43240) CKT 26 | P7-1_E1>>T0493 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 105.8887 | 109.2393 | -
TSTEC,TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | CNTRLAVESUB8 ( 5766) -> COFFPORT4A ( 8914) CKT 1 | P7/C5-SHRY-1 | 138 | 138 | Branch Amp | 991.5362 | - | - | - | 103.0732 | 103.1778 | 102.6274 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CNVLSW_E8 ( 2450) -> CNVLSW_R_E8 (12450) CKT 3 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 105.1924 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CNVLSW_E8 ( 2450) -> CNVLSW_R_E8 (12450) CKT 3 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 104.5212 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CNVLSW_R_E8 (12450) -> GARLDPL1_8 ( 2919) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1986.0011 | - | - | - | - | - | 105.9236 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CNVLSW_R_E8 (12450) -> GARLDPL1_8 ( 2919) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1986.0011 | - | - | - | 105.2478 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CNVLSW_R_W8 (12439) -> GARLDPL2_8 ( 2920) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1986.0011 | - | - | - | - | - | 109.3776 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CNVLSW_R_W8 (12439) -> GARLDPL2_8 ( 2920) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1986.0011 | - | - | - | 108.6913 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CNVLSW_W8 ( 2439) -> CNVLSW_R_W8 (12439) CKT 2 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 108.6224 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CNVLSW_W8 ( 2439) -> CNVLSW_R_W8 (12439) CKT 2 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 107.9409 | - | - | -
TAEPTC | COAST | SOUTHERN | COAST, SOUTHERN | COBRA7A (8728) -> HABER7A (81003) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1780.5816 | - | - | - | 122.0695 | 162.3794 | 104.6126 | -
TAEPTC,TSTEC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | COFFPORT4A ( 8914) -> HIWAY511SUB8 ( 5767) CKT 1 | P7/C5-SHRY-1 | 138 | 138 | Branch Amp | 991.5362 | - | - | - | 100.2494 | 100.1522 | - | -
TAEPTC , TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | COLETO4A (8162) -> VICTORIA4A (8172) CKT 1 | Pre-contingency | 138 | 138 | Amps | 1338.7831 | - | - | - | - | 113.1702 | - | -
TAEPTC , TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | COLETO4A (8162) -> VICTORIA4A (8172) CKT 2 | Pre-contingency | 138 | 138 | Amps | 1338.7831 | - | - | - | - | 119.1102 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COMM_SW_8 ( 1816) -> COMM_S1_8 ( 1819) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.3341 | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | G_136101BLUESKY_S1US1 | 69 | 69 | Branch Amp | 317.961 | 100.6632 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | L_006036YUCCA4A-006525ESMERALD4AC1 | 69 | 69 | Branch Amp | 317.961 | 137.3733 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | L_006036YUCCA4A-060360CASSAVA4AC1 | 69 | 69 | Branch Amp | 317.961 | 120.9234 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | L_006517RUSSEKST4A-006535BIGLAKE4AC1 | 69 | 69 | Branch Amp | 317.961 | 101.7317 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | L_006517RUSSEKST4A-006559JERRY4AC1 | 69 | 69 | Branch Amp | 317.961 | 103.707 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | L_006525ESMERALD4A-006562FDRAN4AC1 | 69 | 69 | Branch Amp | 317.961 | 108.5846 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | L_006530BARNHRT2A-006534BIGLAKE2BC1 | 69 | 69 | Branch Amp | 317.961 | 100.394 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | L_006559JERRY4A-060374PUMPJACK4AC1 | 69 | 69 | Branch Amp | 317.961 | 107.2098 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | L_006562FDRAN4A-060412CARVER4AC1 | 69 | 69 | Branch Amp | 317.961 | 100.8708 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | L_006648HARGROVE4A-060374PUMPJACK4AC1 | 69 | 69 | Branch Amp | 317.961 | 109.3532 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | L_006648HARGROVE4A-076011L_TWINBU8_1YC1 | 69 | 69 | Branch Amp | 317.961 | 110.7618 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | L_060361SANTARIT4A-060414OWLS4AC1 | 69 | 69 | Branch Amp | 317.961 | 103.8175 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 69 | 69 | Branch Amp | 317.961 | 104.6711 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 69 | 69 | Branch Amp | 317.961 | 105.6525 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | L2020925 | 69 | 69 | Branch Amp | 317.961 | 102.167 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | L2020944-A | 69 | 69 | Branch Amp | 317.961 | 104.6131 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | LCRA TSC_BAKERS_CEDACA_DC | 69 | 69 | Branch Amp | 317.961 | - | 102.9567 | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-1 | 69 | 69 | Branch Amp | 317.961 | 101.8617 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-2 | 69 | 69 | Branch Amp | 317.961 | 100.8375 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-1 | 69 | 69 | Branch Amp | 317.961 | 101.8617 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-2 | 69 | 69 | Branch Amp | 317.961 | 100.8374 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | LCRA TSC_NOELK_SNGTR_NOELK_SNGTR2 | 69 | 69 | Branch Amp | 317.961 | 100.4269 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | LCRA TSC_T429_T9426 | 69 | 69 | Branch Amp | 317.961 | 108.8146 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | MB2092520930 | 69 | 69 | Branch Amp | 317.961 | 102.2099 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | STECL_10592 | 69 | 69 | Branch Amp | 317.961 | 104.3764 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | STECL_4720 | 69 | 69 | Branch Amp | 317.961 | 100.1426 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | STECL_4721-1 | 69 | 69 | Branch Amp | 317.961 | 101.8618 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | STECL_4721-2 | 69 | 69 | Branch Amp | 317.961 | 100.8376 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A ( 6450) -> SANW2A ( 6527) CKT 1 | T_060359CASSAVA2A-060360CASSAVA4AC1 | 69 | 69 | Branch Amp | 317.961 | 100.087 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | CONCHO2A (6450) -> SANW2A (6527) CKT 1 | Pre-contingency | 69 | 69 | Amps | 317.961 | - | - | 108.2127 | 118.1923 | 131.6099 | 118.2817 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONCORD8 ( 394) -> JOSHUA ( 398) CKT 1 | BEPC_459 | 138 | 138 | Branch Amp | 962.2503 | - | - | - | 101.8243 | 104.5441 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONCORD8 ( 394) -> JOSHUA ( 398) CKT 1 | L_000419LILLIAN8-000439HIGHPOINTC1 | 138 | 138 | Branch Amp | 962.2503 | - | - | - | 101.5295 | 104.2551 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONCORD8 ( 394) -> JOSHUA ( 398) CKT 1 | L_000432CONLEY-000436GRANDVIEWC1 | 138 | 138 | Branch Amp | 962.2503 | - | - | - | 105.5351 | 107.6285 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONCORD8 ( 394) -> JOSHUA ( 398) CKT 1 | L_000432CONLEY-000439HIGHPOINTC1 | 138 | 138 | Branch Amp | 962.2503 | - | - | - | 103.0293 | 105.7824 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONLEY ( 432) -> HIGHPOINT ( 439) CKT 1 | L_000394CONCORD8-000398JOSHUAC1 | 138 | 138 | Branch Amp | 1112.8635 | - | - | - | - | 103.0458 | - | -
1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONNOLLY_B1 (888887) -> ALLISON_T8 ( 1568) CKT 1 | BASECAMP - BENNETT RD SW 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 104.0355 | - | -
1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONNOLLY_B1 (888887) -> ALLISON_T8 ( 1568) CKT 1 | BEPC_005_1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 101.968 | - | -
1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONNOLLY_B1 (888887) -> ALLISON_T8 ( 1568) CKT 1 | BEPC_242 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.918 | - | -
1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONNOLLY_B1 (888887) -> ALLISON_T8 ( 1568) CKT 1 | EAGLE MOUNTAIN - HICKS/BENNETT 138 KV (DOUBLE B TO B) A NEWLOAD | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 103.9585 | - | -
1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONNOLLY_B1 (888887) -> ALLISON_T8 ( 1568) CKT 1 | L_000541RENO-000595KEETERC1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.0266 | - | -
1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONNOLLY_B1 (888887) -> ALLISON_T8 ( 1568) CKT 1 | L_000579JCKCNTY8-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.9039 | - | -
1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONNOLLY_B1 (888887) -> ALLISON_T8 ( 1568) CKT 1 | L_000595KEETER-000596COTTONDALEC1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.3448 | - | -
1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONNOLLY_B1 (888887) -> ALLISON_T8 ( 1568) CKT 1 | L_000596COTTONDALE-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.9061 | - | -
1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONNOLLY_B1 (888887) -> ALLISON_T8 ( 1568) CKT 1 | L_001570RHOME_8-001594DECATUR_T8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 104.103 | - | -
1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONNOLLY_B1 (888887) -> ALLISON_T8 ( 1568) CKT 1 | L_001582BENNETT_8-001594DECATUR_T8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 104.1012 | - | -
1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONNOLLY_B1 (888887) -> ALLISON_T8 ( 1568) CKT 1 | RAMHORN - HICKS & BASE CAMP - BENNET DC 345 &138 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 103.8167 | - | -
1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONNOLLY_B1 (888887) -> ALLISON_T8 ( 1568) CKT 1 | RAMHORN - HICKS 345 AND BASE CAMP - BENNET 138 (DOUBLE B TO B) CKT 2 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 105.5608 | - | -
1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONNOLLY_B1 (888887) -> ALLISON_T8 ( 1568) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (COMMON TOWER) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 108.6068 | 101.7441 | -
1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONNOLLY_B1 (888887) -> ALLISON_T8 ( 1568) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 105.5608 | - | -
1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CONNOLLY_B1 (888887) -> ALLISON_T8 ( 1568) CKT 1 | WISE COUNTY (BEC) - ALVORD/BRIDGEPORT(BEC) (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 101.8409 | - | -
TONCOR | NORTH | NORTH | NORTH, NORTH | COPPERHD_8 (11809) -> BONHAM_8 ( 1808) CKT 1 | PARIS SW-PACIFIC SW/VALLEY S SW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.6859 | - | -
TONCOR | NORTH | NORTH | NORTH, NORTH | COPPERHD_8 (11809) -> BONHAM_8 ( 1808) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.2291 | 114.0903 | 106.2379 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CORS1_8 ( 3455) -> CHATFIELD ( 200) CKT 1 | L_003723OLYMPUS_SW-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 110.3518 | 129.9617 | 112.2157 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | COSDEN_8 ( 1332) -> BIGSPRIG_8 ( 1322) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 106.0526 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | COSDEN_8 ( 1332) -> ONC900057_TAP (901396) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 1200.7211 | - | 105.3616 | - | - | - | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | BENNETT RD-WISE CTY 138 KV | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 115.5305 | 109.0037 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | BEPC_005_1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 114.4444 | 107.6724 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | BEPC_114 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 106.0012 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | BEPC_21 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.6863 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | BEPC_243 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 106.9374 | 101.034 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | BEPC_283_1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 128.4799 | 120.4065 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | L_000501HILLTOP8-000508RIKERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 103.3466 | 128.2123 | 121.1887 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | L_000508RIKER-000516ZIONHILLC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 103.3477 | 128.2139 | 121.1904 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | L_000516ZIONHILL-000543SWIMMERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 105.3922 | 130.3347 | 123.2421 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | L_000543SWIMMER-000588WILLOWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 106.3151 | 131.2831 | 124.1672 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | L_000570WISECNTY-000571HIDEOUTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 103.426 | 127.5384 | 119.4209 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | L_000571HIDEOUT-000579JCKCNTY8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 104.2888 | 128.4763 | 120.3232 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | L_000579JCKCNTY8-000580WSTBROOKC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 106.8185 | 131.8029 | 124.674 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | L_000579JCKCNTY8-000600BRIDGEPORTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 106.187 | 100.1679 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | L_000580WSTBROOK-000588WILLOWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 106.51 | 131.4678 | 124.3477 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | L_000590PERCHHILL-000600BRIDGEPORTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 104.6586 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | L_000590PERCHHILL-000608CRAFTONC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 103.5265 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | L_000608CRAFTON-000620BOWIE8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 102.9446 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | L_001565BRDGPORT_8-001590BRDGPORT_T8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 114.5286 | 107.9404 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | L_001582BENNETT_8-001590BRDGPORT_T8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 114.526 | 107.9379 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | WISE COUNTY - JACK COUNTY (BEPC) 138 KV (SINGLE B TO B) HIDEOUT | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 104.377 | - | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COTTONDALE ( 596) -> KEETER ( 595) CKT 1 | WISE COUNTY (BEC) - ALVORD/BRIDGEPORT(BEC) (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 114.443 | 107.6723 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COURTLND1_5 ( 1931) -> CHILSW1_5 ( 2420) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 2630.7087 | - | - | - | 106.845 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COURTLND1_5 ( 1931) -> CHILSW1_5 ( 2420) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 2630.7087 | - | - | - | 101.5659 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COURTLND1_5 ( 1931) -> CHILSW1_5 ( 2420) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 2630.7087 | - | - | - | 103.6089 | 109.4549 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COURTLND1_5 ( 1931) -> CHILSW1_5 ( 2420) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 2630.7087 | - | - | - | 105.7321 | 111.7288 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COURTLND1_5 ( 1931) -> CHILSW1_5 ( 2420) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 2630.7087 | - | - | - | 106.9152 | 112.9051 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COURTLND1_5 ( 1931) -> CHILSW1_5 ( 2420) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2630.7087 | - | - | - | - | 100.3879 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COURTLND1_5 ( 1931) -> CHILSW1_5 ( 2420) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2630.7087 | - | - | - | - | 100.2012 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COURTLND1_5 ( 1931) -> CHILSW1_5 ( 2420) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 345 | 345 | Branch Amp | 2630.7087 | - | - | - | 104.6047 | 110.6872 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COURTLND1_5 ( 1931) -> CHILSW1_5 ( 2420) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 2630.7087 | - | - | - | - | 103.7643 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COURTLND1_5 ( 1931) -> CHILSW1_5 ( 2420) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2630.7087 | - | - | - | 103.916 | 110.2091 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COURTLND1_5 ( 1931) -> CHILSW1_5 ( 2420) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 2630.7087 | - | - | - | 102.9972 | 109.0587 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COURTLND1_5 ( 1931) -> CHILSW1_5 ( 2420) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2630.7087 | - | - | - | 103.7647 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COURTLND1_5 ( 1931) -> CHILSW1_5 ( 2420) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2630.7087 | - | - | - | 101.8116 | 108.1301 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | COURTLND1_5 ( 1931) -> CHILSW1_5 ( 2420) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 2630.7087 | - | - | - | 103.7682 | 109.56 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | COYOTE_8 (23832) -> SALEM_8 (10041) CKT 1 | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 895.3112 | 104.7807 | - | - | 100.6048 | 104.4827 | 100.21 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | COYOTE_8 (23832) -> SALEM_8 (10041) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 106.7125 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | COYOTE_8 (23832) -> SALEM_8 (10041) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 895.3112 | - | 117.6956 | - | - | - | - | -
RCOMAN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CPSES_UNIT1 (150111) -> COMCHPKW_5 ( 1900) CKT 1 | XFMR-COMCHPKW_5-2 | 345 | 22 | Branch MVA | 781 | 157.0943 | 160.1613 | 155.5075 | 155.4865 | 156.3053 | 156.2803 | -
RCOMAN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CPSES_UNIT1 (150111) -> COMCHPKW_5 ( 1900) CKT 2 | XFMR-COMCHPKW_5-1 | 345 | 22 | Branch MVA | 781 | 157.0545 | 160.126 | 155.4799 | 155.48 | 156.297 | 156.2458 | -
RCOMAN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CPSES_UNIT2 (150112) -> COMCHPKW_5 ( 1900) CKT 1 | XFMR-COMCHPKW_5-2_REVA | 345 | 22 | Branch MVA | 781 | 155.4756 | 161.0827 | 158.81 | 163.1349 | 166.9259 | 156.8784 | -
RCOMAN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CPSES_UNIT2 (150112) -> COMCHPKW_5 ( 1900) CKT 2 | XFMR-COMCHPKW_5-1_REVA | 345 | 22 | Branch MVA | 781 | 155.4756 | 161.0827 | 158.81 | 163.1349 | 166.9259 | 156.8784 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CROSRDSW_8 ( 1844) -> COMM_SW_8 ( 1816) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.6594 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CROSRDSW_8 ( 1844) -> COMM_SW_8 ( 1816) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 105.2795 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CROSRDSW_8 ( 1844) -> COMM_SW_8 ( 1816) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.6954 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CROSRDSW_8 ( 1844) -> COMM_SW_8 ( 1816) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 105.1934 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CROSRDSW_8 ( 1844) -> COMM_SW_8 ( 1816) CKT 1 | PARIS SW-PACIFIC SW/VALLEY S SW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 117.2833 | 126.0665 | 118.9968 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | CROSRDSW_8 ( 1844) -> COMM_SW_8 ( 1816) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | 100.9619 | 130.2101 | 140.6372 | 131.7776 | -
TBTU | EAST | EAST | EAST, EAST | CSGR (32007) -> BRYN_SOUTH (32880) CKT 1 | L_032000CSST-032001CSPTC2 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | 117.7765 | 116.5329 | -
TRAYBN,TONCOR | EAST | EAST | EAST, EAST | CUMBY_9 ( 1812) -> CUMBY_RC ( 6861) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 103.4052 | 121.3876 | 104.4234 | -
TRAYBN,TONCOR | EAST | EAST | EAST, EAST | CUMBY_9 ( 1812) -> CUMBY_RC ( 6861) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 112.2833 | 129.9352 | 112.2682 | -
TRAYBN,TONCOR | EAST | EAST | EAST, EAST | CUMBY_9 ( 1812) -> CUMBY_RC ( 6861) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 105.084 | 123.048 | 106.0387 | -
TRAYBN,TONCOR | EAST | EAST | EAST, EAST | CUMBY_9 ( 1812) -> CUMBY_RC ( 6861) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 114.0004 | 131.7456 | 114.0296 | -
TRAYBN,TONCOR | EAST | EAST | EAST, EAST | CUMBY_9 ( 1812) -> CUMBY_RC ( 6861) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 105.8461 | 124.3502 | 106.9472 | -
TRAYBN,TONCOR | EAST | EAST | EAST, EAST | CUMBY_9 ( 1812) -> CUMBY_RC ( 6861) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 115.1251 | 133.2353 | 114.7184 | -
TRAYBN,TONCOR | EAST | EAST | EAST, EAST | CUMBY_9 ( 1812) -> CUMBY_RC ( 6861) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 107.5113 | 125.9876 | 108.6887 | -
TRAYBN,TONCOR | EAST | EAST | EAST, EAST | CUMBY_9 ( 1812) -> CUMBY_RC ( 6861) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 116.8389 | 134.993 | 116.9225 | -
TRAYBN,TONCOR | EAST | EAST | EAST, EAST | CUMBY_9 ( 1812) -> CUMBY_RC ( 6861) CKT 1 | CARTWHEEL_CON | 138 | 138 | Branch Amp | 518.7784 | - | - | - | - | 100.6442 | - | -
TRAYBN,TONCOR | EAST | EAST | EAST, EAST | CUMBY_9 ( 1812) -> CUMBY_RC ( 6861) CKT 1 | L_001697SULSP_SS1_5-888847CARTWHEEL_POIC1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | - | 100.219 | - | -
TRAYBN,TONCOR | EAST | EAST | EAST, EAST | CUMBY_9 ( 1812) -> CUMBY_RC ( 6861) CKT 1 | L_888847CARTWHEEL_POI-002464CASHSW_T5C1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | - | 101.7821 | - | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T8 ( 1815) -> CUMBY1_T9 ( 1813) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 106.036 | 124.0693 | 107.0666 | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T8 ( 1815) -> CUMBY1_T9 ( 1813) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 114.9162 | 132.6376 | 114.9184 | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T8 ( 1815) -> CUMBY1_T9 ( 1813) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 107.7213 | 125.7398 | 108.6873 | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T8 ( 1815) -> CUMBY1_T9 ( 1813) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 116.6393 | 134.4543 | 116.6811 | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T8 ( 1815) -> CUMBY1_T9 ( 1813) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 108.4765 | 127.0356 | 109.5948 | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T8 ( 1815) -> CUMBY1_T9 ( 1813) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 117.7577 | 135.9414 | 117.3916 | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T8 ( 1815) -> CUMBY1_T9 ( 1813) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 110.148 | 128.6828 | 111.3359 | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T8 ( 1815) -> CUMBY1_T9 ( 1813) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 119.4771 | 137.7056 | 119.578 | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T8 ( 1815) -> CUMBY1_T9 ( 1813) CKT 1 | CARTWHEEL_CON | 138 | 138 | Branch Amp | 518.7784 | - | - | - | - | 103.3242 | - | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T8 ( 1815) -> CUMBY1_T9 ( 1813) CKT 1 | L_001697SULSP_SS1_5-888847CARTWHEEL_POIC1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | - | 102.8972 | - | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T8 ( 1815) -> CUMBY1_T9 ( 1813) CKT 1 | L_888847CARTWHEEL_POI-002464CASHSW_T5C1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | - | 104.4647 | - | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T8 ( 1815) -> CUMBY1_T9 ( 1813) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 518.7784 | - | - | - | - | 102.5647 | - | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T9 ( 1813) -> CUMBY_9 ( 1812) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 105.3854 | 123.3936 | 106.404 | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T9 ( 1813) -> CUMBY_9 ( 1812) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 114.2647 | 131.9556 | 114.2535 | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T9 ( 1813) -> CUMBY_9 ( 1812) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 107.0685 | 125.0605 | 108.0229 | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T9 ( 1813) -> CUMBY_9 ( 1812) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 115.9856 | 133.7699 | 116.0158 | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T9 ( 1813) -> CUMBY_9 ( 1812) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 107.8261 | 126.3587 | 108.9307 | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T9 ( 1813) -> CUMBY_9 ( 1812) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 117.1063 | 135.2583 | 116.7178 | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T9 ( 1813) -> CUMBY_9 ( 1812) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 109.4954 | 128.0025 | 110.672 | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T9 ( 1813) -> CUMBY_9 ( 1812) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | 118.8237 | 137.0201 | 118.9113 | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T9 ( 1813) -> CUMBY_9 ( 1812) CKT 1 | CARTWHEEL_CON | 138 | 138 | Branch Amp | 518.7784 | - | - | - | - | 102.6481 | - | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T9 ( 1813) -> CUMBY_9 ( 1812) CKT 1 | L_001697SULSP_SS1_5-888847CARTWHEEL_POIC1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | - | 102.2216 | - | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T9 ( 1813) -> CUMBY_9 ( 1812) CKT 1 | L_888847CARTWHEEL_POI-002464CASHSW_T5C1 | 138 | 138 | Branch Amp | 518.7784 | - | - | - | - | 103.7874 | - | -
TONCOR | EAST | EAST | EAST, EAST | CUMBY1_T9 ( 1813) -> CUMBY_9 ( 1812) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 518.7784 | - | - | - | - | 101.9092 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | CYCLONE_5 (11689) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 103.0697 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | CYCLONE_5 (11689) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 103.7422 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | CYCLONE_5 (11689) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.1061 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | CYCLONE_5 (11689) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.7663 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | CYCLONE_5 (11689) -> FARMVLSW_5 ( 1685) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 103.6119 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | CYCLONE_5 (11689) -> FARMVLSW_5 ( 1685) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 111.1505 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | CYCLONE_5 (11689) -> FARMVLSW_5 ( 1685) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 106.7413 | - | -
TAEPTC | COAST | COAST | COAST, COAST | DACOSTA4A ( 8722) -> CHOCBAYU4A (80064) CKT 1 | L_008125LOLITA4A-008172VICTORIA4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 111.5069 | - | -
TAEPTC | COAST | COAST | COAST, COAST | DACOSTA4A ( 8722) -> CHOCBAYU4A (80064) CKT 1 | L_008144SEADRFTC4A-008189TUNGSTEN4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 111.7417 | - | -
TAEPTC | COAST | COAST | COAST, COAST | DACOSTA4A ( 8722) -> CHOCBAYU4A (80064) CKT 1 | L_008144SEADRFTC4A-080065MELNCRK4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 111.7172 | - | -
TAEPTC | COAST | COAST | COAST, COAST | DACOSTA4A ( 8722) -> CHOCBAYU4A (80064) CKT 1 | M100052100072 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 121.9833 | - | -
TAEPTC | COAST | COAST | COAST, COAST | DACOSTA4A ( 8722) -> CHOCBAYU4A (80064) CKT 1 | MB1000710005-2 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 121.22 | - | -
TAEPTC | COAST | COAST | COAST, COAST | DACOSTA4A ( 8722) -> CHOCBAYU4A (80064) CKT 1 | MB1291012930 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 111.6535 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.6482 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | BAS_RANCH_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.5904 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2964 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | BLUBIRD_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2723 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | CLUTCH_CITY_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.538 | 103.3609 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | E_DDPEC_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6051 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | E_FRNYPP_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9211 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | E_FRNYPP_CC2_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9379 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | E_FTR_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5769 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | E_JCKCNTY2_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1584 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | E_PANDA_S_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5913 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | E_PANDA_T1_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.653 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | E_PANDA_T2_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6834 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | E_TGCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0229 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | E_WCPP_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1248 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | E_WHCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8575 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | E_WHCCS2_CC2_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.779 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | E5DVA1C1_1_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.8917 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_000575JCKCNTY5UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4164 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_000579JCKCNTY8UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0925 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_006100OKLA7AUC0 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.459 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_110014WAP_WAP_G4UN4 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4225 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_120041MLSES_UNIT1UL1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.768 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_120042MLSES_UNIT2UL2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8037 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_120043MLSES_UNIT3UL3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8147 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_120131OGSES_UNIT1AUL1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2285 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_120132OGSES_UNIT2UL2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2286 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_150023MCSES_UNIT8UN8 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2067 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_150101LEG_LEG_G1UL1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0953 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_150102LEG_LEG_G2UL2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1635 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_150111CPSES_UNIT1UU1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.3207 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_150112CPSES_UNIT2UU2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.3067 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_150741SCES_UNIT1UL1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5229 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_170126CALAVER_JKS2UL2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3844 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_888839BAS_RANCH_POIUC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.5911 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_888879BLUBIRD_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0681 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | G_RIO_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3696 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | J5LCA1C1_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3723 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.2238 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_001839STONCRK_8-140002SHER1_TLC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5828 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.2657 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9355 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9306 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.5732 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5366 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_005133ELMCREEK-005380SHAULAC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2306 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9729 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_008127LAN_CTY4A-008130LAN_CTY4BCS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.5494 | 101.6596 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.3742 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042030SAMARI__B138-042050CLUTE___B138C26 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9984 | 100.7888 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042030SAMARI__B138-042110ANGLTN_POI_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9972 | 100.7874 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042050CLUTE___B138-043150RIWOOD_X82B8C82 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7907 | 100.5845 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042050CLUTE___B138-043240SINTEK_X26B8C26 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1082 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042100HUDSON_POI_8-042940MONSAN_POI_8C04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3935 | 101.7768 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042100HUDSON_POI_8-888849CLUTCH_CITY_POIC04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.8685 | 103.2421 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042110ANGLTN_POI_8-043150RIWOOD_X82B8C82 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8207 | 100.6149 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042150BASF___POI_8-042210BRZPRT_S02_8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 114.1588 | 118.7687 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042150BASF___POI_8-042810HOFMAN_X02B8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 118.3399 | 122.9247 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042210BRZPRT_S02_8-042215COPPER_X02B8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 111.1228 | 115.7463 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042215COPPER_X02B8-042540JONCRK__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 108.8816 | 112.378 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042410BURKE__POI_8-042980NASH___S02_8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.1421 | 108.3506 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042410BURKE__POI_8-888850LONG_POIC02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8768 | 102.1753 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042420BEASLY_POI_8-044190E_BERN__B138C60 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.4222 | 107.9083 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042420BEASLY_POI_8-044541ORCHRD_T60_8C60 | 138 | 138 | Branch Amp | 1137.9656 | 103.2561 | - | - | - | 112.9263 | 117.2136 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042420BEASLY_POI_8-112433TAV_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8491 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042570ARCHER_POI_8-044430MANVEL_S26_8C26 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.0066 | 103.4113 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042810HOFMAN_X02B8-042880LKJACK_S02_8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 118.612 | 123.1949 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042880LKJACK_S02_8-043170RETREV__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 122.4132 | 126.9694 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042940MONSAN_POI_8-043070PETSON_X04B8C04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.853 | 102.2325 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042960MUSTNG_S04_8-043500WEBSTR_B138AC&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.4168 | 106.7054 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042980NASH___S02_8-888852LIATRIS_POIC02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.7597 | 107.9693 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_042985DYANN__POI_8-043570WHARTN__60B8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | 102.8169 | - | - | - | 122.5525 | 120.983 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_043010NEWGLF_S60_8-043190S_LANE__B138C60 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 120.477 | 113.5082 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_043010NEWGLF_S60_8-043340GLFTIE_POI_8C60 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 120.9442 | 113.9746 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_043070PETSON_X04B8-044890SNUG___POI_8C04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.0745 | 102.4544 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_043570WHARTN__60B8-044150HNGFRD_POI_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | 100.382 | - | - | - | 119.9618 | 118.5138 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_044015W_A_P__POI8B-044170CRABB__S09_8C09 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 116.0354 | 110.0007 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_044060BLUE___POI_5-044220JULIA__POI_5C72 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.2709 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_044150HNGFRD_POI_8-044190E_BERN__B138C60 | 138 | 138 | Branch Amp | 1137.9656 | 109.8739 | - | 101.5941 | - | 127.4774 | 129.0769 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_044170CRABB__S09_8-044570READNG_S09_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 110.1745 | 104.1798 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_044200HILLJE__B345-044220JULIA__POI_5C72 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.7214 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_044230FLEWLN__B138-044510OBRIEN_B138AC&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3227 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_044280FTBEND__B138-044570READNG_S09_8C09 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.3209 | 100.3456 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_044280FTBEND__B138-044615ROSNBG_S60_8C60 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 109.1458 | 113.44 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_044410KARSTN_C26_8-048173ALVIN_26TP_8C26 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.6668 | 102.0695 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_044430MANVEL_S26_8-048173ALVIN_26TP_8C26 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.8503 | 102.2528 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_044540ORCHRD_S60_8-044615ROSNBG_S60_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | 101.7988 | - | - | - | 111.3305 | 115.7021 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_888849CLUTCH_CITY_POI-042960MUSTNG_S04_8C04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.7742 | 107.0577 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_888852LIATRIS_POI-044010W_A_P__POI8AC02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 112.6849 | 121.6796 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8266 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | L10012900 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.5494 | 101.6596 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | LAKE CREEK - RATTLE SNAKE 345 KV WITH SANDY UNIT (SINGLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5229 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | LIATRIS_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.6051 | 109.2021 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | MB210140210145-AAAAB | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.019 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.6451 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2726 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | N5GSU2_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3844 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P1-2_(21.2_SODG_44541) | 138 | 138 | Branch Amp | 1137.9656 | 103.5893 | - | - | - | 113.2976 | 117.5501 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P1-2_(40600-120095-1) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5769 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P1-2_(42980-44010-02)-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.7597 | 107.9693 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P1-2_(42980-44010-02)-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 112.6849 | 121.6796 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P1-2_(44015-49215-GL) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4225 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P1-2_(46020-49208-GL) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0953 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P1-2_(46020-49209-GL) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1635 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P1-2_(8130-43190-1) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.5494 | 101.6596 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P1-2_ALVIN_CKT05 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.8421 | 102.2447 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P1-2_HOC_BUS_REACTOR | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0685 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7.1_CP8-CP9_CP8-CP9 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.5013 | 105.8623 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>JULIA | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.16 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T0202C | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 118.6063 | 123.2098 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T0202E | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 114.3099 | 118.9359 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T0202H | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 108.8826 | 112.3788 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T0202J-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.0794 | 108.3171 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T0202J-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.9334 | 109.5501 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T0202K-1-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.685 | 102.675 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T0202K-1-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.556 | 103.9126 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T0405 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.241 | 106.6494 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T0463 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.4137 | 106.6997 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T0493 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.4854 | 106.7531 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T0980 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 120.6607 | 114.5812 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T1827BY | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8578 | 100.6936 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T1827D | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.5715 | 103.3878 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T1827H | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.5047 | 101.7981 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T1827J | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.7291 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T1899X | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3653 | 101.2296 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T2573B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9391 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T2626D | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.9033 | 103.346 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T2682EX1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 113.5063 | 114.0801 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T2682EX2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 114.0619 | 114.6363 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T2682GY1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 114.1181 | 114.6928 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T2682GY2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 114.1184 | 114.6932 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T2764Y_ERCa | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0194 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T4848K | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.7148 | 100.7387 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T6060D | 138 | 138 | Branch Amp | 1137.9656 | 101.6561 | - | - | - | 121.2215 | 119.8222 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T6472J | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4681 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T9797B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3981 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>>T9899A | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 110.3274 | 104.8888 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>T0202GX | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 114.3399 | 118.2255 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>T2682DX | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 109.5215 | 110.0764 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1_E1>T6060F | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.2041 | 101.8813 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | P7-1>>T2727L | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.0578 | 101.8808 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | Pre-contingency | 138 | 138 | Amps | 874.3927 | 106.1806 | - | - | - | 125.3901 | 124.7733 | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | RAT_SNAKE-SNDY_CREEK_5 (SINGLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5229 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | STP - HOUDINI & STP - SHAULA | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9794 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | TWIN_OAK_BKR_8995_345_OAK_GROVE_SINGLE_B_T0_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2286 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | TWIN_OAK_BKR_9000_345_OAK_GROVE_SINGLE_B_T0_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2285 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.0589 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1249 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | XFMR-MARTINLK_5-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.768 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | XFMR-MARTINLK_5-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8037 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | XFMR-MARTINLK_5-3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8147 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | XFMR-MTCK_8T8-8 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2067 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | XFMR-SANDYCRK_5-01 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5229 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> NEEDVL__B138 (42380) CKT 89 | XFMR-WHCCS2_5-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0732 | - | -
TCNPE | COAST | COAST | COAST, COAST | DAMON__S89_8 (42370) -> W_COL_89T4_8 (43384) CKT 89 | Pre-contingency | 138 | 138 | Amps | 874.3927 | 110.4157 | - | 103.8162 | - | 129.5333 | 128.9147 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | Pre-contingency | 13.8 | 1 | MVA | 70 | - | - | 100.628 | 100.4434 | 100.628 | - | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | AEN_P1-1_GEN_SH5A+5C | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0109 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | AEN_P2HLJ345_RB_570_610_1(94OF224): | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0782 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0628 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | ARGENTA_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0005 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | BAS_RANCH_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.5024 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2236 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | BLUBIRD_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2234 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | DERMOTT - KIRCHHOF CKT 1 & DERMOTT - KIRCHHOF CKT 2 345 KV (DOUBLE B TO B) C | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0206 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | DERMOTT - KIRCHHOF CKT 1 345 KV WIN 2023 - FUTURE (SINGLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0202 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_AMOCOOIL_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0845 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_AMOCOOIL_CC2_TRAIN_NSO | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.115 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_B_DAVIS_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1642 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_BASTEN_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1351 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_BOSQUESW_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0857 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_BRAUNIG_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1188 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_BTE_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1277 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_BVE_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0989 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_BYU_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0062 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_CBECII_CC3_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.3375 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_CBY4_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0759 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_CCEC_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0503 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_CHE_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1358 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_CVC_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1334 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_DDPEC_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.3339 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_DUKE_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0832 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_ETCCS_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0219 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_FERGCC_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1196 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_FORMOSA_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0723 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_FREC_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0267 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_FREC_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0694 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_FRNYPP_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2747 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_FRNYPP_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2743 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_FTR_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2365 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_GUADG_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0928 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_GUADG_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.091 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_INGLCOSW_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0867 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_JACKCNTY_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1191 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_JCKCNTY2_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1469 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_KMCHI_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.128 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_KMCHI_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1297 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_LGE_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0409 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_LOSTPI_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1106 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_LPCCS_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1025 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_LPCCS_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0868 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_NEDIN_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1738 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_NUECES_B_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1626 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_OECCS_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1185 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_OECCS_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1191 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_PANDA_S_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1775 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_PANDA_T1_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2114 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_PANDA_T2_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2139 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_PSA_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0679 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_PSG_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.077 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_TGCCS_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2173 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_THW_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0073 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_THW_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0073 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_TXCTY_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0206 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_WCPP_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2231 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_WHCCS_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2032 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | E_WHCCS2_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.3675 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | ELMAX_POI_Con | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0853 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_000575JCKCNTY5UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1693 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_000579JCKCNTY8UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1001 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_001877MITCHBND_5UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0125 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_003321REDLAND_5UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1227 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_006100OKLA7AUC0 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1739 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_007044L_MARION5_1YUN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.078 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_007048L_GARFIE5_1YUN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0909 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_010012METEOR_5US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0881 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_023908DEAFSMITH_5US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0045 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_023909WALLABY_5US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0391 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_040000CEDARP_B345AUC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1537 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_040700GRNBYU__B345UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0584 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_040710GRNBYU_POI8AUN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0583 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_043060SPEDWY_POI_5US2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0299 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_043060SPEDWY_POI_5US4 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1038 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_043340GLFTIE_POI_8UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0161 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_043990ELMATO_POI_5US2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0458 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_045500T_H_W__POI_5UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0609 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_045515T_H_W__POI_8UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.061 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_060700GAUSS7AUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0245 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_068051REATAUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0142 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_079000GRAYUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1007 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_079007YELLOWWOLFUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0171 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_110014WAP_WAP_G4UN4 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0831 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_110016WAP_WAP_G6UL6 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1432 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_110017WAP_WAP_G7UL7 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1083 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_110018WAP_WAP_G8UL8 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1198 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_110071CBY_CBY_G1UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1722 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_110072CBY_CBY_G2UN2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1747 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_110351STP_STP_G1UU1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.4127 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_110352STP_STP_G2UU2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.4072 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_112261SPACECI_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0678 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_113111LUNIS_CK_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0716 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_113921PARLIMNT_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0263 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_120041MLSES_UNIT1UL1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2005 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_120042MLSES_UNIT2UL2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2008 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_120043MLSES_UNIT3UL3 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2032 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_120131OGSES_UNIT1AUL1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2303 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_120132OGSES_UNIT2UL2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2303 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_120142SCSES_UNIT2UN2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0776 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_143961MISAE2_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0482 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_144211HRNTSLR_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0702 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_150023MCSES_UNIT8UN8 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1384 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_150042GRSES_UNIT2UN2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0485 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_150051HLSES_UNIT3UN3 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0461 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_150052HLSES_UNIT4UN4 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0754 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_150053HLSES_UNIT5UN5 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0733 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_150091LHSES_UNIT1UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.054 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_150092LH2SES_UNIT2UN2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1131 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_150101LEG_LEG_G1UL1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2173 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_150102LEG_LEG_G2UL2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2223 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_150111CPSES_UNIT1UU1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.4151 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_150112CPSES_UNIT2UU2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.411 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_150741SCES_UNIT1UL1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2713 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_153631DORADO_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0082 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_153911PNGT1_PV_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1012 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_154221ASHCRKSL_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0123 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_154331CMPDREPV_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0122 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_160101B_D_B_DAVIG1UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0075 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_160131SAN_SANMIGG1UL1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.05 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_163641CHARGER_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0145 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_163931OUTPOST_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0477 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_170073GID_GIDEONG3UN3 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0282 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_170101FPPYD_FPP_G1UL1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1368 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_170102FPPYD_FPP_G2UL2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1354 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_170103FPPYD_FPP_G3UL3 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.065 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_170126CALAVER_JKS2UL2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2303 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_170671CACHENA_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0766 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_5920EASTDCTIE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1284 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_888839BAS_RANCH_POIUC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.502 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_888841ELMAX_POIUN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0834 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_888851TRIFECTA_POIUN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0828 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_888856HOLLY_POIUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0146 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_888866HANSON_POIUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0115 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_888870BTTM_GRSS_POIUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0382 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_888879BLUBIRD_POIUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2171 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_888881SOLAC_POIUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.002 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | G_RIO_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2258 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | GRAHAM UNIT 2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0485 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | HANSON_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.021 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | HOLLY_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1172 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | J5GSU4_B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0119 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | J5LCA1C1_B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2258 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | J5ST1_B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0119 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_000842GPL_KINGMTSW-000843GPL_KINGMTTPC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.018 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0703 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0319 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_001141HOLTSS_8-132313ECEC_8C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.009 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.3929 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_001839STONCRK_8-140002SHER1_TLC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1775 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.3075 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.098 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2747 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2743 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_003133RICHLND2_5-003199CALFRESTN_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0695 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_003134RICHLND1_5-003186CALPFREST_5C2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0267 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1351 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0196 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_008458B_DAVIS4A-160105B_DAVIS_1_8C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0075 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_008458B_DAVIS4A-160106B_DAVIS_2_8C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0198 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_011270DOGHOUSE_5-023876CLEARFRK_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0668 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_023920ABERNATH_5-141607AEEC_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.048 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_038745TNATTWATER1-111971TOPAZ_8C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0517 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_040000CEDARP_B345A-110076CBY4_1_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0759 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_040010CEDARP_B138A-049201GENGBY2_02_8CGL | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1747 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_040715GRNBYU_POI8B-049211GENGBY7_08_8CGL | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0078 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_042010P_H_R___B138-111131BAC_8C92 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0075 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_042110ANGLTN_POI_8-112597BCH_8C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0027 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_044000W_A_P__POI5A-049205GENWAP6_06_5CGL | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1432 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_044000W_A_P__POI5A-049206GENWAP7_07_5CGL | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1083 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_044005W_A_P__POI5B-049207GENWAP8_08_5CGL | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1198 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_044200HILLJE__B345-111637DANISH_5C01 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0771 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_044200HILLJE__B345-112147PLN_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0369 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_044650SMTHRS_POI_5-112419RABBS_5C01 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0182 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_044880WATERH_POI_5-112878GSTAR_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0262 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_045500T_H_W__POI_5-049204GENTHW5X05_5CGL | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.012 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_045515T_H_W__POI_8-049202GENTHW3X03_8CGL | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0072 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_045515T_H_W__POI_8-049203GENTHW4X04_8CGL | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0073 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_047170H_O_C__POI_8-111800PRO_8C01 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0179 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_059909NOVA_138-059998NOVA8C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0917 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_059909NOVA_138-143115NOVA1SLR_8C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0254 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_068090SAMSW-068092LIBERTYC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0364 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_068092LIBERTY-152433MERCURY_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0084 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_080071ZORILLO7A-080076AJO7AC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1142 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_080071ZORILLO7A-080171SARITA7AC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0378 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L_080171SARITA7A-160299BAFFIN_2_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0378 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L10011585 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0378 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L201000169 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0425 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | L20255426 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0425 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | LAKE CREEK - RATTLE SNAKE 345 KV WITH SANDY UNIT (SINGLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2713 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | M10000271115801 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1687 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | M105311105321 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0409 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | M115851115803 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1142 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | MB100002711580 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1687 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | MB1158011585 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1142 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | MB210140210145-AAAAA | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1192 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | MB210140210145-AAAAB | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1385 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | MB210140210145-AAABA | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0646 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | MB210140210145-AABA | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0979 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | MB210140210145-AABB | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0431 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | MB210140210145-ABAAA | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0833 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | MB210140210145-ABAAB | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.064 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | MB210140210145-ABABB | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0838 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | MB210140210145-ABBA | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0424 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | MB2726627277 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0244 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2287 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2234 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | MITCHELL BEND-WOLF HOLLOW II UNIT 4 345 KV (SINGLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0218 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1019 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | N5GSU2_B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2303 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | ODESSA EHV - NORTH MCCAMEY 345 KV (SINGLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0227 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_BTE_1_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0116 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_BTE_2_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0116 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_BTE_3_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0116 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_BVE_1_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.039 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_BVE_2_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0389 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_CBT_1_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2008 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_CBT_2_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2032 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_CBY_1_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0111 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_CBY_2_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0111 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_CHE_2_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0124 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_CHE_3_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0165 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_CVC_1_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0011 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_DPEC_1_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0565 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_DPEC_2_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0605 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_DPEC_3_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0566 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_DPEC_4_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0605 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_DPEC_5_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0503 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_FTR_1_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1047 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_FTR_2_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1047 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_FTR_3_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1047 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_GEN_BLY-CBT_C0_111143 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0677 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_GEN_BLY-CBT_C1_111141 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0079 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_GEN_BLY-CBT_C2_111142 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0102 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_GEN_RNS-FTR_C0_120094 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0392 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_PSG_1_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0104 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-1_PSG_2_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0104 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-2_(40015-49200-GL) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1722 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-2_(40450-110666-02) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0166 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-2_(40600-120095-1) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2365 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-2_(40890-113219-01) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0375 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-2_(41430-110825-03) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0011 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-2_(42985-110797-60) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1023 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-2_(44015-49215-GL) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0831 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-2_(44090-111865-1) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0092 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-2_(44200-112261-1) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0678 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-2_(46020-49208-GL) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2173 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P1-2_(46020-49209-GL) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2223 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P7-1_E1>>T0202K-2-2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0309 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P7-1_E1>>T6060B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0218 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P7-1_E1>>T7475B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1334 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P7-1_E1>>T9797B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.3341 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | P7-1_E1>T6060F | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1033 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | PINEFOREST_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0368 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | QUANT_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0028 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | R4U2A5C1_1_B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1188 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | RAT_SNAKE-SNDY_CREEK_5 (SINGLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2713 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | SAM_NAV_P7F1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0382 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | SAN_PAT_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0759 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | SKYSLY_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0047 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | SOLACE_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0024 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | STECL_10262 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.05 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | T_059908NOVA_345-059998NOVA8CT1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0917 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | TRIFECTA_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0829 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | TWIN_OAK_BKR_8995_345_OAK_GROVE_SINGLE_B_T0_B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2303 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | TWIN_OAK_BKR_9000_345_OAK_GROVE_SINGLE_B_T0_B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2303 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | U3GSU1_B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0345 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.5319 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2231 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | WINDMILL - AJSWOPE (SINGLE B TO B) SUM 2028 - FUTURE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0391 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1008 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | XFMR-HANDLEYC_8-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0461 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | XFMR-HANDLEYC_8-3 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0733 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | XFMR-HANDLEYD_8-2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0754 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | XFMR-LKHB_1T8-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.054 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | XFMR-LKHB_2T8-2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1131 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | XFMR-MARTINLK_5-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2005 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | XFMR-MARTINLK_5-2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2008 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | XFMR-MARTINLK_5-3 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2032 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | XFMR-MTCK_8T8-8 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1384 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | XFMR-MTENTRPR_5G-4 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0367 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | XFMR-SANDYCRK_5-01 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2713 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | XFMR-STRYKER_8-2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0776 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | XFMR-WHCCS2_4-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0218 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | XFMR-WHCCS2_5-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2208 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | XFMR-WLFHMDPT_5-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1008 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_1X (151195) -> DEC_1STR (500368) CKT 2 | YELLOW_WOLF_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0177 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | Pre-contingency | 13.8 | 1 | MVA | 70 | - | - | 100.628 | 100.4433 | 100.628 | - | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | AEN_P1-1_GEN_SH5A+5C | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0109 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | AEN_P2HLJ345_RB_570_610_1(94OF224): | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0782 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0628 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | ARGENTA_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0005 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | BAS_RANCH_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.5024 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2236 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | BLUBIRD_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2234 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | DERMOTT - KIRCHHOF CKT 1 & DERMOTT - KIRCHHOF CKT 2 345 KV (DOUBLE B TO B) C | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0206 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | DERMOTT - KIRCHHOF CKT 1 345 KV WIN 2023 - FUTURE (SINGLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0201 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_AMOCOOIL_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0845 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_AMOCOOIL_CC2_TRAIN_NSO | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.115 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_B_DAVIS_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1642 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_BASTEN_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1351 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_BOSQUESW_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0857 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_BRAUNIG_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1188 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_BTE_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1277 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_BVE_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0989 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_BYU_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0062 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_CBECII_CC3_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.3375 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_CBY4_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0759 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_CCEC_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0503 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_CHE_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1357 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_CVC_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1334 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_DDPEC_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.3339 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_DUKE_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0832 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_ETCCS_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0219 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_FERGCC_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1195 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_FORMOSA_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0723 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_FREC_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0267 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_FREC_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0694 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_FRNYPP_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2747 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_FRNYPP_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2743 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_FTR_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2365 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_GUADG_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0928 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_GUADG_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.091 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_INGLCOSW_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0867 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_JACKCNTY_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1191 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_JCKCNTY2_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1469 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_KMCHI_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.128 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_KMCHI_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1296 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_LGE_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0409 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_LOSTPI_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1106 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_LPCCS_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1025 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_LPCCS_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0868 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_NEDIN_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1737 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_NUECES_B_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1626 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_OECCS_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1185 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_OECCS_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1191 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_PANDA_S_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1775 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_PANDA_T1_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2114 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_PANDA_T2_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2139 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_PSA_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0678 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_PSG_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.077 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_TGCCS_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2173 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_THW_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0072 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_THW_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0072 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_TXCTY_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0206 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_WCPP_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2231 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_WHCCS_CC1_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2032 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | E_WHCCS2_CC2_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.3674 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | ELMAX_POI_Con | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0853 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_000575JCKCNTY5UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1693 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_000579JCKCNTY8UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1001 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_001877MITCHBND_5UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0125 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_003321REDLAND_5UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1227 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_006100OKLA7AUC0 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1739 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_007044L_MARION5_1YUN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.078 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_007048L_GARFIE5_1YUN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0909 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_010012METEOR_5US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0881 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_023908DEAFSMITH_5US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0045 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_023909WALLABY_5US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0391 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_040000CEDARP_B345AUC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1537 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_040700GRNBYU__B345UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0584 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_040710GRNBYU_POI8AUN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0583 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_043060SPEDWY_POI_5US2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0299 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_043060SPEDWY_POI_5US4 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1038 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_043340GLFTIE_POI_8UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0161 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_043990ELMATO_POI_5US2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0458 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_045500T_H_W__POI_5UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0609 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_045515T_H_W__POI_8UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.061 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_060700GAUSS7AUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0245 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_068051REATAUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0142 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_079000GRAYUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1006 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_079007YELLOWWOLFUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0171 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_110014WAP_WAP_G4UN4 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0831 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_110016WAP_WAP_G6UL6 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1431 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_110017WAP_WAP_G7UL7 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1083 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_110018WAP_WAP_G8UL8 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1198 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_110071CBY_CBY_G1UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1722 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_110072CBY_CBY_G2UN2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1747 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_110351STP_STP_G1UU1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.4127 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_110352STP_STP_G2UU2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.4072 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_112261SPACECI_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0678 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_113111LUNIS_CK_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0716 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_113921PARLIMNT_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0263 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_120041MLSES_UNIT1UL1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2005 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_120042MLSES_UNIT2UL2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2008 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_120043MLSES_UNIT3UL3 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2032 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_120131OGSES_UNIT1AUL1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2303 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_120132OGSES_UNIT2UL2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2303 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_120142SCSES_UNIT2UN2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0776 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_143961MISAE2_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0482 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_144211HRNTSLR_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0702 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_150023MCSES_UNIT8UN8 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1384 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_150042GRSES_UNIT2UN2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0485 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_150051HLSES_UNIT3UN3 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0461 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_150052HLSES_UNIT4UN4 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0754 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_150053HLSES_UNIT5UN5 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0733 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_150091LHSES_UNIT1UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.054 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_150092LH2SES_UNIT2UN2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1131 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_150101LEG_LEG_G1UL1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2173 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_150102LEG_LEG_G2UL2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2222 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_150111CPSES_UNIT1UU1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.4151 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_150112CPSES_UNIT2UU2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.411 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_150741SCES_UNIT1UL1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2713 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_153631DORADO_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0082 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_153911PNGT1_PV_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1012 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_154221ASHCRKSL_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0123 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_154331CMPDREPV_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0121 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_160101B_D_B_DAVIG1UN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0075 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_160131SAN_SANMIGG1UL1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.05 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_163641CHARGER_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0145 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_163931OUTPOST_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0477 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_170073GID_GIDEONG3UN3 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0282 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_170101FPPYD_FPP_G1UL1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1368 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_170102FPPYD_FPP_G2UL2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1354 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_170103FPPYD_FPP_G3UL3 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.065 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_170126CALAVER_JKS2UL2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2303 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_170671CACHENA_S1US1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0766 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_5920EASTDCTIE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1284 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_888839BAS_RANCH_POIUC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.502 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_888841ELMAX_POIUN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0834 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_888851TRIFECTA_POIUN1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0828 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_888856HOLLY_POIUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0145 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_888866HANSON_POIUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0115 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_888870BTTM_GRSS_POIUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0382 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_888879BLUBIRD_POIUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2171 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_888881SOLAC_POIUS1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.002 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | G_RIO_TRAIN | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2258 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | GRAHAM UNIT 2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0485 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | HANSON_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.021 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | HOLLY_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1172 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | J5GSU4_B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0119 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | J5LCA1C1_B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2258 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | J5ST1_B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0119 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_000842GPL_KINGMTSW-000843GPL_KINGMTTPC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.018 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0703 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0319 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_001141HOLTSS_8-132313ECEC_8C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.009 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.3929 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_001839STONCRK_8-140002SHER1_TLC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1775 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.3075 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.098 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2747 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2743 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_003133RICHLND2_5-003199CALFRESTN_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0695 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_003134RICHLND1_5-003186CALPFREST_5C2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0267 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1351 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0196 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_008458B_DAVIS4A-160105B_DAVIS_1_8C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0075 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_008458B_DAVIS4A-160106B_DAVIS_2_8C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0198 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_011270DOGHOUSE_5-023876CLEARFRK_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0668 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_023920ABERNATH_5-141607AEEC_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.048 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_038745TNATTWATER1-111971TOPAZ_8C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0517 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_040000CEDARP_B345A-110076CBY4_1_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0759 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_040010CEDARP_B138A-049201GENGBY2_02_8CGL | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1747 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_040715GRNBYU_POI8B-049211GENGBY7_08_8CGL | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0078 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_042010P_H_R___B138-111131BAC_8C92 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0075 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_042110ANGLTN_POI_8-112597BCH_8C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0027 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_044000W_A_P__POI5A-049205GENWAP6_06_5CGL | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1431 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_044000W_A_P__POI5A-049206GENWAP7_07_5CGL | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1083 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_044005W_A_P__POI5B-049207GENWAP8_08_5CGL | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1198 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_044200HILLJE__B345-111637DANISH_5C01 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0771 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_044200HILLJE__B345-112147PLN_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0369 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_044650SMTHRS_POI_5-112419RABBS_5C01 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0182 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_044880WATERH_POI_5-112878GSTAR_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0262 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_045500T_H_W__POI_5-049204GENTHW5X05_5CGL | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.012 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_045515T_H_W__POI_8-049202GENTHW3X03_8CGL | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0072 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_045515T_H_W__POI_8-049203GENTHW4X04_8CGL | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0072 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_047170H_O_C__POI_8-111800PRO_8C01 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0179 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_059909NOVA_138-059998NOVA8C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0917 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_059909NOVA_138-143115NOVA1SLR_8C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0254 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_068090SAMSW-068092LIBERTYC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0364 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_068092LIBERTY-152433MERCURY_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0084 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_080071ZORILLO7A-080076AJO7AC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1142 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_080071ZORILLO7A-080171SARITA7AC1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0378 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L_080171SARITA7A-160299BAFFIN_2_5C1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0378 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L10011585 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0378 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L201000169 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0425 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | L20255426 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0425 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | LAKE CREEK - RATTLE SNAKE 345 KV WITH SANDY UNIT (SINGLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2713 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | M10000271115801 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1687 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | M105311105321 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0409 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | M115851115803 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1142 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | MB100002711580 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1687 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | MB1158011585 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1142 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | MB210140210145-AAAAA | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1192 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | MB210140210145-AAAAB | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1385 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | MB210140210145-AAABA | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0646 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | MB210140210145-AABA | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0979 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | MB210140210145-AABB | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0431 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | MB210140210145-ABAAA | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0833 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | MB210140210145-ABAAB | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.064 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | MB210140210145-ABABB | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0838 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | MB210140210145-ABBA | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0424 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | MB2726627277 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0244 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2287 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2234 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | MITCHELL BEND-WOLF HOLLOW II UNIT 4 345 KV (SINGLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0218 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1018 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | N5GSU2_B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2303 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | ODESSA EHV - NORTH MCCAMEY 345 KV (SINGLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0227 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_BTE_1_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0116 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_BTE_2_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0116 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_BTE_3_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0116 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_BVE_1_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.039 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_BVE_2_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0388 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_CBT_1_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2008 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_CBT_2_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2031 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_CBY_1_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0111 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_CBY_2_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0111 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_CHE_2_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0124 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_CHE_3_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0165 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_CVC_1_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0011 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_DPEC_1_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0565 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_DPEC_2_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0605 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_DPEC_3_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0566 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_DPEC_4_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0605 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_DPEC_5_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0503 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_FTR_1_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1047 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_FTR_2_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1047 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_FTR_3_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1047 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_GEN_BLY-CBT_C0_111143 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0677 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_GEN_BLY-CBT_C1_111141 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0079 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_GEN_BLY-CBT_C2_111142 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0102 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_GEN_RNS-FTR_C0_120094 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0392 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_PSG_1_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0104 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-1_PSG_2_COMBINED-CYCLE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0104 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-2_(40015-49200-GL) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1722 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-2_(40450-110666-02) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0165 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-2_(40600-120095-1) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2365 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-2_(40890-113219-01) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0375 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-2_(41430-110825-03) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0011 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-2_(42985-110797-60) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1023 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-2_(44015-49215-GL) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0831 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-2_(44090-111865-1) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0092 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-2_(44200-112261-1) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0678 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-2_(46020-49208-GL) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2173 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P1-2_(46020-49209-GL) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2222 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P7-1_E1>>T0202K-2-2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0309 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P7-1_E1>>T6060B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0218 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P7-1_E1>>T7475B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1334 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P7-1_E1>>T9797B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.3341 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | P7-1_E1>T6060F | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1033 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | PINEFOREST_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0368 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | QUANT_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0028 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | R4U2A5C1_1_B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1187 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | RAT_SNAKE-SNDY_CREEK_5 (SINGLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2713 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | SAM_NAV_P7F1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0382 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | SAN_PAT_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0759 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | SKYSLY_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0047 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | SOLACE_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0024 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | STECL_10262 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.05 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | T_059908NOVA_345-059998NOVA8CT1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0917 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | TRIFECTA_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0829 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | TWIN_OAK_BKR_8995_345_OAK_GROVE_SINGLE_B_T0_B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2303 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | TWIN_OAK_BKR_9000_345_OAK_GROVE_SINGLE_B_T0_B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2303 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | U3GSU1_B | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0345 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.5319 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2231 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | WINDMILL - AJSWOPE (SINGLE B TO B) SUM 2028 - FUTURE | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0391 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1008 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | XFMR-HANDLEYC_8-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0461 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | XFMR-HANDLEYC_8-3 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0733 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | XFMR-HANDLEYD_8-2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0754 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | XFMR-LKHB_1T8-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.054 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | XFMR-LKHB_2T8-2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1131 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | XFMR-MARTINLK_5-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2005 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | XFMR-MARTINLK_5-2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2008 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | XFMR-MARTINLK_5-3 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2032 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | XFMR-MTCK_8T8-8 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1384 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | XFMR-MTENTRPR_5G-4 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0367 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | XFMR-SANDYCRK_5-01 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2713 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | XFMR-STRYKER_8-2 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0776 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | XFMR-WHCCS2_4-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0218 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | XFMR-WHCCS2_5-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.2208 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | XFMR-WLFHMDPT_5-1 | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.1008 | -
RDENT1 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DEC_2Y (151200) -> DEC_2STR (500369) CKT 3 | YELLOW_WOLF_CON | 13.8 | 1 | Branch MVA | 70 | - | - | - | - | - | 100.0177 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DECATUR_T8 ( 1594) -> RHOME_8 ( 1570) CKT 1 | L_000670KRUM-001568ALLISON_T8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 103.8103 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DECATUR_T8 ( 1594) -> RHOME_8 ( 1570) CKT 1 | L_001568ALLISON_T8-888887CONNOLLY_B1C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 106.134 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DECATUR_T8 ( 1594) -> RHOME_8 ( 1570) CKT 1 | NEW-KRUM TAP - DECATUR 138-69 KV AUTO (SINGLE B TO B) DECATUR 138-69 KV AUTO #1 (SINGLE AUTO) (FLATWOOD)-1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 100.1178 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DECATUR_T8 ( 1594) -> RHOME_8 ( 1570) CKT 1 | NEW-KRUM TAP - DECATUR 138-69 KV AUTO (SINGLE B TO B) DECATUR 138-69 KV AUTO #1 (SINGLE AUTO) (FLATWOOD)-2 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 100.1178 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB1 (9187) -> DECKER_MB3 (9188) CKT 1 | Pre-contingency | 138 | 138 | Amps | 2677.5662 | - | - | - | 108.0782 | 113.5719 | 108.3114 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | 3WT_009048GARFIELD5_009071GARFIELD8_090002GARFIELD_TR1 C 1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 104.9207 | - | 105.2387 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | 3WT_009048GARFIELD5_009071GARFIELD8_090003GARFIELD_TR2 C 2 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 105.0467 | - | 105.3665 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | 3WT_009074LYTTON5_009075LYTTON8_009078LYTTON_T1 C 1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 101.2205 | - | 101.4879 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | 3WT_009074LYTTON5_009075LYTTON8_009081LYTTON_T2 C 2 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.7617 | - | 101.021 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | 3WT_009074LYTTON5_009075LYTTON8_077075L_LYTTSP2_1Y C 3 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.7945 | - | 101.0543 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | AEN_AU-DG¦DL_2013 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 104.6399 | - | 104.9234 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | AEN_DP-SH¦OC | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 104.3446 | - | 104.9898 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | AEN_DP-SK¦MC | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.9834 | - | 101.1946 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | AEN_FPP-HO¦LY | 138 | 138 | Branch Amp | 2970.425 | - | - | - | - | - | 100.8154 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | AEN_GF-SR: EP-HC | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 122.0069 | - | 122.634 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | AEN_GF-SR¦EP | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 122.4828 | - | 123.1496 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | AEN_LY-BF¦TV_2017 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 103.9609 | - | 104.2738 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | AEN_LY-FPP:CIS-HO | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 108.4121 | - | 108.0685 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | AEN_LY-FPP¦CIS | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 110.7223 | - | 110.0697 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | AEN_MC-DP_1013¦W_S | 138 | 138 | Branch Amp | 2970.425 | - | - | 106.7621 | 133.2196 | - | 133.8884 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | AEN_MC-DP¦DE | 138 | 138 | Branch Amp | 2970.425 | - | - | 102.4159 | 128.459 | - | 129.1018 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | AEN_P1-1_GEN_SH5A+5C | 138 | 138 | Branch Amp | 2970.425 | - | - | - | - | - | 111.3654 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | AEN_P71TR_HL_AW_138_DBLCKT_1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 108.1459 | - | 108.5367 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | E_FERGCC_CC1_TRAIN | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 102.3127 | - | 102.3782 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | E_SANDHSYD_CC1_TRAIN | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 111.2269 | - | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | E5DVA1C1_1_B | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 104.59 | - | 101.0114 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | E5DVA1C1_1_B_1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 102.3965 | - | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | E5DVA1C1_1_B_2 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 101.2969 | - | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | G8DVA1C1_B | 138 | 138 | Branch Amp | 2970.425 | - | - | - | - | - | 100.1663 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 114.7865 | - | 110.811 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 110.2831 | - | 107.276 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 112.5242 | - | 109.5892 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_000132BELLCNTY8-003415TEMP_SS__8C1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.0208 | - | 100.0315 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.1747 | - | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 109.3443 | - | 106.3738 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.8853 | - | 100.6448 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C2 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.8853 | - | 100.6448 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.1133 | - | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_007040L_AUSTRO5_1Y-007042L_ZORN__5_1YC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.2486 | - | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_007040L_AUSTRO5_1Y-007048L_GARFIE5_1YC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.519 | - | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_007041L_JOHNDU5_1Y-007047L_HORNSB5_1YC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.2764 | - | 100.7107 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_007055L_FPPYD25_1Y-009074LYTTON5C1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 101.1637 | - | 101.2474 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_007310L_SIMGID8_1Y-007319L_BASTCI8_2YC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 101.853 | - | 102.0457 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_007310L_SIMGID8_1Y-007555L_BASTWE8_1YC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.3326 | - | 100.4493 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_007319L_BASTCI8_2Y-007326L_SWIFTE8_1YC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 101.8546 | - | 102.0461 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_007323L_SHADGL8_1Y-007330L_MANOR_8_1YC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | - | - | 100.0839 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_007326L_SWIFTE8_1Y-007331L_CEDAHI8_1YC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 101.4129 | - | 101.6151 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_007330L_MANOR_8_1Y-007331L_CEDAHI8_1YC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.4082 | - | 100.6271 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_009043CISTERN-009073HOLMANC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 101.3339 | - | 101.2975 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_009043CISTERN-009074LYTTON5C1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 102.6455 | - | 102.5085 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_009045DUNLAP8-009195EAST_VILLAGEC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 114.0204 | - | 114.4456 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_009071GARFIELD8-009237STONEYC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 109.2904 | - | 109.8281 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_009075LYTTON8-009259PILOTKNOBC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 105.5637 | - | 106.1822 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_009075LYTTON8-009262BLUFFSPGC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.8347 | - | 101.1536 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_009082MC1013BT-009188DECKER_MB3C1 | 138 | 138 | Branch Amp | 2970.425 | - | - | 105.1351 | 131.5127 | - | 132.2032 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_009184DAFFIN-009271SPRNKL_MB2C1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 115.7921 | - | 116.2057 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_009184DAFFIN-009328AUSTROP8C1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 117.8516 | - | 118.2698 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_009190TRIDGE_MB1-009195EAST_VILLAGEC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 112.9346 | - | 113.3862 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_009191TRIDGE_MB2-009217HOWARDLNC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.5726 | - | 100.86 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_009237STONEY-009240SOUTHEASTC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 108.5129 | - | 109.0527 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_009240SOUTHEAST-009251ONIONCKC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 108.5101 | - | 109.0502 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | L_009262BLUFFSPG-009267SLAUGHTRC1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.1284 | - | 100.4251 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | LCRA TSC_T143_TAE988_1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 102.1398 | - | 102.8189 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | LCRA TSC_T150_T608 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 101.6724 | - | 101.8307 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | LCRA TSC_T150_T608_A | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 101.7108 | - | 101.8693 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | LCRA TSC_T171_T231_1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | - | - | 100.122 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | LCRA TSC_T182_T185 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 107.121 | - | 103.0852 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | LCRA TSC_T185_T246 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 102.6471 | - | 100.459 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | LCRA TSC_T185_T352 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 101.7819 | - | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | LCRA TSC_T255_TAE3121_1 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 109.81 | - | 109.0097 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | LCRA TSC_T410_T648 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 102.3641 | - | 102.2551 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | LCRA TSC_T510_T775 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 101.7938 | - | 102.2617 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | LCRA TSC_T608 | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 101.8553 | - | 102.048 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | LCRATSC_4_WHISVA_HORNSB | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.7694 | - | 101.3272 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | LCRATSC_5_HORNSB_EUCLID | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 102.2276 | - | 102.6407 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | LCRATSC_6_EUCLID_JOHNDU | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 103.8995 | - | 104.6552 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | LCRATSC_7_JOHNDU_ZORN__ | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 101.8461 | - | 101.9451 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | P7-1_E1>>T1827GX_ERC | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 100.6396 | - | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 103.2767 | - | 102.214 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DECKER_MB3 ( 9188) -> DECKER_MB1 ( 9187) CKT 1 | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 138 | 138 | Branch Amp | 2970.425 | - | - | - | 102.019 | - | - | -
TONCOR | WEST | WEST | WEST, WEST | DEEPCRK_8 (1304) -> SACROC_8 (1311) CKT 1 | Pre-contingency | 138 | 138 | Amps | 748.8818 | 110.0685 | 106.825 | 115.7775 | 117.8237 | 110.6733 | 102.4581 | -
TONCOR | EAST | EAST | EAST, EAST | DELEKTAP2_8 ( 3214) -> TYLROMNR_8 ( 3212) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 106.8387 | - | -
TONCOR | EAST | EAST | EAST, EAST | DELELKTAP1_8 ( 3208) -> TYLERE_8 ( 3211) CKT 1 | L_003100MARTINLK_5-003102TYLERGND_5C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 102.2823 | 127.2859 | 114.2118 | -
TONCOR | EAST | EAST | EAST, EAST | DELELKTAP1_8 ( 3208) -> TYLERE_8 ( 3211) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | 102.3467 | 146.9109 | 184.2117 | 160.3234 | -
TONCOR | EAST | EAST | EAST, EAST | DELELKTAP1_8 ( 3208) -> TYLERE_8 ( 3211) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1313.6809 | 100.712 | - | 107.4217 | 152.9649 | - | 165.3865 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | DELTA1_8 ( 1802) -> COMMERCE1_8 ( 1820) CKT 2 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.8644 | - | -
TONCOR | WEST | WEST | WEST, WEST | DERMOTT_8 (11306) -> ENNISCK_8 ( 1314) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 2033.2769 | - | - | - | - | 103.5335 | - | -
TONCOR | WEST | WEST | WEST, WEST | DERMOTT_8 (11306) -> ENNISCK_8 ( 1314) CKT 1 | SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 1 & SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 2033.2769 | - | - | - | - | 114.8935 | 105.0828 | -
TONCOR | WEST | WEST | WEST, WEST | DERMOTT_8 (11306) -> ENNISCK_8 ( 1314) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 2033.2769 | - | - | - | - | 121.3957 | 110.4428 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DES_WILL_POI (888880) -> LIGGETTA2_5 ( 1916) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | 107.1643 | 118.2439 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DES_WILL_POI (888880) -> LIGGETTA2_5 ( 1916) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | 109.9796 | 120.6212 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DES_WILL_POI (888880) -> LIGGETTA2_5 ( 1916) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 101.7116 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DES_WILL_POI (888880) -> LIGGETTA2_5 ( 1916) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 103.7511 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DES_WILL_POI (888880) -> LIGGETTA2_5 ( 1916) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 104.8435 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DES_WILL_POI (888880) -> LIGGETTA2_5 ( 1916) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 103.6779 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DES_WILL_POI (888880) -> LIGGETTA2_5 ( 1916) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 103.3742 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DES_WILL_POI (888880) -> LIGGETTA2_5 ( 1916) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.149 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DES_WILL_POI (888880) -> LIGGETTA2_5 ( 1916) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 101.0139 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DES_WILL_POI (888880) -> LIGGETTA2_5 ( 1916) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.5313 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DESSAU ( 9193) -> MCNEIL_DB1 ( 9076) CKT 2 | AEN_MC-DP¦DE | 138 | 138 | Branch Amp | 2008.1747 | - | - | - | 104.8624 | 111.5293 | 106.3182 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_5 ( 2431) -> DESSWSTR (500084) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.724 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_5 ( 2431) -> DESSWSTR (500084) CKT 1 | 3WT_002847LOOP9_5_002848LOOP9_8_012847LOOP9_2_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.0745 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_5 ( 2431) -> DESSWSTR (500084) CKT 1 | 3WT_002847LOOP9_5_002848LOOP9_8_012848LOOP9_1_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.0745 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 895.3112 | - | - | 101.1228 | - | 130.689 | 140.4115 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | E_ETCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 106.3919 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | ENNIS WEST - STERRETT 138 KV (SINGLE B TO B) A REAGOR SPRINGS | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 111.4619 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | L_000203SARDIS8-012317STERRETTL_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 103.7394 | 108.3979 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | L_002237STERTRD_8-002317STERRETT1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 117.6702 | 111.2644 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 113.7613 | 137.9714 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 109.3578 | 118.7132 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | L_002305AIRPRD_T8-002307MDLTHTXI1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 105.2085 | 115.1502 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | L_002307MDLTHTXI1_8-012307NEWBRCH_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 104.2805 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | L_002308MDLTH_S_8-002309WAX_NW_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 101.7596 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | L_002308MDLTH_S_8-012307NEWBRCH_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 101.3417 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | L_002315WAX_PMP2_8-002319WAX_PMP1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 114.658 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | L_002315WAX_PMP2_8-002320WAX_N_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 115.4162 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | L_002316MG_IND_T8-002319WAX_PMP1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 112.1059 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | L_002320WAX_N_8-002321WAX_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 106.4844 | 131.6088 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 111.1999 | 135.5635 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | DESSW1_8 ( 2424) -> GLNHEIGHTS ( 217) CKT 1 | WAXAHACHI-WAXAHACHI OFC 69KV/ENNIS-STERRETT 138KV (DOUBLE B TO B) A REAGOR | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 115.0342 | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | DKEC2A ( 6152) -> JATN2A ( 6153) CKT 1 | L_006195ROBY2A-006196ROTN2AC1 | 69 | 69 | Branch Amp | 267.7566 | 112.3079 | - | 109.0378 | 100.4368 | 102.0829 | 102.3455 | -
RDOW | COAST | COAST | COAST, COAST | DOW_647Y (110161) -> DOWGESTR (500346) CKT 1 | L_110127DOWGEN_2_8-110128DOWGEN_3_8CSG | 14.4 | 1 | Branch MVA | 100 | - | 126.0806 | - | - | - | - | -
RDOW | COAST | COAST | COAST, COAST | DOW_647Y (110161) -> DOWGESTR (500347) CKT 1 | L_110127DOWGEN_2_8-110128DOWGEN_3_8CSG | 14.4 | 1 | Branch MVA | 100 | - | - | - | - | 124.0314 | 119.9307 | -
RDOW | COAST | COAST | COAST, COAST | DOWGEN_2_8 (110127) -> DOW_G66_ST65 (110126) CKT 1 | Pre-contingency | 138 | 14.4 | MVA | 120 | 133.4533 | 124.6828 | 133.1682 | 131.706 | 128.431 | 123.0984 | -
RDOW | COAST | COAST | COAST, COAST | DOWGEN_2_8 (110127) -> DOWGEN_3_8 (110128) CKT SG | Pre-contingency | 138 | 138 | Amps | 502.0437 | 136.0893 | 125.9077 | 135.7628 | 134.0082 | 129.9065 | 123.8345 | -
RDOW | COAST | COAST | COAST, COAST | DOWGEN_3_8 (110128) -> DOWGEN_1_8 (110120) CKT SG | G_110114DOWG_DOW_G61UP1 | 138 | 138 | Branch Amp | 502.0437 | 101.2536 | - | 100.7777 | - | - | - | -
RDOW | COAST | COAST | COAST, COAST | DOWGEN_3_8 (110128) -> DOWGEN_1_8 (110120) CKT SG | G_110116DOWG_DOW_G63UP1 | 138 | 138 | Branch Amp | 502.0437 | 101.2182 | - | 100.7425 | - | - | - | -
TBTU | EAST | EAST | EAST, EAST | DOWLNGRD (32005) -> ENTERPRISE (32790) CKT 1 | L_032780BRYN_RELLIS-032852BRYN_STEELE_C1 | 138 | 138 | Branch Amp | 912.046 | - | - | - | - | 117.1758 | 115.954 | -
TBTU | EAST | EAST | EAST, EAST | DOWLNGRD (32005) -> ENTERPRISE (32790) CKT 1 | L_032852BRYN_STEELE_-032857BRYN_SNOO138C1 | 138 | 138 | Branch Amp | 912.046 | - | - | - | - | 120.744 | 119.3855 | -
TBTU | EAST | EAST | EAST, EAST | DOWLNGRD (32005) -> ENTERPRISE (32790) CKT 1 | L_032857BRYN_SNOO138-032860BRYN_KOPPEC1 | 138 | 138 | Branch Amp | 912.046 | - | - | - | - | 102.9306 | 102.0122 | -
TBTU | EAST | EAST | EAST, EAST | DOWLNGRD (32005) -> ENTERPRISE (32790) CKT 1 | L_032860BRYN_KOPPE-032895BRYN_WBRN138C1 | 138 | 138 | Branch Amp | 912.046 | - | - | - | - | 107.6931 | 106.4427 | -
TBTU | EAST | EAST | EAST, EAST | DOWLNGRD (32005) -> ENTERPRISE (32790) CKT 1 | L_032878BRYN_GRNPRAI-032895BRYN_WBRN138C1 | 138 | 138 | Branch Amp | 912.046 | - | - | - | - | 112.7461 | 111.4702 | -
TONCOR | EAST | EAST | EAST, EAST | DRY_CREEK_POI (888845) -> ELKTON_5 ( 3105) CKT 1 | L_003100MARTINLK_5-003102TYLERGND_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 108.6945 | - | -
TONCOR | EAST | EAST | EAST, EAST | DRY_CREEK_POI (888845) -> ELKTON_5 ( 3105) CKT 1 | L_003109STRYKER_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 100.5316 | - | -
TONCOR | EAST | EAST | EAST, EAST | DRY_CREEK_POI (888845) -> ELKTON_5 ( 3105) CKT 1 | ML-SK*ME-TR (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 105.6027 | - | -
TONCOR | EAST | EAST | EAST, EAST | DRY_CREEK_POI (888845) -> ELKTON_5 ( 3105) CKT 1 | TRICORNER - TYLER GRANDE (single B TO B) new_load | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 100.9191 | - | -
TONCOR | EAST | EAST | EAST, EAST | DRY_CREEK_POI (888845) -> ELKTON_5 ( 3105) CKT 1 | TRIN-SK*ME (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | 110.0697 | 123.0493 | 112.1058 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DUNLAP5 ( 9044) -> DUNLASTR (500189) CKT 1 | 3WT_009044DUNLAP5_009045DUNLAP8_090007DUNLAP_TR2 C 2 | 345 | 1 | Branch MVA | 672 | - | - | - | 104.1674 | 117.4966 | 105.7527 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DUNLAP5 ( 9044) -> DUNLASTR (500189) CKT 1 | AEN_AU-DG¦DL_2013 | 345 | 1 | Branch MVA | 672 | - | - | - | - | 101.4283 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DUNLAP5 ( 9044) -> DUNLASTR (500190) CKT 2 | 3WT_009044DUNLAP5_009045DUNLAP8_090001DUNLAP_TR C 1 | 345 | 1 | Branch MVA | 672 | - | - | - | 104.1674 | 117.4966 | 105.7527 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DUNLAP5 ( 9044) -> DUNLASTR (500190) CKT 2 | AEN_AU-DG¦DL_2013 | 345 | 1 | Branch MVA | 672 | - | - | - | - | 101.4283 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DUNLASTR (500189) -> DUNLAP8 ( 9045) CKT 1 | 3WT_009044DUNLAP5_009045DUNLAP8_090007DUNLAP_TR2 C 2 | 138 | 1 | Branch MVA | 672 | - | - | - | 103.953 | 109.5838 | 105.1288 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | DUNLASTR (500190) -> DUNLAP8 ( 9045) CKT 2 | 3WT_009044DUNLAP5_009045DUNLAP8_090001DUNLAP_TR C 1 | 138 | 1 | Branch MVA | 672 | - | - | - | 103.953 | 109.5838 | 105.1288 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | EASTON PARK ( 9143) -> HICROS_DB1 ( 9147) CKT 1 | AEN_OC-PK:SE-SR | 138 | 138 | Branch Amp | 2008.1747 | - | - | - | - | 100.0551 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | EASTON PARK ( 9143) -> HICROS_DB1 ( 9147) CKT 1 | AEN_OC-PK¦SE | 138 | 138 | Branch Amp | 2008.1747 | - | - | - | - | 100.0615 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | EILAND_8 (23853) -> LONGSHRE_8 (10035) CKT 1 | L_010080REDBERRY_8-023833BULLDOG_8C1 | 138 | 138 | Branch Amp | 2568.79 | - | - | - | - | 100.6456 | 100.4947 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | EILAND_8 (23853) -> LONGSHRE_8 (10035) CKT 1 | L_010080REDBERRY_8-900043Other_132C1 | 138 | 138 | Branch Amp | 2568.79 | - | - | - | - | 100.7966 | 100.6445 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | EILAND_8 (23853) -> Other_131 (900100) CKT 1 | L_010080REDBERRY_8-023833BULLDOG_8C1 | 138 | 138 | Branch Amp | 2568.79 | 104.419 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | EILAND_8 (23853) -> Other_131 (900100) CKT 1 | L_010080REDBERRY_8-900043Other_132C1 | 138 | 138 | Branch Amp | 2568.79 | 104.6589 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | EILAND_8 (23853) -> Other_131 (900100) CKT 1 | L_023834ELBOW_8-900043Other_132C1 | 138 | 138 | Branch Amp | 2568.79 | 102.5242 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | EILAND_8 (23853) -> Other_131 (900100) CKT 1 | L_023834ELBOW_8-900100Other_131C1 | 138 | 138 | Branch Amp | 2568.79 | 100.584 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | EILAND_8 (23853) -> Other_131 (900100) CKT 1 | Pre-contingency | 138 | 138 | Amps | 861.8416 | - | 228.0828 | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | EINSTN_8 (23852) -> CARTVLRNCH_8 (10018) CKT 1 | L_001328QUARTZSAND_8-010029LILDEWEY_8C1 | 138 | 138 | Branch Amp | 1146.333 | 102.6457 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | EINSTN_8 (23852) -> CARTVLRNCH_8 (10018) CKT 1 | L_001333MCDONALD_8-001334GLASSCNTYN_8C1 | 138 | 138 | Branch Amp | 1146.333 | - | - | - | - | 101.6286 | 100.9176 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | EINSTN_8 (23852) -> CARTVLRNCH_8 (10018) CKT 1 | L_010029LILDEWEY_8-011350WRGRN_P8C1 | 138 | 138 | Branch Amp | 1146.333 | 102.5999 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | EINSTN_8 (23852) -> CARTVLRNCH_8 (10018) CKT 1 | L_011337POLECAT1_8-011350WRGRN_P8C1 | 138 | 138 | Branch Amp | 1146.333 | 100.4688 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | EINSTN_8 (23852) -> CARTVLRNCH_8 (10018) CKT 1 | QUARTZ SAND - POLECAT CREEK 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 1146.333 | 100.4625 | - | - | - | - | - | -
TLCRA,TAEPTC | COAST | COAST | COAST, COAST | EL_CAMPO4A ( 8102) -> L_RICEBI8_1Y (78104) CKT 1 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 138 | 138 | Branch Amp | 920.4134 | - | - | - | - | 105.4869 | - | -
TLCRA,TAEPTC | COAST | COAST | COAST, COAST | EL_CAMPO4A ( 8102) -> L_RICEBI8_1Y (78104) CKT 1 | L_005521GALOWSW8-111583MUSTNGCK_8C1 | 138 | 138 | Branch Amp | 920.4134 | - | - | - | - | 104.105 | 100.3175 | -
TLCRA,TAEPTC | COAST | COAST | COAST, COAST | EL_CAMPO4A ( 8102) -> L_RICEBI8_1Y (78104) CKT 1 | L_008099CORICHI4A-008102EL_CAMPO4AC1 | 138 | 138 | Branch Amp | 920.4134 | - | - | - | - | 101.0477 | - | -
TLCRA,TAEPTC | COAST | COAST | COAST, COAST | EL_CAMPO4A ( 8102) -> L_RICEBI8_1Y (78104) CKT 1 | L_008117GANADO4A-008118EDNA4AC1 | 138 | 138 | Branch Amp | 920.4134 | - | - | - | - | 126.2446 | 107.7808 | -
TLCRA,TAEPTC | COAST | COAST | COAST, COAST | EL_CAMPO4A ( 8102) -> L_RICEBI8_1Y (78104) CKT 1 | L_008117GANADO4A-008192PULSAR4AC1 | 138 | 138 | Branch Amp | 920.4134 | - | - | - | - | 126.8751 | 108.3965 | -
TLCRA,TAEPTC | COAST | COAST | COAST, COAST | EL_CAMPO4A ( 8102) -> L_RICEBI8_1Y (78104) CKT 1 | L_008118EDNA4A-008172VICTORIA4AC1 | 138 | 138 | Branch Amp | 920.4134 | - | - | - | - | 123.7784 | 105.3725 | -
TLCRA,TAEPTC | COAST | COAST | COAST, COAST | EL_CAMPO4A ( 8102) -> L_RICEBI8_1Y (78104) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | 138 | Branch Amp | 920.4134 | - | - | - | - | 106.5441 | - | -
TLCRA,TAEPTC | COAST | COAST | COAST, COAST | EL_CAMPO4A ( 8102) -> L_RICEBI8_1Y (78104) CKT 1 | L_042985DYANN__POI_8-043570WHARTN__60B8C&1-MS | 138 | 138 | Branch Amp | 920.4134 | - | - | - | - | 106.5451 | 102.5828 | -
TLCRA,TAEPTC | COAST | COAST | COAST, COAST | EL_CAMPO4A ( 8102) -> L_RICEBI8_1Y (78104) CKT 1 | L_043570WHARTN__60B8-044150HNGFRD_POI_8C&1-MS | 138 | 138 | Branch Amp | 920.4134 | - | - | - | - | 104.4087 | 100.6669 | -
TLCRA,TAEPTC | COAST | COAST | COAST, COAST | EL_CAMPO4A ( 8102) -> L_RICEBI8_1Y (78104) CKT 1 | L_044150HNGFRD_POI_8-044190E_BERN__B138C60 | 138 | 138 | Branch Amp | 920.4134 | 105.8389 | - | - | - | 110.5273 | 108.8196 | -
TLCRA,TAEPTC | COAST | COAST | COAST, COAST | EL_CAMPO4A ( 8102) -> L_RICEBI8_1Y (78104) CKT 1 | L10005-2B | 138 | 138 | Branch Amp | 920.4134 | - | - | - | - | 100.434 | - | -
TLCRA,TAEPTC | COAST | COAST | COAST, COAST | EL_CAMPO4A ( 8102) -> L_RICEBI8_1Y (78104) CKT 1 | L10010005-1A | 138 | 138 | Branch Amp | 920.4134 | - | - | - | - | 101.0477 | - | -
TLCRA,TAEPTC | COAST | COAST | COAST, COAST | EL_CAMPO4A ( 8102) -> L_RICEBI8_1Y (78104) CKT 1 | M100052100072 | 138 | 138 | Branch Amp | 920.4134 | - | - | - | - | 128.3688 | 107.7949 | -
TLCRA,TAEPTC | COAST | COAST | COAST, COAST | EL_CAMPO4A ( 8102) -> L_RICEBI8_1Y (78104) CKT 1 | MB1000710005-2 | 138 | 138 | Branch Amp | 920.4134 | - | - | - | - | 105.0171 | - | -
TLCRA,TAEPTC | COAST | COAST | COAST, COAST | EL_CAMPO4A ( 8102) -> L_RICEBI8_1Y (78104) CKT 1 | P7-1_E1>>T6060D | 138 | 138 | Branch Amp | 920.4134 | - | - | - | - | 106.4046 | 102.5506 | -
TSTEC | SOUTH_CE | COAST | SOUTH_CE, COAST | ELCAMPOSUB9 ( 5538) -> NADASUB9 ( 5536) CKT 1 | L_078103L_NADA8_1Y-078104L_RICEBI8_1YC1 | 69 | 69 | Branch Amp | 376.5327 | 112.5741 | - | 104.9813 | 101.0551 | 110.5449 | 115.0056 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | ELKTON_5 ( 3105) -> ERIKA_POI (888878) CKT 1 | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3707 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | ELKTON_5 ( 3105) -> ERIKA_POI (888878) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 109.3702 | 130.2343 | 115.2326 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | ELKTON_5 ( 3105) -> KNGSCRK1_5 (15202) CKT 1 | ERIKA_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 112.7662 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | ELKTON_5 ( 3105) -> KNGSCRK1_5 (15202) CKT 1 | L_002432TRICRN1_5-888878ERIKA_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.2984 | 118.0308 | 105.0344 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | ELKTON_5 ( 3105) -> KNGSCRK1_5 (15202) CKT 1 | L_888878ERIKA_POI-003105ELKTON_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 111.2888 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | ELKTON_5 ( 3105) -> KNGSCRK1_5 (15202) CKT 1 | TRICORNER - TYLER GRANDE (single B TO B) new_load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.8996 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | ELKTON_5 ( 3105) -> KNGSCRK1_5 (15202) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 127.6103 | 148.0138 | 132.6812 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | ELKTON_5 ( 3105) -> KNGSCRK1_5 (15202) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 120.385 | 140.2927 | 125.8012 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | ELKTON_5 ( 3105) -> KNGSCRK1_5 (15202) CKT 1 | TRIN-SK*ME (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.8954 | 116.7568 | 102.8868 | -
TONCOR | EAST | EAST | EAST, EAST | ELKTON_8 ( 3106) -> ELKTOSTR (500101) CKT 1 | DRY_CREEK_CON | 138 | 1 | Branch MVA | 528 | - | - | - | 111.2888 | 136.7842 | 113.6618 | -
TONCOR | EAST | EAST | EAST, EAST | ELKTON_8 ( 3106) -> ELKTOSTR (500101) CKT 1 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 138 | 1 | Branch MVA | 528 | - | - | - | - | 125.4877 | 109.7802 | -
TONCOR | EAST | EAST | EAST, EAST | ELKTON_8 ( 3106) -> ELKTOSTR (500101) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 138 | 1 | Branch MVA | 528 | - | - | - | 115.0278 | 139.1779 | 120.3131 | -
TONCOR | EAST | EAST | EAST, EAST | ELKTON_8 ( 3106) -> ELKTOSTR (500101) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 1 | Branch MVA | 528 | - | - | - | 104.0921 | 122.492 | 104.9169 | -
TONCOR | EAST | EAST | EAST, EAST | ELKTON_8 ( 3106) -> ELKTOSTR (500101) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 1 | Branch MVA | 528 | - | - | - | 108.5301 | - | 121.1235 | -
TONCOR | EAST | EAST | EAST, EAST | ELKTON_8 ( 3106) -> ELKTOSTR (500101) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 1 | Branch MVA | 528 | - | - | - | 155.9487 | 182.269 | 172.7118 | -
TONCOR | EAST | EAST | EAST, EAST | ELKTON_8 ( 3106) -> ELKTOSTR (500101) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 1 | Branch MVA | 528 | - | - | - | 149.7932 | 177.9034 | 161.6318 | -
TONCOR | EAST | EAST | EAST, EAST | ELKTON_8 ( 3106) -> ELKTOSTR (500101) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 1 | Branch MVA | 528 | - | - | 101.1005 | 160.1002 | 186.2299 | 177.0425 | -
TONCOR | EAST | EAST | EAST, EAST | ELKTOSTR (500101) -> ELKTON_5 ( 3105) CKT 1 | DRY_CREEK_CON | 345 | 1 | Branch MVA | 528 | - | - | - | 115.9293 | 143.5281 | 118.1132 | -
TONCOR | EAST | EAST | EAST, EAST | ELKTOSTR (500101) -> ELKTON_5 ( 3105) CKT 1 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 345 | 1 | Branch MVA | 528 | - | - | - | 101.6316 | 130.7313 | 114.4514 | -
TONCOR | EAST | EAST | EAST, EAST | ELKTOSTR (500101) -> ELKTON_5 ( 3105) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | 1 | Branch MVA | 528 | - | - | - | 120.0348 | 146.0579 | 125.7738 | -
TONCOR | EAST | EAST | EAST, EAST | ELKTOSTR (500101) -> ELKTON_5 ( 3105) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 1 | Branch MVA | 528 | - | - | - | 109.9215 | 129.5622 | 110.4714 | -
TONCOR | EAST | EAST | EAST, EAST | ELKTOSTR (500101) -> ELKTON_5 ( 3105) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 345 | 1 | Branch MVA | 528 | - | - | - | 114.148 | - | 128.7388 | -
TONCOR | EAST | EAST | EAST, EAST | ELKTOSTR (500101) -> ELKTON_5 ( 3105) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 1 | Branch MVA | 528 | - | - | 100.309 | 164.4308 | 192.3874 | 184.5274 | -
TONCOR | EAST | EAST | EAST, EAST | ELKTOSTR (500101) -> ELKTON_5 ( 3105) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 1 | Branch MVA | 528 | - | - | - | 158.1599 | 188.73 | 171.4998 | -
TONCOR | EAST | EAST | EAST, EAST | ELKTOSTR (500101) -> ELKTON_5 ( 3105) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 1 | Branch MVA | 528 | - | - | 104.6301 | 168.7448 | 196.2766 | 189.2035 | -
TCNPE | COAST | COAST | COAST, COAST | ELMATO_POI_5 (43990) -> SO_TEX__345A ( 5915) CKT 64 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 345 | 345 | Branch Amp | 2426.5444 | - | - | - | - | 102.4776 | - | -
TCNPE | COAST | COAST | COAST, COAST | ELMATO_POI_5 (43990) -> SO_TEX__345A ( 5915) CKT 64 | L_005915SO_TEX__345A-044200HILLJE__B345C1 | 345 | 345 | Branch Amp | 2426.5444 | - | - | - | - | 101.2879 | - | -
TCNPE | COAST | COAST | COAST, COAST | ELMATO_POI_5 (43990) -> SO_TEX__345A ( 5915) CKT 64 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 345 | 345 | Branch Amp | 2426.5444 | - | - | - | - | 108.6286 | - | -
TCNPE | COAST | COAST | COAST, COAST | ELMATO_POI_5 (43990) -> SO_TEX__345A ( 5915) CKT 64 | P7-1_E1>>T1827D | 345 | 345 | Branch Amp | 2426.5444 | - | - | - | - | 101.0366 | - | -
TCPSE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | ELMCREEK ( 5133) -> SKYLINE_5 ( 5371) CKT 1 | E5T5A1C1_B | 345 | 345 | Branch Amp | 1733.724 | - | - | - | - | 114.3235 | - | -
TCPSE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | ELMCREEK ( 5133) -> SKYLINE_5 ( 5371) CKT 1 | L_005133ELMCREEK-005371SKYLINE_5C2 | 345 | 345 | Branch Amp | 1733.724 | - | - | - | - | 100.2674 | - | -
TCPSE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | ELMCREEK ( 5133) -> SKYLINE_5 ( 5371) CKT 2 | E5T5A1C1_B | 345 | 345 | Branch Amp | 1837.4797 | - | - | - | - | 107.8681 | - | -
TCPSE , RBECR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | ELMCREEK (5133) -> SHAULA (5380) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1715.3158 | - | - | - | - | 115.4249 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.2675 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1086 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8506 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1133 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9085 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2216 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9767 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3549 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0838 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2356 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9803 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3599 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0875 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0824 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7905 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0797 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7919 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | BAS_RANCH_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0482 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 105.0998 | - | 106.2405 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.2651 | - | 104.9432 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.3977 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | BEPC_015_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.7042 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | BEPC_301_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.194 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | BEPC_304_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.26 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 132.8102 | - | 122.4018 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | BLUBIRD_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.3394 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.3801 | - | 103.5451 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | CARTWHEEL_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1105 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | CEDAR HILL - DESOTO/LOOP NINE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.1563 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 114.1025 | - | 101.5985 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 113.6581 | - | 101.4749 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | CLEAR CROSSING - COODY CROSSING/THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1925 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | CLY_PHNT1P7F1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0863 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | COODY CROSSING - TECUMSEH AND CLEAR CROSSING - THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4138 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | DES_WILL_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.0411 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | DRY_CREEK_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.0562 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.5481 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E_ETCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.1337 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E_FRNYPP_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.4191 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E_FRNYPP_CC2_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.4251 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E_JACKCNTY_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8754 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E_JCKCNTY2_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8959 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E_KMCHI_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.6414 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E_KMCHI_CC2_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.6594 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E_LPCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3383 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E_LPCCS_CC2_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.1211 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E_PANDA_S_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.3119 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E_TGCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8477 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E_TNSKA_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0403 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E_WCPP_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5122 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E_WHCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.1671 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E_WHCCS2_CC2_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.4001 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E5DVA1C1_1_B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9899 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E5DVA1C1_1_B_1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6907 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | E5DVA1C1_1_B_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4286 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | EAST LEVEE - NORWOOD 138 KV & NORWOOD - WEST LEVEE 345 KV DCKT A LUPO | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.9085 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7509 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6284 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ENNIS - PEBBLE CREEK 138 KV SWITCH (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3451 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ERIKA_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.614 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5289 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | FORNEY - SEAGOVILLE SW/TRI CORNER DCKT 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4031 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_000575JCKCNTY5UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0815 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_000579JCKCNTY8UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2063 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_003321REDLAND_5UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1488 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_006100OKLA7AUC0 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5707 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_120041MLSES_UNIT1UL1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9549 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_120042MLSES_UNIT2UL2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0054 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_120043MLSES_UNIT3UL3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0262 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_150023MCSES_UNIT8UN8 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.9497 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_150051HLSES_UNIT3UN3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5588 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_150052HLSES_UNIT4UN4 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0127 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_150053HLSES_UNIT5UN5 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7677 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_150091LHSES_UNIT1UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5797 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_150092LH2SES_UNIT2UN2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.3221 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_150111CPSES_UNIT1UU1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.5397 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_150112CPSES_UNIT2UU2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.6025 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_153911PNGT1_PV_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4942 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_5920EASTDCTIE | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.6323 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_888839BAS_RANCH_POIUC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0553 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_888854PINEFOREST_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1758 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | G_888879BLUBIRD_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4971 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | GLASGOW_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 129.1756 | - | 118.9239 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | HICKS - EAGLE MTN*PARKER 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5038 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | HICKS -ALLIANCE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0994 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | JEW- LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2272 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9807 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9844 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | KRUM WEST - RILEY A 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4245 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | KRUMW-WEST DENT/DUNHAM 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3005 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8522 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8739 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_000221TRUMBULL8-002229PEBBLCRK_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2931 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_000221TRUMBULL8-012344GAMMA_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3181 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_000646LEWISVLSW5_1-021851DUNHAM_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2371 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001421WILLOWCK_5-031875RAMHORNH_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.016 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001421WILLOWCK_5-031875RAMHORNH_5C2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.016 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001436PARKER_5-002081HICKS_SW1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0302 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.8855 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001730W_KRUM_5-152087NOBLESLR_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0514 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.3122 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001880ROCKYCRK_5-888879BLUBIRD_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3302 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001895MITCHBND2_5-002285CARMICHL_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0029 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 105.5481 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.075 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.2544 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.3911 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001906VENUS_S5-015201FORBESR2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.1991 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001906VENUS_S5-888857OYSTER_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 108.2681 | - | 103.4514 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001906VENUS_S5-888880DES_WILL_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.747 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3851 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.1862 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001907VENUS_N5-011902BRITTNRD2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0338 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001907VENUS_N5-015200FORBESR1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3179 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001907VENUS_N5-068091NAVARROC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 107.4468 | - | 103.478 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001911WEBB1_5-011902BRITTNRD2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0122 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001921LIGGETTA1_5-002632MILLERRD_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.9702 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001928LIGGETT_3T5-002406NORWD1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.5332 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.7211 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.335 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 132.8102 | - | 122.4018 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002263GELLER_8-003079SSWWT2T_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4478 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002263GELLER_8-003083WILMER1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4129 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6967 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6557 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002406NORWD1_5-012398TOPEKA1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.746 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002420CHILSW1_5-002431DESSW1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.1021 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002420CHILSW1_5-002847LOOP9_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6733 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 105.779 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 105.779 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 110.3284 | - | 102.4363 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 109.1807 | - | 101.6015 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002432TRICRN1_5-888878ERIKA_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.1091 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002434SGVLSW1_8-003076SGVL1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6692 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.4191 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.4251 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 130.6183 | - | 120.5817 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_002478ROYSE_S5-002485POETRY_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0616 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003076SGVL1_8-003077KLEBRG1T_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5727 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003077KLEBRG1T_8-003079SSWWT2T_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4794 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003100MARTINLK_5-003102TYLERGND_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9164 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.0508 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 105.7374 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 108.1147 | - | 101.6953 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003127TRINIDAD_8-003260NIPAKTAP_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0916 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003133RICHLND2_5-003381BIGBRNW_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7718 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003134RICHLND1_5-003380BIGBRNE_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.411 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003260NIPAKTAP_8-003265MANKIN_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0899 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003262CEDRCREK_8-003263CEDRCKPU_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0556 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003262CEDRCREK_8-003287WILL_WHT_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.038 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003263CEDRCKPU_8-003265MANKIN_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0709 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003264SEVENPTS_8-003287WILL_WHT_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0126 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.4989 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003374FILESVALY_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4561 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003377LITTLEPOND_5-003687BELL_E_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5083 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003377LITTLEPOND_5-003704HOGCREEK_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0854 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003384STJOHNS_5-003409LAKE_CRK1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3436 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003384STJOHNS_5-003711BALE_S5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7424 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003388FOURBTHRS_5-003405THOUSE__5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0041 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003388FOURBTHRS_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1821 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9174 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003687BELL_E_5-003705BRANGUS_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6557 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_003705BRANGUS_5-003706GIBSON_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2691 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.359 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_011688THORNTRE_5-143625SAMSON_1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.1252 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_011688THORNTRE_5-143705DELILA_1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0136 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_012329SHANKLSW_8-012344GAMMA_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3168 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_013401TIGERCK_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0526 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.9977 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.0019 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_021851DUNHAM_5-033646LEWISVLSW5_2C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1902 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_068011ASPIRE-068051REATAC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1537 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_081003HABER7A-081005ACME7AC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0183 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_143705DELILA_1_5-143757DELILA_2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0856 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.8731 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_888857OYSTER_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.2411 | - | 101.5192 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 126.8835 | - | 117.3588 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_888878ERIKA_POI-003105ELKTON_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.482 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | L_888880DES_WILL_POI-001916LIGGETTA2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.8901 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | LAKE CREEK - LAKE HALL/TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4322 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | LAKE CREEK-RATTLESNAKE/ST JOHNS_5 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3436 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | LAKE CREEK-ST JOHNS_5 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3436 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | LATIMER_REATA_P7F1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4592 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0011 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.1371 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3767 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5159 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.0487 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.8976 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.8577 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | Liggett SW - MillerRoad 345 KV (SINGLE B TO B) New Load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.9702 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT-NORWOOD 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.7778 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.3308 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.1517 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.346 | - | 101.8954 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | LOOP NINE-DESOTO/CEDAR HILL 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9806 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 105.556 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.2352 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | MB210140210145-AAAAA | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1694 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | MB210140210145-AAAAB | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2812 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | MB210140210145-AABA | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0476 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | MB210160210165 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.178 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | MB255152551420840 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1697 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.2778 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5874 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.3298 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4656 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.7812 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0661 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.803 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | NORTHWEST CARROLLTON - LEWISVILLE SW (BEPC) 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8746 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | NORWOOD - LIGGETT/CEDAR HILL DCKT 345 KV (DOUBLE B TO B) NEW_LOAD | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4564 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | NORWOOD - WEST LEVEE 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.8736 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | NORWOOD-LIGGETT 345 & MOUNTAIN CREEK - LIGGETT 138 KV DCKT A BLUBONT | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.1737 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | OYSTER_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 107.069 | - | 102.0311 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T1827GX_ERC | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2789 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | P7-1_E1>>T4848K | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1892 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5446 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV DCKT & EAGLE MOUNTAIN - WEATHERFORD 138 KV LINE | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4189 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | PINEFOREST_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0431 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | RAMHORN - DUNHAM DC 345 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0549 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (COMMON TOWER) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5184 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | RAMHORN - WILLOW CREEK DC 345 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.6953 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | RICH-BBROWN (DOUBLE B TO B)A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 107.619 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4159 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.5846 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.2862 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 107.2517 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | SCUR_CLY_P7 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1792 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | SHERRY-TIMBERVIEW*VENUS 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2278 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8368 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0856 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.2852 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TIMBERVIEW-COMANCHE PEAK*CARMICHAEL BEND 345 KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6093 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TIMBERVIEW-COMANCHE PEAK*DECORDOVA 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4013 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.9054 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5125 | - | 100.5533 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.0881 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.1997 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.6836 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.9215 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 116.0161 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TRINIDAD - MANKIN (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0898 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TRIN-MANKIN*EUSTACE SOUTHEAST(DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1283 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 118.1328 | - | 110.0439 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.8962 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.6803 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 123.8108 | - | 113.4325 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5175 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5328 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6464 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 107.111 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 107.3766 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS - WEBB 345KV (SINGLE B TO B) BRITTONRD2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0006 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 108.315 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | Venus SW - MillerRoad 345 KV (SINGLE B TO B) New Load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.1862 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 120.986 | - | 118.9454 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 116.6051 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.5379 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 105.387 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 105.7085 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-FORT SMITH SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.2652 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.2827 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0784 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0667 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.2022 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.7156 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5238 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-NAVARRO 345 KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 118.4596 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VENUS-SAM SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3611 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | VIKING_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4701 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 131.6245 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.3731 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 107.0163 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | WILLOW CREEK - CLEAR CROSSING (THOMAS PRICE) & COODY CROSSING - TECUMSEH 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV SUM 2026 - FUTURE (TRIPLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2099 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | WILLOW CREEK - HENDERSON RANCH 345 KV & WILLOW CREEK - JACKSBORO 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0048 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | WILLOW CREEK - TECUMSEH/THOMAS PRICE 345 KV DCKT WIN 2023 - FUTURE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5524 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | WILLOW CREEK - THOMAS PRICE\TECUMSEH CREEK 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV WIN 2023 - FUTURE (TRIPLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4782 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5126 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4333 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | WSHACK_LATIMER_P7 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.846 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-ENNSTRAC_8-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3304 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-HANDLEYC_8-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5588 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-HANDLEYC_8-3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7677 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-HANDLEYD_8-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0127 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-LKHB_1T8-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5797 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-LKHB_2T8-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.3221 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MARTINLK_5-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9549 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MARTINLK_5-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0054 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MARTINLK_5-3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0262 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-MTCK_8T8-8 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.9497 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-WHCCS2_5-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.2842 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 ( 3159) -> BATCHLRD_8 ( 2217) CKT 1 | XFMR-WLFHMDPT_5-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4336 | - | - | -
TLSTR , TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ELROD_5 (3159) -> NAVARRO (68091) CKT 1 | Pre-contingency | 345 | 345 | Amps | 2729.4439 | - | - | - | - | 108.79 | - | -
TONCOR | WEST | WEST | WEST, WEST | ENISCKTA_8 ( 1313) -> BRAND_8 ( 1315) CKT 1 | SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 1 & SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 108.8675 | - | -
TONCOR | WEST | WEST | WEST, WEST | ENISCKTA_8 ( 1313) -> BRAND_8 ( 1315) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 115.3757 | 102.2255 | -
TONCOR | EAST | EAST | EAST, EAST | ENLOE_T8 (11806) -> DELTA1_8 ( 1802) CKT 4 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.4568 | - | -
TBTU | EAST | EAST | EAST, EAST | ENTERPRISE (32790) -> BRYN_TAMU_B (32799) CKT 1 | L_032780BRYN_RELLIS-032852BRYN_STEELE_C1 | 138 | 138 | Branch Amp | 912.046 | - | - | - | - | 111.061 | 109.8656 | -
TBTU | EAST | EAST | EAST, EAST | ENTERPRISE (32790) -> BRYN_TAMU_B (32799) CKT 1 | L_032852BRYN_STEELE_-032857BRYN_SNOO138C1 | 138 | 138 | Branch Amp | 912.046 | - | - | - | - | 114.6026 | 113.2737 | -
TBTU | EAST | EAST | EAST, EAST | ENTERPRISE (32790) -> BRYN_TAMU_B (32799) CKT 1 | L_032860BRYN_KOPPE-032895BRYN_WBRN138C1 | 138 | 138 | Branch Amp | 912.046 | - | - | - | - | 101.743 | 100.5106 | -
TBTU | EAST | EAST | EAST, EAST | ENTERPRISE (32790) -> BRYN_TAMU_B (32799) CKT 1 | L_032878BRYN_GRNPRAI-032895BRYN_WBRN138C1 | 138 | 138 | Branch Amp | 912.046 | - | - | - | - | 106.7709 | 105.5141 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ERIKA_POI (888878) -> TRICRN1_5 ( 2432) CKT 1 | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.1262 | 116.7104 | 102.5261 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ERIKA_POI (888878) -> TRICRN1_5 ( 2432) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 125.5063 | 146.9358 | 129.1632 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ERIKA_POI (888878) -> TRICRN1_5 ( 2432) CKT 1 | TRIN-SK*ME (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 110.2471 | - | -
TSTEC,TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | ERIOHONDOSB8 ( 5764) -> RIOHONDO4A ( 8319) CKT 1 | L_005761PAREDESSW8-005766CNTRLAVESUB8C1 | 138 | 138 | Branch Amp | 719.5959 | - | - | 100.2627 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ESIDE2T_8 ( 2771) -> MSQT1_8 ( 2775) CKT 1 | 3WT_002433SGVLSW1_5_002434SGVLSW1_8_012434SGVLSW1_3 C 2 | 138 | 138 | Branch Amp | 1499.8555 | - | - | - | 107.1585 | 115.3107 | 102.6162 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ESIDE2T_8 ( 2771) -> MSQT1_8 ( 2775) CKT 1 | SEAGOVILLE SW - FORNEY/TRICORNER DCKT 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1499.8555 | - | - | - | 108.3026 | 116.2365 | 102.4821 | -
REXMOR | COAST | COAST | COAST, COAST | EXN_2_9 (110378) -> EXN_1_9 (110377) CKT SG | L_110377EXN_1_9-110378EXN_2_9CSH | 69 | 69 | Branch Amp | 1547.968 | - | 106.1037 | - | - | - | - | -
TONCOR | WEST | WEST | WEST, WEST | EXSHARNR_8 ( 1300) -> BLUFCKTA_8 ( 1309) CKT 1 | DERMOTT - BLUFF CREEK SW & DERMOTT - ENNIS CREEK 138 KV (DOUBLE B TO B) 2023 WIN - FUTURE | 138 | 138 | Branch Amp | 748.8818 | 111.7176 | 102.3238 | 116.2235 | 118.4624 | 136.7868 | 137.3542 | -
TONCOR | WEST | WEST | WEST, WEST | EXSHARNR_8 ( 1300) -> BLUFCKTA_8 ( 1309) CKT 1 | DERMOTT - BLUFF CREEK SW & ENNIS CREEK - GOLDEN SW 138 KV (DOUBLE B TO B) 2023 WIN - FUTURE | 138 | 138 | Branch Amp | 748.8818 | 100.6741 | - | 105.0807 | 107.9883 | 124.24 | 124.9557 | -
TONCOR | WEST | WEST | WEST, WEST | EXSHARNR_8 ( 1300) -> BLUFCKTA_8 ( 1309) CKT 1 | DERMOTT - BLUFF CREEK SW 138 KV (SINGLE B TO B) 2023 SUM - FUTURE | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 108.0514 | 110.4888 | -
TONCOR | WEST | WEST | WEST, WEST | EXSHARNR_8 ( 1300) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001309BLUFCKTA_8-001310KNAPP_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 108.1501 | 110.5777 | -
TONCOR | WEST | WEST | WEST, WEST | EXSHARNR_8 ( 1300) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001310KNAPP_8-001366ONC900041_TAPC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 100.6223 | 110.5352 | 112.8039 | -
TONCOR | WEST | WEST | WEST, WEST | EXSHARNR_8 ( 1300) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001312SCURYCHV_8-011130KNDRSACRC_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.9175 | 104.7347 | 114.5761 | 116.8689 | -
TONCOR | WEST | WEST | WEST, WEST | EXSHARNR_8 ( 1300) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001312SCURYCHV_8-011306DERMOTT_8C1 | 138 | 138 | Branch Amp | 748.8818 | 100.3319 | - | 103.8044 | 106.5803 | 116.4665 | 118.7883 | -
TONCOR | WEST | WEST | WEST, WEST | EXSHARNR_8 ( 1300) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001366ONC900041_TAP-011130KNDRSACRC_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 101.5754 | 111.4728 | 113.7346 | -
TONCOR | WEST | WEST | WEST, WEST | EXSHARNR_8 ( 1300) -> BLUFCKTA_8 ( 1309) CKT 1 | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | - | 105.1014 | -
TONCOR | WEST | WEST | WEST, WEST | EXSHARNR_8 ( 1300) -> BLUFCKTA_8 ( 1309) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 106.1421 | 109.8669 | -
TONCOR | WEST | WEST | WEST, WEST | EXSHARNR_8 ( 1300) -> BLUFCKTA_8 ( 1309) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 748.8818 | - | 121.71 | - | - | - | - | -
TONCOR | EAST | EAST | EAST, EAST | FAIRFIELD ( 196) -> FAIRWPOD_8 ( 3503) CKT 1 | L_003394JEWETTA_8-003501SEATEAG_T_8C1 | 138 | 138 | Branch Amp | 351.4305 | 114.9553 | - | 115.7261 | 117.3659 | 118.7387 | 118.0369 | -
TONCOR | EAST | EAST | EAST, EAST | FAIRFIELD ( 196) -> FAIRWPOD_8 ( 3503) CKT 1 | L_003495BLAIN_8-003501SEATEAG_T_8C1 | 138 | 138 | Branch Amp | 351.4305 | - | - | 100.1806 | 101.6096 | 102.7767 | 102.1894 | -
TONCOR | EAST | EAST | EAST, EAST | FAIRWPOD_8 ( 3503) -> FAIRFIELD ( 196) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 138 | 138 | Branch Amp | 351.4305 | - | - | - | - | 122.1755 | - | -
TSTEC,TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | FANNINSUB9 ( 5736) -> GOLIAD2A ( 8587) CKT 1 | E5DVA1C1_1_B | 69 | 69 | Branch Amp | 317.961 | - | - | 102.1779 | - | - | - | -
TSTEC,TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | FANNINSUB9 ( 5736) -> GOLIAD2A ( 8587) CKT 1 | L_005725PAWNEESW5-008164COLETO7AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.9493 | - | - | - | -
TSTEC,TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | FANNINSUB9 ( 5736) -> GOLIAD2A ( 8587) CKT 1 | L_008403THRRVRS4A-008404SIGMOR4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.0713 | - | - | - | -
TSTEC,TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | FANNINSUB9 ( 5736) -> GOLIAD2A ( 8587) CKT 1 | L10010060-1A-1 | 69 | 69 | Branch Amp | 317.961 | - | - | 100.6099 | - | - | - | -
TSTEC , TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | FANNINSUB9 (5736) -> GOLIAD2A (8587) CKT 1 | Pre-contingency | 69 | 69 | Amps | 317.961 | 103.8829 | - | - | 105.986 | 127.4474 | 105.2171 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | 3WT_001690VALLYSES1_5_001691VALLYSES1_8_017017VALLYSES1_3 C 1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6306 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | 3WT_002372COLLINSS1_5_029554COLLINSR1_8_029577COLLIN1_3 C 1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5941 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | 3WT_002372COLLINSS1_5_029555COLLIN3_8_029578COLLINT_3 C 3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6362 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | 3WT_002373ANNASW_5_002374ANNASW_8_012373ANNASW1_3 C 1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.1006 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | 3WT_002373ANNASW_5_002374ANNASW_8_012374ANNASW2_3 C 1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.1151 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW - ANNA SW 138 KV (DOUBLE B TO B) A 23 RIDGEVIEW | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.6694 | 108.5258 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW - ANNA SW CKT 2 138 KV (SINGLE B TO B) A 23 RIDGEVIE | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.3774 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW - ANNA SW/BLOOMDALE SW 138 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.4298 | 108.2904 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW - BLOOMDALE SW 138 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.3868 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW - MONTICELLO 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.1984 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.4219 | 114.1159 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 120.9097 | 133.8892 | 114.638 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 129.2656 | 140.7957 | 120.9705 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 120.4941 | 133.3209 | 114.1636 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 128.677 | 140.1352 | 120.4447 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 127.262 | 141.5374 | 121.4065 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 135.8785 | 149.3025 | 128.4269 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 128.4037 | 142.7408 | 122.3412 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 137.2359 | 150.4781 | 129.4958 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 126.8021 | 140.9026 | 120.862 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 135.3234 | 148.5587 | 127.5563 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 127.9392 | 142.1164 | 121.8382 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 136.6851 | 149.7889 | 128.8626 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN-MOSES 345-138 AUTO-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.8512 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLEN-MOSES 345-138 AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.7757 | 115.045 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 132.048 | 147.6248 | 126.3326 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | 102.3788 | 141.4574 | 156.2355 | 134.1692 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 128.711 | 143.2735 | 122.8106 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 137.7185 | 151.2877 | 130.232 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ANNA 138 KV SW - GREENBRIAR SW 138 KV(SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.1403 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ANNA 138 KV SW - GREENBRIAR SW/WALDRIP SW 138 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.1663 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ANNA 345 KV - KRUM WEST/CEDAR ELM (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.1945 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ANNA SW - ALLEN SW/BLOOMDALE SW 138 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.6152 | 109.5948 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ANNA SW - VALLEY SOUTH 345 KV & ANNA SW - FARMERSVILLE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 110.8734 | 122.4147 | 105.1351 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | BEPC_015_2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.245 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | BEPC_22 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5913 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | BEPC_304_2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.2698 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.9629 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | BIGBRN__5-JEWETT_S5 & BIGBRN__5-JEWETT_N5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.1049 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | BLOOMDALE SW - ANNA SW 138 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.1745 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | CARROLLTON NORTHWEST - RENNER/COLLIN SW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.6993 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | CARROLLTON NW-HACKBERRY-NORWOOD 345KV (SINGLE B TO B) HACKBERRY 345/138 TRANSFORMER | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.1379 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | CARTWHEEL_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 111.2516 | 122.2881 | 104.1111 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | CEDAR HILL - DESOTO/LOOP NINE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.2721 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.1673 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.6743 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2878 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5942 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | COMMERCE SW-PARIS SW/CROSSROAD SW 138 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.415 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | COMMERCE-ROYSE SW 138 KV B (SINGLE B TO B) 23 R985 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.9723 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | DRY_CREEK_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.732 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | DUNHAM - KRUMW/RNK DC 345 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.1164 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3052 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | E_FRNYPP_CC1_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.1588 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | E_FRNYPP_CC2_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.1972 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | E_TGCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2809 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | EAST LEVEE - NORWOOD 138 KV & NORWOOD - WEST LEVEE 345 KV DCKT A LUPO | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.0419 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6539 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ERIKA_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.0777 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | G_120041MLSES_UNIT1UL1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.24 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | G_120042MLSES_UNIT2UL2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2791 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | G_120043MLSES_UNIT3UL3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3183 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | G_150091LHSES_UNIT1UN1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.7344 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | G_150092LH2SES_UNIT2UN2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6583 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | GLASGOW_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.8432 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | KRUM WEST - CEDAR ELM/ANNA 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.4251 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | KRUMW-WEST DENT/DUNHAM 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 108.1806 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_000722JORDAN-001738WHTBORSE_P8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2407 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_000988W_DENT_5-001730W_KRUM_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3385 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001685FARMVLSW_5-002373ANNASW_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.9743 | 111.5788 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001685FARMVLSW_5-002478ROYSE_S5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | 102.8013 | 147.8864 | 160.7979 | 135.66 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001690VALLYSES1_5-002373ANNASW_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.5477 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001695MOSES_5-001697SULSP_SS1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 111.3092 | 122.4966 | 104.3595 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.1984 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.1827 | 114.2685 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001696MOSES1_T5-888854PINEFOREST_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.1984 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001697SULSP_SS1_5-888847CARTWHEEL_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 110.7186 | 121.7845 | 103.7315 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001724WHTBORSE_8-001744GORDVL_T8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3472 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001729VAL_STH_5-002373ANNASW_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.7389 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001730W_KRUM_5-011735CEDARELM_5C2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.584 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001730W_KRUM_5-021851DUNHAM_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.9915 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001744GORDVL_T8-888885GALAC_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4006 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001757ALLA_HUB_P8-012351OUTERLOOP_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5141 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001757ALLA_HUB_P8-012468EPCO_P8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6343 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001816COMM_SW_8-001818SCTBRCH1_9C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3609 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001816COMM_SW_8-001844CROSRDSW_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.0476 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001818SCTBRCH1_9-001824NEYLNDVL1_9C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3023 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001824NEYLNDVL1_9-001827CADMLX_T8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3055 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001827CADMLX_T8-001831CADMHW66_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3045 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001829BURROW_T8-001830ROYSEGN_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5637 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001829BURROW_T8-001837INGLE_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.1013 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001830ROYSEGN_8-002471ROYSE_S_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5638 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001831CADMHW66_8-001837INGLE_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3014 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001839STONCRK_8-011757DORCHEST_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6798 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3383 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5397 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6266 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.0974 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3804 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001978WESTON1_8-002544CHAMBVLE_P8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.7127 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001978WESTON1_8-002546MCKNY2_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.5677 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001979WESTON2_8-002341TRINITYFL_T8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.9801 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_001979WESTON2_8-002625BLOOMDALE_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.9791 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.9629 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6539 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002340MELSSA_P8-002374ANNASW_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.9441 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002340MELSSA_P8-002704ANNASE_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5988 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002341TRINITYFL_T8-002374ANNASW_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.2173 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002350CELINASE1_8-002366WILSNCRK_P8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.171 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002350CELINASE1_8-012351OUTERLOOP_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2913 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002361CRLTN_NW1_5-002372COLLINSS1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.4655 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002361CRLTN_NW1_5-002387HACKBRY1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6061 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002372COLLINSS1_5-002373ANNASW_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 113.7959 | 123.8987 | 106.5215 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002374ANNASW_8-002544CHAMBVLE_P8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.8814 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002406NORWD1_5-012398TOPEKA1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.9687 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.4438 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.3072 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.2284 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.2085 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002461ROYSE_N5-002464CASHSW_T5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 106.6395 | 116.9633 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.7459 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002478ROYSE_S5-002485POETRY_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.1197 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002514ALLENSW2_5-002522PL_TENNY_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.192 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002520ANNAGCEC_T8-002704ANNASE_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.0767 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002529MCKNY1_8-002560MCKNY_TI_T8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.545 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002529MCKNY1_8-002625BLOOMDALE_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.9796 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002530MCKNY_SW1_8-002554MCKNY_S1_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6352 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002530MCKNY_SW1_8-002560MCKNY_TI_T8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.368 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002534CRGRNCH1_8-002554MCKNY_S1_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6352 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002534CRGRNCH1_8-002585CYRUSONE1_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.9573 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002546MCKNY2_8-002561MCKNYWHT_T8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.2562 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002547MCKNY_SW2_8-002557MCKNY_S2_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3717 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002547MCKNY_SW2_8-002561MCKNYWHT_T8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6473 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002548ALLEN_N2_8-002585CYRUSONE1_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6628 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002556CRGRNCH2_8-002557MCKNY_S2_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6906 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_002556CRGRNCH2_8-012585CYRUSONE2_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2064 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5601 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.945 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.4983 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_006823KIOWA_RC-006871LNOK_RCC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2865 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_006823KIOWA_RC-006884QUINL_RCC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.1609 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_011757DORCHEST_8-012468EPCO_P8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.646 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_029554COLLINSR1_8-030392COLLINSR2_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5941 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_029555COLLIN3_8-030393COLLIN2SR_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6362 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4321 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_888847CARTWHEEL_POI-002464CASHSW_T5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 111.7422 | 122.7961 | 104.6551 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_888848BARRETT_POI-006871LNOK_RCC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3472 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.1827 | 114.2685 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.0871 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.5174 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5442 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.0411 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | MOSES-SULPHUR SPRINGS SW 345-138 KV AUTO SULPHUR SPRINGS SW 345-138 KV AUTO #1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 113.7055 | 125.4174 | 106.9137 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.7946 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | NORTHWEST CARROLLTON - RENNER 345 KV & PLANO TENNYSON - ALLEN SW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.4069 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | NORWOOD - WEST LEVEE 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.0142 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | OUTERLOOP - COLLIN 138 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.8788 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.1674 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | PARIS-COMMERCE/CROSSROAD (DOUBLE B TO B) MALLORY | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3264 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | PINEFOREST_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.3333 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | RICH-BBROWN (DOUBLE B TO B)A | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4915 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | ROYSE SW-COMMERCE SW 138 KV (SINGLE B TO B) DUPLICATE | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3193 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | STONE CREEK - OUTERLOOP 138 KV (SINGLE B TO B) A DORCHESTER | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.7111 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.9317 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | TIMBERVIEW-COMANCHE PEAK*CARMICHAEL BEND 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2748 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | TIMBERVIEW-COMANCHE PEAK*DECORDOVA 345 KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5341 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.2497 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.9648 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.2817 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.0959 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6905 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4641 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2393 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2798 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3845 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4581 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | XFMR-LKHB_1T8-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.7344 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | XFMR-LKHB_2T8-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6583 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | XFMR-MARTINLK_5-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.24 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | XFMR-MARTINLK_5-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2791 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_N5 ( 2461) CKT 1 | XFMR-MARTINLK_5-3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3183 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | 3WT_001690VALLYSES1_5_001691VALLYSES1_8_017017VALLYSES1_3 C 1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6742 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | 3WT_002372COLLINSS1_5_029554COLLINSR1_8_029577COLLIN1_3 C 1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6511 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | 3WT_002372COLLINSS1_5_029555COLLIN3_8_029578COLLINT_3 C 3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6932 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | 3WT_002373ANNASW_5_002374ANNASW_8_012373ANNASW1_3 C 1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.1449 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | 3WT_002373ANNASW_5_002374ANNASW_8_012374ANNASW2_3 C 1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.1591 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW - ANNA SW 138 KV (DOUBLE B TO B) A 23 RIDGEVIEW | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.7588 | 108.6298 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW - ANNA SW CKT 2 138 KV (SINGLE B TO B) A 23 RIDGEVIE | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.463 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW - ANNA SW/BLOOMDALE SW 138 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.5179 | 108.393 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW - BLOOMDALE SW 138 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.4712 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW - MONTICELLO 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.3445 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.5671 | 114.2961 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 120.0372 | 132.8947 | 113.6196 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 128.2805 | 139.754 | 119.9216 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 119.6233 | 132.329 | 113.1469 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 127.6797 | 139.0963 | 119.3977 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 126.4103 | 140.561 | 120.3913 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 134.9279 | 148.2735 | 127.3814 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 127.5107 | 141.7281 | 121.2932 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 136.2293 | 149.412 | 128.4169 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 125.9538 | 139.9309 | 119.8503 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 134.3765 | 147.5351 | 126.5156 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 127.0496 | 141.1083 | 120.7934 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 135.6819 | 148.7276 | 127.7878 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN-MOSES 345-138 AUTO-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0099 | 109.9916 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLEN-MOSES 345-138 AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.9187 | 115.2131 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 131.2599 | 146.7277 | 125.3845 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | 101.435 | 140.5837 | 155.2882 | 133.1889 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 127.9919 | 142.4604 | 121.9331 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 136.9177 | 150.4359 | 129.3311 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ANNA 138 KV SW - GREENBRIAR SW 138 KV(SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.1983 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ANNA 138 KV SW - GREENBRIAR SW/WALDRIP SW 138 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2247 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ANNA 345 KV - KRUM WEST/CEDAR ELM (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2598 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ANNA SW - ALLEN SW/BLOOMDALE SW 138 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.6449 | 109.6536 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ANNA SW - VALLEY SOUTH 345 KV & ANNA SW - FARMERSVILLE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 110.8223 | 122.3789 | 104.9135 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | BEPC_015_2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.1332 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | BEPC_22 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6478 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | BEPC_304_2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.2841 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.1002 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | BIGBRN__5-JEWETT_S5 & BIGBRN__5-JEWETT_N5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2057 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | BLOOMDALE SW - ANNA SW 138 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.2198 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | CARROLLTON NORTHWEST - RENNER/COLLIN SW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.7009 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | CARROLLTON NW-HACKBERRY-NORWOOD 345KV (SINGLE B TO B) HACKBERRY 345/138 TRANSFORMER | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2708 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | CARTWHEEL_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 110.4507 | 121.3912 | 103.1516 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | CEDAR HILL - DESOTO/LOOP NINE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.4402 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.3755 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.8735 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3815 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6926 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | COMMERCE SW-PARIS SW/CROSSROAD SW 138 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.4352 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | COMMERCE-ROYSE SW 138 KV B (SINGLE B TO B) 23 R985 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.0456 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | DRY_CREEK_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.8189 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | DUNHAM - KRUMW/RNK DC 345 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.1572 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.1942 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | E_FRNYPP_CC1_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.3749 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | E_FRNYPP_CC2_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.4149 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | E_TGCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3889 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | EAST LEVEE - NORWOOD 138 KV & NORWOOD - WEST LEVEE 345 KV DCKT A LUPO | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.1895 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.7859 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ERIKA_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.1638 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | G_120041MLSES_UNIT1UL1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3518 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | G_120042MLSES_UNIT2UL2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3913 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | G_120043MLSES_UNIT3UL3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4309 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | G_150091LHSES_UNIT1UN1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.8815 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | G_150092LH2SES_UNIT2UN2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.8397 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | GLASGOW_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.9766 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | KRUM WEST - CEDAR ELM/ANNA 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.4873 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | KRUMW-WEST DENT/DUNHAM 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 108.2019 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_000722JORDAN-001738WHTBORSE_P8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3054 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_000988W_DENT_5-001730W_KRUM_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3935 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001685FARMVLSW_5-002373ANNASW_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.9614 | 111.5705 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001685FARMVLSW_5-002461ROYSE_N5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | 102.5516 | 147.7116 | 160.6112 | 135.4308 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001690VALLYSES1_5-002373ANNASW_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.6167 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001695MOSES_5-001697SULSP_SS1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 110.6739 | 121.7783 | 103.5546 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.3445 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.3308 | 114.4446 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001696MOSES1_T5-888854PINEFOREST_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.3445 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001697SULSP_SS1_5-888847CARTWHEEL_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 109.9725 | 120.9326 | 102.8102 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001724WHTBORSE_8-001744GORDVL_T8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4121 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001729VAL_STH_5-002373ANNASW_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.8051 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001730W_KRUM_5-011735CEDARELM_5C2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6442 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001730W_KRUM_5-021851DUNHAM_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.0398 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001744GORDVL_T8-888885GALAC_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4656 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001757ALLA_HUB_P8-012351OUTERLOOP_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5726 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001757ALLA_HUB_P8-012468EPCO_P8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6927 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001816COMM_SW_8-001818SCTBRCH1_9C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.4228 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001816COMM_SW_8-001844CROSRDSW_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.0888 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001818SCTBRCH1_9-001824NEYLNDVL1_9C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3643 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001824NEYLNDVL1_9-001827CADMLX_T8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3675 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001827CADMLX_T8-001831CADMHW66_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3666 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001829BURROW_T8-001830ROYSEGN_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.626 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001829BURROW_T8-001837INGLE_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.1635 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001830ROYSEGN_8-002471ROYSE_S_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6262 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001831CADMHW66_8-001837INGLE_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3635 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001839STONCRK_8-011757DORCHEST_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.7382 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4388 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6424 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.7307 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.2117 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.5011 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001978WESTON1_8-002544CHAMBVLE_P8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.7573 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001978WESTON1_8-002546MCKNY2_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.6128 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001979WESTON2_8-002341TRINITYFL_T8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.0236 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_001979WESTON2_8-002625BLOOMDALE_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.0226 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.1002 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.7859 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002340MELSSA_P8-002374ANNASW_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.9785 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002340MELSSA_P8-002704ANNASE_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6368 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002341TRINITYFL_T8-002374ANNASW_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.26 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002350CELINASE1_8-002366WILSNCRK_P8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.23 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002350CELINASE1_8-012351OUTERLOOP_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3505 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002361CRLTN_NW1_5-002372COLLINSS1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.4908 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002361CRLTN_NW1_5-002387HACKBRY1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.7577 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002372COLLINSS1_5-002373ANNASW_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 113.7151 | 123.8345 | 106.2691 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002374ANNASW_8-002544CHAMBVLE_P8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.9253 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002406NORWD1_5-012398TOPEKA1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.1146 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002429WATMLL_8-003083WILMER1_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.073 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.5916 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.5085 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.4457 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.4249 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002461ROYSE_N5-002464CASHSW_T5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 105.8468 | 116.0683 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.8785 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002478ROYSE_S5-002485POETRY_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6147 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002485POETRY_5-003103SHAMBRGR_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.062 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002514ALLENSW2_5-002522PL_TENNY_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.2784 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002520ANNAGCEC_T8-002704ANNASE_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.1204 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002529MCKNY1_8-002560MCKNY_TI_T8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.5902 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002529MCKNY1_8-002625BLOOMDALE_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.0231 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002530MCKNY_SW1_8-002554MCKNY_S1_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6826 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002530MCKNY_SW1_8-002560MCKNY_TI_T8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.4137 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002534CRGRNCH1_8-002554MCKNY_S1_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6826 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002534CRGRNCH1_8-002585CYRUSONE1_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.0072 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002546MCKNY2_8-002561MCKNYWHT_T8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.3024 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002547MCKNY_SW2_8-002557MCKNY_S2_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.4201 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002547MCKNY_SW2_8-002561MCKNYWHT_T8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6947 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002548ALLEN_N2_8-002585CYRUSONE1_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.7139 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002556CRGRNCH2_8-002557MCKNY_S2_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.7416 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_002556CRGRNCH2_8-012585CYRUSONE2_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2594 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6787 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.0739 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.6231 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_006823KIOWA_RC-006871LNOK_RCC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3264 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_006823KIOWA_RC-006884QUINL_RCC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2025 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_011757DORCHEST_8-012468EPCO_P8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.7044 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_029554COLLINSR1_8-030392COLLINSR2_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6511 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_029555COLLIN3_8-030393COLLIN2SR_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6932 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5103 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_888847CARTWHEEL_POI-002464CASHSW_T5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 110.9424 | 121.9008 | 103.697 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_888848BARRETT_POI-006871LNOK_RCC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3863 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.3308 | 114.4446 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.2031 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.6159 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5949 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.1209 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | MOSES-SULPHUR SPRINGS SW 345-138 KV AUTO SULPHUR SPRINGS SW 345-138 KV AUTO #1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 112.9274 | 124.535 | 105.9669 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.8961 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | NORTHWEST CARROLLTON - RENNER 345 KV & PLANO TENNYSON - ALLEN SW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.4852 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | NORWOOD - WEST LEVEE 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.1604 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | OUTERLOOP - COLLIN 138 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.9603 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2593 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | PARIS-COMMERCE/CROSSROAD (DOUBLE B TO B) MALLORY | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3735 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | PINEFOREST_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.4298 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | RICH-BBROWN (DOUBLE B TO B)A | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6035 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | ROYSE SW-COMMERCE SW 138 KV (SINGLE B TO B) DUPLICATE | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3866 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | SHAMBURGER - POETRY_5(SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.062 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | STONE CREEK - OUTERLOOP 138 KV (SINGLE B TO B) A DORCHESTER | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.7712 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.0476 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | TIMBERVIEW-COMANCHE PEAK*CARMICHAEL BEND 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3673 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | TIMBERVIEW-COMANCHE PEAK*DECORDOVA 345 KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6307 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.3713 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.061 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.0006 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.5001 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.1545 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.7616 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | Valley Switch-Haggerty 138 kV Line (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.0443 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5655 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2917 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3813 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.061 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4833 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5578 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | XFMR-LKHB_1T8-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.8815 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | XFMR-LKHB_2T8-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.8398 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | XFMR-MARTINLK_5-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3518 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | XFMR-MARTINLK_5-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3913 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FARMVLSW_5 ( 1685) -> ROYSE_S5 ( 2478) CKT 1 | XFMR-MARTINLK_5-3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4309 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 118.0429 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 113.5609 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 107.2013 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | BEPC_015_2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.2708 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.333 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | BIGBRN__5-JEWETT_S5 & BIGBRN__5-JEWETT_N5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.2485 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.7077 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | BLUBIRD_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 105.9081 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | COODY CROSSING - TECUMSEH AND CLEAR CROSSING - THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.0106 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | DRY_CREEK_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.3471 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.8779 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | E_FRNYPP_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.5558 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | E_FRNYPP_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.5795 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | E_JACKCNTY_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.0986 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | E_JCKCNTY2_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.2647 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | E_KMCHI_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.8899 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | E_KMCHI_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.9225 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | E_LPCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.3489 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | E_PANDA_S_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.1688 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | E_TGCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.9171 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | E_WCPP_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.5889 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | E_WHCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.9062 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | E_WHCCS2_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 105.0628 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.8354 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_000575JCKCNTY5UN1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.648 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_120041MLSES_UNIT1UL1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.7649 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_120042MLSES_UNIT2UL2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.834 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_120043MLSES_UNIT3UL3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.856 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_150023MCSES_UNIT8UN8 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.8428 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_150052HLSES_UNIT4UN4 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.7907 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_150053HLSES_UNIT5UN5 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.3292 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_150091LHSES_UNIT1UN1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.1957 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_150092LH2SES_UNIT2UN2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.3856 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_150111CPSES_UNIT1UU1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 105.4106 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_150112CPSES_UNIT2UU2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 105.4644 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_150151MDANP_CT1UN1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.094 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_150152MDANP_CT2UN2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.3595 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_150155MDANP_CT5UN5 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.2929 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_150156MDANP_CT6UN6 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.3249 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_152331FILESSLR_S1US1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.8857 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_5920EASTDCTIE | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.8342 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | G_888879BLUBIRD_POIUS1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.951 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | GLASGOW_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.6431 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 106.2121 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 106.7436 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 106.646 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.1692 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_001880ROCKYCRK_5-888879BLUBIRD_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.9001 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 116.3473 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_001906VENUS_S5-888857OYSTER_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 111.5117 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 107.3765 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_001907VENUS_N5-015200FORBESR1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 127.124 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_001921LIGGETTA1_5-002632MILLERRD_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.4193 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.333 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.8354 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.5226 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.5226 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.1901 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.6605 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.5558 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.5796 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.8562 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.0126 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.8827 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.1975 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_003381BIGBRNW_5-003391JEWETT_N5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.6827 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_003386OUTLAW_5-046020LIMEST_POI_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.0982 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_003386OUTLAW_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.421 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_003389FORTSMITH_5-152333FILESSLR_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.2909 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_003404BELFALLS_8-003414TEMP_SS__5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.6416 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 105.5077 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.9719 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | 102.8014 | 135.1407 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_046020LIMEST_POI_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.3572 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_068035HELIX-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.7544 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_081003HABER7A-081005ACME7AC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.0583 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_888857OYSTER_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 108.3018 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_888874VIKING_POI-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.0844 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.0549 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | LATIMER_REATA_P7F1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.1446 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | Liggett SW - MillerRoad 345 KV (SINGLE B TO B) New Load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.4193 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | LIMESTONE - OUTLAW / NAVARRO_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 113.1431 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.9195 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.5743 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 109.4515 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.5287 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 105.8966 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.0818 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.6892 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 116.0598 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | OYSTER_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 112.02 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | PINEFOREST_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.2188 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (COMMON TOWER) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.8256 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | RAMHORN - WILLOW CREEK DC 345 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.1057 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | RICH-BBROWN (DOUBLE B TO B)A | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.1403 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.4018 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | TEMPLE - BELFALLS_5 (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.6416 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | TEMPLE PECAN CREEK/BELFALLS - TRADINGHOUSE/STEAKLEYDAM_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.3626 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | TEMPLE PECAN CREEK/STEAKLEYDAM - TRADINGHOUSE/LAKE CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.4178 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | TIMBERVIEW-COMANCHE PEAK*CARMICHAEL BEND 345 KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.6298 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | TIMBERVIEW-COMANCHE PEAK*DECORDOVA 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.5755 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 106.8947 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.2149 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 112.1647 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | Venus SW - MillerRoad 345 KV (SINGLE B TO B) New Load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 107.3765 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 115.2661 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 119.7334 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | VENUS-NAVARRO 345 KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 111.8754 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | VENUS-SAM SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | 101.6496 | 132.6035 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | VIKING_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.2512 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 114.6661 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | WILLOW CREEK - TECUMSEH/THOMAS PRICE 345 KV DCKT WIN 2023 - FUTURE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.4606 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | WILLOW CREEK - THOMAS PRICE\TECUMSEH CREEK 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV WIN 2023 - FUTURE (TRIPLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.2676 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.5895 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.0047 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | WSHACK_LATIMER_P7 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.1968 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | XFMR-HANDLEYC_8-3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.3292 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | XFMR-HANDLEYD_8-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.7907 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | XFMR-LKHB_1T8-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.1957 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | XFMR-LKHB_2T8-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.3856 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | XFMR-MARTINLK_5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.7649 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | XFMR-MARTINLK_5-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.834 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | XFMR-MARTINLK_5-3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.856 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | XFMR-MDLTHELP_5-5 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.2929 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | XFMR-MDLTHELP_5-6 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.3249 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | XFMR-MDLTHELP_S5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.094 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | XFMR-MDLTHELP_S5-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.3595 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | XFMR-MTCK_8T8-8 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.8428 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | XFMR-WHCCS2_5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.2271 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 ( 3374) -> FORTSMITH_5 ( 3389) CKT 1 | XFMR-WLFHMDPT_5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.0041 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FILESVALY_5 (3374) -> FORTSMITH_5 (3389) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1793.9694 | - | - | - | - | 126.8553 | 104.9285 | -
TCNPE | COAST | COAST | COAST, COAST | FLEWLN__B138 (44230) -> FTBEND_C60_8 (44300) CKT 60 | Pre-contingency | 138 | 138 | Amps | 928.7808 | - | - | - | - | 122.824 | 124.5419 | -
TONCOR | EAST | EAST | EAST, EAST | FLINTSUB_8 ( 3251) -> ELKTON_8 ( 3106) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1004.0873 | - | - | - | - | 107.1918 | - | -
TONCOR | EAST | EAST | EAST, EAST | FLINTSUB_8 ( 3251) -> ELKTON_8 ( 3106) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1004.0873 | - | - | - | 103.0549 | - | 103.3229 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FLOWRGRVE_8 (11362) -> HOWDEN_8 (11149) CKT 1 | BIG SPRING - BUZZARD DRAW 138 KV (SINGLE B TO B) 2021 WIN - FUTURE | 138 | 138 | Branch Amp | 502.0437 | - | - | - | - | 103.839 | 104.5571 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FLOWRGRVE_8 (11362) -> HOWDEN_8 (11149) CKT 1 | L_001322BIGSPRIG_8-001358KNOTT_8C1 | 138 | 138 | Branch Amp | 502.0437 | - | - | - | - | 102.3422 | 103.0794 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FLOWRGRVE_8 (11362) -> HOWDEN_8 (11149) CKT 1 | L_001355BUZZDRAW_8-001358KNOTT_8C1 | 138 | 138 | Branch Amp | 502.0437 | - | - | - | - | 104.7781 | 105.4872 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FLOWRGRVE_8 (11362) -> HOWDEN_8 (11149) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 502.0437 | - | - | - | - | 104.7782 | 102.7243 | -
TONCOR , TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> SAMSW (68090) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1793.9694 | - | - | - | - | 128.6068 | 111.1016 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5733 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5922 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.8154 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5914 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.8035 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.7732 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.0871 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.9074 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.3027 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.7741 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.0756 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.9087 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.2969 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.0954 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.4759 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.1053 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.4562 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLEN-MOSES 345-138 AUTO-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.6325 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.6147 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.0971 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.7532 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.0219 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | BAS_RANCH_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.0759 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 110.4844 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | BEPC_015_2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.9691 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | BEPC_227-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.2907 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | BEPC_227-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.2907 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.3497 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | BIGBRN__5-JEWETT_S5 & BIGBRN__5-JEWETT_N5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.3475 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.0273 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | BLUBIRD_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 109.2645 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | BROWN SS - RUSSELL GAP / BUCKHORN_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.1347 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.6716 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.7645 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | CLEAR CROSSING - COODY CROSSING/THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.2043 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | CLY_PHNT1P7F1-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.6571 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | CLY_PHNT1P7F1-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.2916 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | CLY_PHNT2P7F1-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.2576 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | CLY_PHNT2P7F1-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.8983 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.3472 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 108.443 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | COODY CROSSING - TECUMSEH AND CLEAR CROSSING - THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.078 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | DES_WILL_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.289 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | DRY_CREEK_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.0454 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.3864 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_ETCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.2066 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_FREC_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.8696 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_FRNYPP_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.3086 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_FRNYPP_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.3688 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_JACKCNTY_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.1014 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_JCKCNTY2_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.649 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_KMCHI_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.5612 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_KMCHI_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.5932 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_LPCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.6703 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_LPCCS_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.3298 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_OECCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1154 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_OECCS_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1204 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_PANDA_S_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.7708 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_TEN_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.3172 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_TGCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.1189 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_WCPP_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.2907 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_WHCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.6456 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | E_WHCCS2_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 110.8976 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.0268 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.6033 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.3995 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ERIKA_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.6321 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_000575JCKCNTY5UN1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.869 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_000579JCKCNTY8UN1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.6831 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_001877MITCHBND_5UN1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.4712 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_003321REDLAND_5UN1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.8649 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_006100OKLA7AUC0 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.3346 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_079000GRAYUS1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.6887 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_120041MLSES_UNIT1UL1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.977 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_120042MLSES_UNIT2UL2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.0532 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_120043MLSES_UNIT3UL3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.1197 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_120142SCSES_UNIT2UN2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.3828 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_143961MISAE2_S1US1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1484 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_144211HRNTSLR_S1US1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.2649 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_150023MCSES_UNIT8UN8 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.4128 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_150042GRSES_UNIT2UN2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.9392 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_150051HLSES_UNIT3UN3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.2692 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_150052HLSES_UNIT4UN4 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.2744 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_150053HLSES_UNIT5UN5 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.0186 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_150091LHSES_UNIT1UN1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.5039 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_150092LH2SES_UNIT2UN2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.9814 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_150111CPSES_UNIT1UU1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 111.9378 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_150112CPSES_UNIT2UU2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 112.387 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_150151MDANP_CT1UN1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.06 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_150152MDANP_CT2UN2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1518 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_150153MDANP_CT3UN3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.3186 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_150154MDANP_CT4UN4 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.3144 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_150155MDANP_CT5UN5 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1283 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_150156MDANP_CT6UN6 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1394 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_153911PNGT1_PV_S1US1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.6633 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_5920EASTDCTIE | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.094 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_888839BAS_RANCH_POIUC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.0853 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_888854PINEFOREST_POIUS1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.2526 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_888874VIKING_POIUS1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.7409 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | G_888879BLUBIRD_POIUS1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.4886 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | GLASGOW_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.7247 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | GRAHAM UNIT 2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.9392 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | GreenRD Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.288 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | HIGHNOON_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.4736 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | HUTTO - PFGRLVIL & HUTTO - RDRSE-GILLELAND CREEK (DOUBLE B TO B )B | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.4556 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.6119 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | KRUMW-WEST DENT/DUNHAM 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.6129 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.9612 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.9924 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_000237BLANTON-888875THRESLR_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.0852 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_000240WHITNEY5-000246BOSQUESW5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.9212 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_000436GRANDVIEW-000443SANDFLATSWC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.8256 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_000443SANDFLATSW-000444COVINGTONC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.9789 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_000444COVINGTON-888859HIGHNOON_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.1579 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 109.6077 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.6091 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001730W_KRUM_5-152087NOBLESLR_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.374 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.7899 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001880ROCKYCRK_5-888879BLUBIRD_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.9934 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001885EVRMNTIE1_5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.9927 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001900COMCHPKW_5-001902JHNSONSW_P5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.4959 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001902JHNSONSW_P5-015106LILLIAN1C_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.8825 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.11 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.6999 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.0529 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001906VENUS_S5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.1979 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.0307 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001906VENUS_S5-015201FORBESR2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 112.0373 | 142.7044 | 118.3149 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001906VENUS_S5-888880DES_WILL_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.848 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 108.6645 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001907VENUS_N5-015106LILLIAN1C_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.3569 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001907VENUS_N5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 116.1643 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001930CENTURY3_5-001932KENNDALE1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.4241 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001930CENTURY3_5-001934SHRYAUTO2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.9338 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_001932KENNDALE1_5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.5407 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.3497 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.6033 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002279CLEBRNSW_8-002290CLEBRN_8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.4436 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002285CARMICHL_5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.0691 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002290CLEBRN_8-002291CLEBRN_W_8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.0768 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002291CLEBRN_W_8-037810TNHILL_CO_8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.5091 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5922 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5095 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002372COLLINSS1_5-002373ANNASW_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.3568 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.1814 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.1814 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.9543 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 108.0669 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002432TRICRN1_5-888878ERIKA_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5805 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.3506 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.32 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.6435 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003100MARTINLK_5-003102TYLERGND_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.4187 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.4506 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.8852 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.6527 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003133RICHLND2_5-003199CALFRESTN_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.9068 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003134RICHLND1_5-003380BIGBRNE_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.0404 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.9028 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003306STEKLY_DAM_5-003404BELFALLS_8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.5932 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 115.7753 | 150.6375 | 125.9084 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003374FILESVALY_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 106.6224 | 138.0729 | 114.2426 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003380BIGBRNE_5-003390JEWETT_S5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1321 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.5429 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003381BIGBRNW_5-003391JEWETT_N5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.5306 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003386OUTLAW_5-046020LIMEST_POI_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.7557 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003386OUTLAW_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.4523 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003404BELFALLS_8-003414TEMP_SS__5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.362 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.1002 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 112.7312 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003431SDSES_2_8-013430SAND_TXU_8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.2052 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003518BLUMPUMP1_8-037810TNHILL_CO_8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.6106 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_003522HILLBORO1_8-003546WHITNEY__8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.2896 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.2171 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_011688THORNTRE_5-143625SAMSON_1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.532 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_011688THORNTRE_5-143705DELILA_1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.7855 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 120.0604 | 155.378 | 130.0884 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_046020LIMEST_POI_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.0576 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_059909NOVA_138-059998NOVA8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1956 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_068005SAMREACTR-068051REATAC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5829 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_068006NAVREACTR-068008LATIMERC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.8677 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_068008LATIMER-068051REATAC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.429 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_068035HELIX-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.2587 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_081003HABER7A-081005ACME7AC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.9899 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.3616 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.6091 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_888874VIKING_POI-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5236 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.443 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_888880DES_WILL_POI-001916LIGGETTA2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.0248 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | L_888889MIDPOINT_POI-003518BLUMPUMP1_8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.6381 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | LATIMER_REATA_P7F1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 114.2384 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | LCRA TSC_BAKERS_CEDACA_DC | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.3388 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | LCRA TSC_T510_T738_1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.4114 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.3432 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.7705 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.096 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.2865 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.2705 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.0062 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.4171 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | MB210140210145-AAAAA | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.3139 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | MB210140210145-AAAAB | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.5777 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | MB210140210145-AABA | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.0271 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | MB210140210145-ABAAA | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.649 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | MB210140210145-ABAAB | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.382 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | MB210140210145-ABABB | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.0027 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | MB210140210145-ABBA | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.0746 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | MB2551525514 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.7596 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | MB255152551420840 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.7365 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 111.1283 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.0752 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 109.2656 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNIT 4 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.6903 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.9817 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.7104 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 123.7376 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-1-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.4287 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.4287 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.2665 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | NEW-GRAHAM-PARKER 345 KV-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.0889 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | NEW-HILLSBORO-CLEBURNE_SW_8 (SINGLE B TO B )-1-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.2665 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.6971 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | OYSTER_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.4392 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 120.8685 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | PHNT_WSHACK_P7-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1013 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | PINEFOREST_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.0101 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (COMMON TOWER) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.4548 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | RAMHORN - WILLOW CREEK DC 345 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.8306 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | RICH-BBROWN (DOUBLE B TO B)A | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.3828 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.6776 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | SCUR_CLY_P7 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.9847 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | T_059908NOVA_345-059998NOVA8CT1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1956 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.5141 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | TEMPLE - BELFALLS_5 (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.362 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | TEMPLE PECAN CREEK/BELFALLS - TEMPLE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.8334 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | TEMPLE PECAN CREEK/BELFALLS - TRADINGHOUSE/STEAKLEYDAM_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.979 | 102.3472 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | TEMPLE PECAN CREEK/STEAKLEYDAM - TRADINGHOUSE/LAKE CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.8944 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.104 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | THRESLR_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.0531 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | TIMBERVIEW-COMANCHE PEAK*CARMICHAEL BEND 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.136 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | TIMBERVIEW-COMANCHE PEAK*DECORDOVA 345 KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.8203 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | TIMBERVIEW-VENUS 345 KV DOUBLE-CIRCUIT LINE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.2212 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.9037 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.8975 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.424 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.4543 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 113.3722 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | TRIN-SK*ME (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.0198 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.3844 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.8103 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.841 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.1422 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 121.897 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 120.9849 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 117.4178 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.5401 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | VENUS-FORT SMITH SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 117.5568 | 150.6789 | 127.6288 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | VENUS-JOHNSON 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.4156 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | VENUS-JOHNSON 345KV/DECORDOVA-CLEBURNE 138KV (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.0104 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.9991 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.6716 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.6715 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.9025 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.6267 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.2677 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | VIKING_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.7538 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | Voss Lake - Temple 138 kV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.0218 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.1488 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.0819 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.7935 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.7078 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | WILLOW CREEK - CLEAR CROSSING (THOMAS PRICE) & COODY CROSSING - TECUMSEH 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV SUM 2026 - FUTURE (TRIPLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1493 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | WILLOW CREEK - HENDERSON RANCH 345 KV & WILLOW CREEK - JACKSBORO 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.9068 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | WILLOW CREEK - TECUMSEH/THOMAS PRICE 345 KV DCKT WIN 2023 - FUTURE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.4017 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | WILLOW CREEK - THOMAS PRICE\TECUMSEH CREEK 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV WIN 2023 - FUTURE (TRIPLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.11 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.2914 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.9174 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C2_345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5481 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | WSHACK_LATIMER_L1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.84 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | WSHACK_LATIMER_P7 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 115.5738 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | WSHACK_REATA_L2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5593 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-ENNSTRAC_8-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.6534 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-HANDLEYC_8-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.2692 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-HANDLEYC_8-3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.0185 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-HANDLEYD_8-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.2744 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-LKHB_1T8-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.5039 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-LKHB_2T8-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.9814 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-MARTINLK_5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.977 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-MARTINLK_5-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.0532 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-MARTINLK_5-3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.1197 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-MDLTHELP_5-5 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1283 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-MDLTHELP_5-6 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1394 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-MDLTHELP_N5-3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.3186 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-MDLTHELP_N5-4 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.3144 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-MDLTHELP_S5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.06 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-MDLTHELP_S5-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1518 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-MTCK_8T8-8 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.4128 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-STRYKER_8-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.3828 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-WHCCS2_4-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.6903 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-WHCCS2_5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.1237 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-WLFHMDPT_5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.9172 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR1_5 (15200) -> VENUS_N5 ( 1907) CKT 1 | XFMR-WLFHOSTR-3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5478 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 112.898 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 108.373 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.8953 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | BLUBIRD_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.5701 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | G_150111CPSES_UNIT1UU1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.1486 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | G_150112CPSES_UNIT2UU2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.1943 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.9692 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.5275 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.3723 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 111.3488 | - | 105.6891 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | L_001906VENUS_S5-888857OYSTER_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 106.4864 | - | 106.0743 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.1045 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | L_001907VENUS_N5-015200FORBESR1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 122.7102 | - | 124.7949 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | L_003404BELFALLS_8-003414TEMP_SS__5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.2291 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.241 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 131.0343 | - | 136.9297 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | L_888857OYSTER_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 103.1924 | - | 103.393 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | LATIMER_REATA_P7F1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.5018 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | LIMESTONE - OUTLAW / NAVARRO_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 108.1415 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.1831 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.559 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 111.1296 | - | 105.5517 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | OYSTER_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 107.02 | - | 106.3564 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 103.5936 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | TEMPLE - BELFALLS_5 (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.2291 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | TEMPLE PECAN CREEK/BELFALLS - TEMPLE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 104.2867 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | TEMPLE PECAN CREEK/BELFALLS - TRADINGHOUSE/STEAKLEYDAM_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 111.0245 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | TEMPLE PECAN CREEK/STEAKLEYDAM - TRADINGHOUSE/LAKE CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 106.9748 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.5622 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 106.93 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | Venus SW - MillerRoad 345 KV (SINGLE B TO B) New Load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.1045 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 110.3715 | - | 108.1651 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 105.4546 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 114.8264 | - | 107.021 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | VENUS-NAVARRO 345 KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 106.8939 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | VENUS-SAM SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 128.4077 | - | 134.3933 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 109.3654 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORBESR2_5 (15201) -> VENUS_S5 ( 1906) CKT 1 | WSHACK_LATIMER_P7 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 101.5175 | -
RFORVN | COAST | COAST | COAST, COAST | FORFPC_1_8 (110471) -> FORMOSA4A ( 8126) CKT 3 | E_FORMOSA_CC1_TRAIN | 138 | 138 | Branch Amp | 1486.0492 | - | - | - | - | - | 110.2688 | -
RFORVN | COAST | COAST | COAST, COAST | FORMOSA_1 (110461) -> FORMOSA4A (8126) CKT 5 | Pre-contingency | 12.5 | 138 | MVA | 42 | 236.6938 | - | 236.0692 | 235.5329 | 235.7501 | 235.9107 | -
RFORVN | COAST | COAST | COAST, COAST | FORMOSA_11_9 (110464) -> FORMOSA_10_9 (110463) CKT 1 | E_FORMOSA_CC1_TRAIN | 69 | 69 | Branch Amp | 1330.4158 | - | - | - | - | - | 213.3006 | -
RFORVN | COAST | COAST | COAST, COAST | FORMOSA_13_9 (110466) -> FORMOSA_0_9 (110472) CKT 1 | E_FORMOSA_CC1_TRAIN | 69 | 69 | Branch Amp | 1330.4158 | - | - | - | - | - | 217.5987 | -
RFORVN | COAST | COAST | COAST, COAST | FORMOSA_2 (110462) -> FORMOSTR (500174) CKT X3 | Pre-contingency | 12.5 | 1 | MVA | 25 | - | 208.3275 | - | - | - | - | -
RFORVN | COAST | COAST | COAST, COAST | FORMOSA_2 (110462) -> FORMOSTR (500175) CKT X3 | Pre-contingency | 12.5 | 1 | MVA | 25 | 184.2601 | - | 182.0674 | 180.2296 | 177.9864 | 178.6445 | -
RFORVN | COAST | COAST | COAST, COAST | FORMOSA_3 (110477) -> FORMOSTR (500175) CKT X3 | Pre-contingency | 12.5 | 1 | MVA | 25 | 322.1379 | - | 322.982 | 323.8385 | 325.6079 | 325.729 | -
RFORVN | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> FORMOSA_11_9 (110464) CKT 1 | E_FORMOSA_CC1_TRAIN | 69 | 138 | Branch MVA | 159.6 | - | - | - | - | - | 206.3385 | -
RFORVN | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> FORMOSA_13_9 (110466) CKT 2 | E_FORMOSA_CC1_TRAIN | 69 | 138 | Branch MVA | 159.6 | - | - | - | - | - | 210.4962 | -
RFORVN | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> FORMOSTR (500174) CKT X3 | G_110458FOR_FORMOSG8UP8 | 138 | 1 | Branch MVA | 67 | - | 126.2528 | - | - | - | - | -
TAEPTC | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> JOSLIN4A ( 8140) CKT 1 | L_008125LOLITA4A-008126FORMOSA4AC1 | 138 | 138 | Branch Amp | 903.6786 | 102.9971 | - | - | - | - | 106.7287 | -
TAEPTC | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> JOSLIN4A ( 8140) CKT 1 | L_008125LOLITA4A-008172VICTORIA4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 101.0233 | - | 107.5676 | -
TAEPTC | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> JOSLIN4A ( 8140) CKT 1 | M100052100072 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 107.1654 | - | 113.4522 | -
TAEPTC | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> JOSLIN4A ( 8140) CKT 1 | MB1000510007-2 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 105.3921 | - | - | -
TAEPTC | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> JOSLIN4A ( 8140) CKT 1 | MB1000710005-2 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | - | 111.6781 | -
TAEPTC | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> LOLITA4A ( 8125) CKT 1 | L_008126FORMOSA4A-008140JOSLIN4AC1 | 138 | 138 | Branch Amp | 903.6786 | 102.4573 | - | - | - | 102.7729 | 106.3174 | -
TAEPTC | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> LOLITA4A ( 8125) CKT 1 | L_008140JOSLIN4A-008685COBIA4AC1 | 138 | 138 | Branch Amp | 903.6786 | 111.1024 | - | - | - | - | - | -
TAEPTC | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> LOLITA4A ( 8125) CKT 1 | L_008155SANDCRAB4A-008685COBIA4AC1 | 138 | 138 | Branch Amp | 903.6786 | 109.0575 | - | - | - | - | - | -
TAEPTC | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> LOLITA4A ( 8125) CKT 1 | L_008155SANDCRAB4A-008723CANGREJO4AC1 | 138 | 138 | Branch Amp | 903.6786 | 106.4131 | - | - | - | - | - | -
TAEPTC | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> LOLITA4A ( 8125) CKT 1 | M100101100271-1A | 138 | 138 | Branch Amp | 903.6786 | 108.9166 | - | - | - | - | - | -
TAEPTC | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> LOLITA4A ( 8125) CKT 1 | M100101100271-1B | 138 | 138 | Branch Amp | 903.6786 | 106.7863 | - | - | - | - | - | -
TAEPTC | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> LOLITA4A ( 8125) CKT 1 | M128606128703-1_MODIFIED_BY_MZ | 138 | 138 | Branch Amp | 903.6786 | 111.7421 | - | - | - | - | - | -
TAEPTC | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> LOLITA4A ( 8125) CKT 1 | MB1002710010-1 | 138 | 138 | Branch Amp | 903.6786 | 108.8529 | - | - | - | - | - | -
TAEPTC | COAST | COAST | COAST, COAST | FORMOSA4A ( 8126) -> LOLITA4A ( 8125) CKT 1 | MB1287012860-2_MODIFIED_BY_MZ | 138 | 138 | Branch Amp | 903.6786 | 113.1159 | - | - | - | - | - | -
RFORVN | COAST | COAST | COAST, COAST | FORMOSA4A (8126) -> FORMOSTR (500174) CKT X3 | Pre-contingency | 138 | 1 | MVA | 50 | - | 118.7171 | - | - | - | - | -
RFORVN | COAST | COAST | COAST, COAST | FORMOSA4A (8126) -> FORMOSTR (500175) CKT X3 | Pre-contingency | 138 | 1 | MVA | 50 | 110.91 | - | 111.1119 | 111.6009 | 111.5 | 112.1875 | -
TAEPTC | COAST | COAST | COAST, COAST | FORMOSA4A (8126) -> JOSLIN4A (8140) CKT 1 | Pre-contingency | 138 | 138 | Amps | 903.6786 | - | - | - | - | 103.81 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORNEYS_8 (12715) -> CRANDALL1_8 ( 2727) CKT 1 | 3WT_002433SGVLSW1_5_002434SGVLSW1_8_012434SGVLSW1_3 C 2 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 106.1286 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORNEYS_8 (12715) -> CRANDALL1_8 ( 2727) CKT 1 | L_002723ROSEHILL1_8-002731TERRL_S1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 103.2312 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORNEYS_8 (12715) -> CRANDALL1_8 ( 2727) CKT 1 | SEAGOVILLE SW - FORNEY/TRICORNER DCKT 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 106.2138 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORRESTON ( 225) -> BARDWELL_9 ( 2295) CKT 1 | 3WT_003522HILLBORO1_8_003523HILLBORO1_9_003519HILLBORO1_3 C 1 | 69 | 69 | Branch Amp | 410.0023 | - | - | - | - | 100.5502 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | 3WT_018548PRAIRILND_5_018549PRAIRILND_8_018550PRAIRILND1_3 C 1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.1476 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | 3WT_018548PRAIRILND_5_018549PRAIRILND_8_018551PRAIRILND2_3 C 2 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.1476 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | 3WT_023875EINSTN_5_023852EINSTN_8_023874EINSTN_3 C 1 | 138 | 138 | Branch Amp | 748.8818 | 128.5788 | - | 149.9762 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | BIG SPRING WEST SWITCH - BIG SPRING 138 KV WIN 2025 - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | 103.4344 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | CATCLAW - MCDONALD ROAD 138 KV LINE 2025 WIN - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | 103.4498 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | CATCLAW - MCDONALD ROAD/PECK TAP (DOUBLE B TO B) 2025 WIN - FUTURE | 138 | 138 | Branch Amp | 748.8818 | - | - | 103.83 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | Cattleman-Longshore Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | - | - | 117.3572 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | EINSTEIN - CARTERVILLE 138 KV LINE 2025 SUM - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | 132.4997 | - | 145.9056 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_000844GPL_NEVILLSW-076000L_NORTMC5_1YC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.0865 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_001058LONGSHORE_5-010053CATTLEMEN_5C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.7512 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_001058LONGSHORE_5-010053CATTLEMEN_5C2 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.7512 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_001225GARDCITYE_8-001333MCDONALD_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 103.8395 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_001225GARDCITYE_8-011218SHIPWRCK_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.6484 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_001322BIGSPRIG_8-010044STEER_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 103.1979 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_001328QUARTZSAND_8-010029LILDEWEY_8C1 | 138 | 138 | Branch Amp | 748.8818 | 136.2583 | - | 150.2659 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_001328QUARTZSAND_8-018552HOGMNTN_P8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.8024 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_001329SPRABERY_8-001337CRMWDTAP_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.2282 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_001331DRUMRIGT_8-001336FORSAN_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.3574 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_010018CARTVLRNCH_8-023851CARTRVL_8C1 | 138 | 138 | Branch Amp | 748.8818 | 132.4997 | - | 145.9054 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_010018CARTVLRNCH_8-023852EINSTN_8C1 | 138 | 138 | Branch Amp | 748.8818 | 132.4878 | - | 145.8947 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_010029LILDEWEY_8-011350WRGRN_P8C1 | 138 | 138 | Branch Amp | 748.8818 | 136.181 | - | 150.1756 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_010032LILLUTHER_8-010034LILVLMOOR_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 109.2065 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_010032LILLUTHER_8-023831LUTHER_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 109.2094 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_010034LILVLMOOR_8-023835VLMOOR_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 109.1322 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_010041SALEM_8-023832COYOTE_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 107.6555 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_010041SALEM_8-023833BULLDOG_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 107.658 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_010044STEER_8-011316BSPGWSW_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 103.2007 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_010080REDBERRY_8-023833BULLDOG_8C1 | 138 | 138 | Branch Amp | 748.8818 | 114.5557 | - | 124.3628 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_010080REDBERRY_8-900043Other_132C1 | 138 | 138 | Branch Amp | 748.8818 | 114.9268 | - | 124.6508 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_011227THRYSIX_P8-011282DESERTWD2_T8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.5348 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_011316BSPGWSW_8-011331BEALSCRK_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.3537 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_011337POLECAT1_8-011350WRGRN_P8C1 | 138 | 138 | Branch Amp | 748.8818 | 132.5463 | - | 146.0397 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_018549PRAIRILND_8-018552HOGMNTN_P8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.7724 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_023831LUTHER_8-023832COYOTE_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 108.6923 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_023834ELBOW_8-900043Other_132C1 | 138 | 138 | Branch Amp | 748.8818 | 112.2536 | - | 122.2913 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_023834ELBOW_8-900100Other_131C1 | 138 | 138 | Branch Amp | 748.8818 | 109.8645 | - | 119.9412 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_023851CARTRVL_8-023853EILAND_8C1 | 138 | 138 | Branch Amp | 748.8818 | 128.3536 | - | 141.0229 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_023875EINSTN_5-059903BEARKATC1 | 138 | 138 | Branch Amp | 748.8818 | 128.5789 | - | 149.9766 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_059902SAND_BLUFF-059907BERNOULLIC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 104.4739 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | L_059903BEARKAT-059907BERNOULLIC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 105.5976 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.0307 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-2 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.6831 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.0305 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-2 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.6829 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | LCRA TSC_NOELK_SNGTR_NOELK_SNGTR2 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.5484 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | LCRA TSC_SNGTR_SCHDR_SNGTR_SCHDR2 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.1396 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE CKT 2 (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.7512 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | LONGSHORE - PRAIRIELAND 345 KV SUM 2027 - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.0049 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | LUTHER - VEALMOOR 138 KV LINE 2027 SUM - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | 109.208 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | MCDONALD ROAD - SHIPWRECK & MCDONALD ROAD - PECK TAP 138 KV DCKT LINE (DOUBLE B TO B) B 2025 WIN - FUTURE (PECK TO DRIVER UPDATE) | 138 | 138 | Branch Amp | 748.8818 | - | - | 106.4665 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | NATURAL DAM - CALF CREEK - BIG SPRING 138 KV SUM 2026 - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | 103.8044 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | Prairieland-Quartzsand Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | 103.9981 | - | 121.4468 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | QUARTZ SAND - POLECAT CREEK 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | 132.5722 | - | 146.0572 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | - | - | 111.1939 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | STECL_10592 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.8902 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | STECL_4720 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.5895 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | STECL_4721-1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.0307 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 ( 1335) -> POLECAT1_8 (11337) CKT 1 | STECL_4721-2 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.6831 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FORSANTA_8 (1335) -> POLECAT1_8 (11337) CKT 1 | Pre-contingency | 138 | 138 | Amps | 748.8818 | - | 107.1442 | - | 100.6362 | 115.4958 | 106.2177 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORTSMITH_5 ( 3389) -> FORBESR2_5 (15201) CKT 1 | L_001907VENUS_N5-015200FORBESR1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | 101.4418 | - | 104.858 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORTSMITH_5 ( 3389) -> FORBESR2_5 (15201) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 1725.3568 | 102.7581 | - | 108.8949 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORTSMITH_5 ( 3389) -> FORBESR2_5 (15201) CKT 1 | VENUS-SAM SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | 102.3891 | - | 107.6809 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FORTSMITH_5 (3389) -> FORBESR2_5 (15201) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1725.3568 | - | - | - | 112.6798 | 144.0045 | 120.1487 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FOURBTHRS_5 ( 3388) -> SAMSW (68090) CKT 1 | L_003409LAKE_CRK1_5-013405THOUSE_A_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 111.3653 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FOURBTHRS_5 ( 3388) -> SAMSW (68090) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.056 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FOURBTHRS_5 ( 3388) -> SAMSW (68090) CKT 1 | L_013401TIGERCK_5-013405THOUSE_A_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 111.3749 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FOURBTHRS_5 ( 3388) -> SAMSW (68090) CKT 1 | L_013401TIGERCK_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.126 | 126.3117 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FOURBTHRS_5 ( 3388) -> SAMSW (68090) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 116.2377 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FOURBTHRS_5 ( 3388) -> SAMSW (68090) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 113.1984 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FOURBTHRS_5 ( 3388) -> SAMSW (68090) CKT 1 | THOUSE-LCRK*PCNCRK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.3097 | 115.4402 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FOURBTHRS_5 ( 3388) -> SAMSW (68090) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.8615 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FOURBTHRS_5 ( 3388) -> SAMSW (68090) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.1941 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FOURBTHRS_5 ( 3388) -> SAMSW (68090) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.535 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRANKLNCAMP8 ( 5568) -> FRNKLNCMPSB9 ( 5566) CKT 1 | L_005557CAYCESW9-005558VANVLECKSUB9C1 | 69 | 138 | Branch MVA | 56 | - | - | - | - | 109.7 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRANKLNCAMP8 ( 5568) -> FRNKLNCMPSB9 ( 5566) CKT 1 | L_005915SO_TEX__345A-008123BLESSING7AC1 | 69 | 138 | Branch MVA | 56 | - | - | - | - | 107.5866 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRANKLNCAMP8 ( 5568) -> FRNKLNCMPSB9 ( 5566) CKT 1 | L_008127LAN_CTY4A-008130LAN_CTY4BCS1 | 69 | 138 | Branch MVA | 56 | - | - | - | - | 101.2834 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRANKLNCAMP8 ( 5568) -> FRNKLNCMPSB9 ( 5566) CKT 1 | L10012900 | 69 | 138 | Branch MVA | 56 | - | - | - | - | 101.2834 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRANKLNCAMP8 ( 5568) -> FRNKLNCMPSB9 ( 5566) CKT 1 | P1-2_(8130-43190-1) | 69 | 138 | Branch MVA | 56 | - | - | - | - | 101.2834 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRANKLNCAMP8 ( 5568) -> FRNKLNCMPSB9 ( 5566) CKT 1 | P7-1_E1>>T1827D | 69 | 138 | Branch MVA | 56 | - | - | - | - | 100.9866 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRANKLNCAMP8 ( 5568) -> FRNKLNCMPSB9 ( 5566) CKT 1 | STECL_10301 | 69 | 138 | Branch MVA | 56 | - | - | - | - | 109.285 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRANKLNCAMP8 ( 5568) -> FRNKLNCMPSB9 ( 5566) CKT 1 | T_008121BLESSING4A-008123BLESSING7AC1 | 69 | 138 | Branch MVA | 56 | - | - | - | - | 107.5697 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 107.4968 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 106.1535 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 104.7838 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 102.9677 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | DVCPA1C21B_1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 103.172 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | DVCPA1C21B_2 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.3949 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | E_B_DAVIS_CC1_TRAIN | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 103.415 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | E_INGLCOSW_CC1_TRAIN | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.9147 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | E_NUECES_B_CC1_TRAIN | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 103.5215 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | G_005555SHROPSHRSUB9US1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 113.9553 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 106.7352 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 111.079 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 101.5642 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 103.3686 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_005555SHROPSHRSUB9-005557CAYCESW9C1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 101.4809 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_005557CAYCESW9-005558VANVLECKSUB9C1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 126.6731 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_005558VANVLECKSUB9-005560BAYCITYSUB9C1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.8359 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_005915SO_TEX__345A-008123BLESSING7AC1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 122.9803 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 108.8997 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_005915SO_TEX__345A-042400REFUGE_POI_5C27 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 101.0379 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_008102EL_CAMPO4A-008679ARROZ4AC1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 101.5956 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_008104LANCTYPM4A-008127LAN_CTY4AC1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.1888 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_008104LANCTYPM4A-008679ARROZ4AC1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.1381 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_008127LAN_CTY4A-008130LAN_CTY4BCS1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 115.368 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 109.6987 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_043010NEWGLF_S60_8-043190S_LANE__B138C60 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.1177 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_043010NEWGLF_S60_8-043340GLFTIE_POI_8C60 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.3066 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_044040BAILEY_POI_5-044060BLUE___POI_5C72 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 102.1846 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_044060BLUE___POI_5-044220JULIA__POI_5C72 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 104.0046 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_044200HILLJE__B345-044220JULIA__POI_5C72 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 104.8342 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 103.3932 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L10006-1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 102.2077 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L10010006-1B | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.1149 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | L10012900 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 115.368 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.5626 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | P1-2_(8130-43190-1) | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 115.368 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | P7-1_E1>>JULIA | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 104.0181 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | P7-1_E1>>T1827BY | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 105.6922 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | P7-1_E1>>T1827D | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 114.6851 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | P7-1_E1>>T1827H | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.4003 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | P7-1_E1>>T1839X1_ERC | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.2791 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | P7-1_E1>>T1839X2_ERC | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 103.0571 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | P7-1_E1>>T3944Z_ERC | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 110.2123 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | P7-1_E1>>T4848K | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 103.0774 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | P7-1_E1>>T6472CX1A | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 109.0886 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | P7-1_E1>>T6472CX1B | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 108.0405 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | P7-1_E1>>T6472E | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 105.7708 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | P7-1>>T2727L | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 109.7049 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | SAN_PAT_CON | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.9186 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | STECL_10301 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 126.1526 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | STECL_10302 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.3338 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | STECL_10306 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 102.9429 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | STECL_10614 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 104.3864 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | T_008121BLESSING4A-008123BLESSING7AC1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 122.9574 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | T100002 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.8589 | - | -
TSTEC | COAST | COAST | COAST, COAST | FRNKLNCMPSB9 ( 5566) -> SARGENTSUB9 ( 5564) CKT 1 | WAP - HOUDINI & STP - SHAULA | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.5404 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FRNY1_5 ( 2437) -> FRNY1_8 ( 2438) CKT 2 | 3WT_002437FRNY1_5_002438FRNY1_8_012438FRNY1_3 C 1 | 345 | 138 | Branch MVA | 600 | - | - | - | - | 103.6462 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FRNY1_5 ( 2437) -> FRNY1_8 ( 2438) CKT 2 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 138 | Branch MVA | 600 | - | - | - | 101.9109 | - | - | -
ERCC,RLAFRO | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FRNYPP_GT21 (150185) -> FRNYPP_2_5 (150190) CKT 4 | E_CBECII_CC3_TRAIN | 345 | 18 | Branch MVA | 210 | - | 100.0353 | - | - | - | - | -
ERCC,RLAFRO | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FRNYPP_GT21 (150185) -> FRNYPP_2_5 (150190) CKT 4 | E_DDPEC_CC1_TRAIN | 345 | 18 | Branch MVA | 210 | - | 100.2977 | - | - | - | - | -
ERCC,RLAFRO | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FRNYPP_GT21 (150185) -> FRNYPP_2_5 (150190) CKT 4 | G_110351STP_STP_G1UU1 | 345 | 18 | Branch MVA | 210 | - | 100.3617 | - | - | - | - | -
ERCC,RLAFRO | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FRNYPP_GT21 (150185) -> FRNYPP_2_5 (150190) CKT 4 | G_110352STP_STP_G2UU2 | 345 | 18 | Branch MVA | 210 | - | 100.3318 | - | - | - | - | -
ERCC,RLAFRO | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FRNYPP_GT21 (150185) -> FRNYPP_2_5 (150190) CKT 4 | G_150111CPSES_UNIT1UU1 | 345 | 18 | Branch MVA | 210 | - | 100.3384 | - | - | - | - | -
ERCC,RLAFRO | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FRNYPP_GT21 (150185) -> FRNYPP_2_5 (150190) CKT 4 | G_150112CPSES_UNIT2UU2 | 345 | 18 | Branch MVA | 210 | - | 100.3149 | - | - | - | - | -
ERCC,RLAFRO | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FRNYPP_GT21 (150185) -> FRNYPP_2_5 (150190) CKT 4 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 18 | Branch MVA | 210 | - | 100.073 | - | - | - | - | -
ERCC,RLAFRO | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FRNYPP_GT21 (150185) -> FRNYPP_2_5 (150190) CKT 4 | P7-1_E1>>T9797B | 345 | 18 | Branch MVA | 210 | - | 100.2987 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.572 | 110.5193 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | 3WT_001918SHRYAUTO1_5_001920SHRY_B8_011920SHRY_B_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 104.0489 | 112.4047 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | 3WT_002420CHILSW1_5_016421CHILSW_1T8_012419CHILSW1_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 109.523 | 117.0288 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 123.2291 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 116.2112 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | BEPC_015_2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 100.0315 | 106.5816 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 109.598 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | 102.5217 | 150.0708 | 163.5081 | 106.4843 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | CEDAR HILL SW - MOUNTAIN CREEK DCKT (DOUBLE B TO B) GUINN CREEK | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2898 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | CEDAR HILL SW 345-138 KV AUTO #1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.4031 | 105.1946 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | 104.3202 | 152.5742 | 165.8339 | 109.0065 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | DIVISION-SHERRY/GENERAL MOTORS 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.2152 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 100.4781 | 107.6312 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.0018 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | EXECUTIVE PKWY-SHERRY/GENERAL MOTORS 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.9164 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8714 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | G_150023MCSES_UNIT8UN8 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.2553 | 108.768 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | GLASGOW_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.6221 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | HANDLEY C-DEEN 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.8431 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | HANDLEY-DEEN 138 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 100.5025 | 107.2517 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | HANDLEY-EXECUTIVE PKWY/LIGGETT 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5791 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | KEMP RANCH - SOAP CREEK / SARDIS 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6867 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.0801 | 112.1534 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 103.3977 | 113.5426 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 104.1238 | 114.2993 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.3176 | 112.1151 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_001919SHRY_A8-002143DIVISION1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5005 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_001920SHRY_B8-002258PARKROW2_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 103.2666 | 116.3597 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_001921LIGGETTA1_5-002632MILLERRD_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.5103 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_001922LIGGETT_N8-002124INT_AIR1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0636 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_001928LIGGETT_3T5-002406NORWD1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.498 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 112.6745 | 122.5452 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 116.6137 | 126.8972 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_001950HANDLEYC_8-002104RANDL_E_T8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.3681 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 109.598 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.0018 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_002258PARKROW2_8-002259LTV1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.8575 | 114.9122 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_002259LTV1_8-002262GRANDPR1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 100.6624 | 113.6954 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_002262GRANDPR1_8-012491FSHCRK2_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 110.2815 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9929 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4591 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.1022 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.829 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.8293 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.91 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 108.6109 | 116.9564 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 110.2834 | 120.2347 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 110.1408 | 120.0528 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1617 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | SHERRY-EXECUTIVE PKWY 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.1533 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 114.3413 | 124.1293 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.5849 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.7075 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 113.8716 | 125.3975 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | Venus SW - MillerRoad 345 KV (SINGLE B TO B) New Load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.3176 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.2232 | 112.8929 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4058 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.8974 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 111.9824 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.8248 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | FSHCRK1_8 ( 2491) -> CHILSW_N8 ( 2422) CKT 1 | XFMR-MTCK_8T8-8 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.2553 | 108.768 | - | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | BAS_RANCH_CON | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 104.2733 | - | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | E_FRNYPP_CC1_TRAIN | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 100.5735 | - | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | E_FRNYPP_CC2_TRAIN | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 100.5965 | - | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | E_FTR_CC1_TRAIN | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 100.1004 | - | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | E_WHCCS2_CC2_TRAIN | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 101.7904 | - | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | G_150111CPSES_UNIT1UU1 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 102.5499 | - | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | G_150112CPSES_UNIT2UU2 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 102.5306 | - | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | G_888839BAS_RANCH_POIUC1 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 104.2743 | - | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 102.4169 | - | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 101.036 | - | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 100.5933 | - | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 100.5867 | - | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_008127LAN_CTY4A-008130LAN_CTY4BCS1 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 110.0909 | 109.6402 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_042150BASF___POI_8-042210BRZPRT_S02_8C02 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 100.8804 | 104.1898 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_042150BASF___POI_8-042810HOFMAN_X02B8C02 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 102.5606 | 105.8349 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_042210BRZPRT_S02_8-042215COPPER_X02B8C02 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | - | 102.9852 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_042215COPPER_X02B8-042540JONCRK__B138C&1-MS | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | - | 101.7044 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_042810HOFMAN_X02B8-042880LKJACK_S02_8C02 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 102.6704 | 105.9425 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_042880LKJACK_S02_8-043170RETREV__B138C&1-MS | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 104.2243 | 107.4538 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_042985DYANN__POI_8-043190S_LANE__B138C60 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | - | 101.7244 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_044010W_A_P__POI8A-044342IMPERL05T3_8C05 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 102.6185 | 102.9868 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_044015W_A_P__POI8B-044020ALIEF__S09_8C&1-MS | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 105.1481 | 105.3189 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_044015W_A_P__POI8B-044180DEWALT_S02_8C&1-MS | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 101.9163 | 102.8534 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_044020ALIEF__S09_8-044310HAYES___09B8C09 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 101.2557 | 101.4583 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_044100BRAZOS_S09_8-044230FLEWLN__B138C09 | 138 | 138 | Branch Amp | 1217.4559 | 111.4081 | - | - | - | 141.4039 | 143.3392 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_044100BRAZOS_S09_8-044280FTBEND__B138C09 | 138 | 138 | Branch Amp | 1217.4559 | 122.5762 | - | 108.4416 | - | 153.5757 | 155.4217 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_044190E_BERN__B138-044740WALLIS_S65_8C65 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 122.3099 | 119.4067 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_044230FLEWLN__B138-044510OBRIEN_B138AC&1-MS | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 102.0745 | 100.4706 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_044260FRANZ___09B8-044910ZENITH__B138C&1-MS | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | - | 100.4075 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_044342IMPERL05T3_8-044670STAFRD_S05_8C&1-MS | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 100.7906 | 101.1667 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_044640SEALY__S65_8-044700GEBHRT_X65B8C65 | 138 | 138 | Branch Amp | 1217.4559 | 109.1974 | - | - | - | 138.1847 | 141.8552 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_044640SEALY__S65_8-046220PETERS__B138C65 | 138 | 138 | Branch Amp | 1217.4559 | 105.5207 | - | - | - | 133.903 | 137.6498 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_044700GEBHRT_X65B8-888872SKYSLY_POIC65 | 138 | 138 | Branch Amp | 1217.4559 | 110.4902 | - | - | - | 139.5844 | 143.2307 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L_888872SKYSLY_POI-044740WALLIS_S65_8C65 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 121.8092 | 118.9155 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | L10012900 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 110.0909 | 109.6402 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 100.1625 | - | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P1-2_(33.1X_SODG_44342) | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 100.3856 | 100.7575 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P1-2_(40600-120095-1) | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 100.1004 | - | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P1-2_(8130-43190-1) | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 110.0909 | 109.6402 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P1-2_HOC_BUS_REACTOR | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 104.6102 | 104.8248 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>>T0202C | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 102.6553 | 105.947 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>>T0202E | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 100.924 | 104.2445 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>>T0202H | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | - | 101.7038 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>>T0205B | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 109.4719 | 109.8172 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>>T0226 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 104.5497 | 103.8859 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>>T0405 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | - | 100.0247 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>>T0924B | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 101.8563 | 101.875 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>>T0990A | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | - | 100.2108 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>>T2573B | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 108.6204 | 103.6199 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>>T2682EX1 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 103.0939 | 104.8755 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>>T2682EX2 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 103.4002 | 105.1696 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>>T2682GY1 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 103.4311 | 105.2 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>>T2682GY2 | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 103.4312 | 105.2001 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>>T9899A | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 111.9051 | 106.9692 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>T0202GX | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 101.4232 | 104.0055 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>T0205CX | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 111.6419 | 111.3257 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>T0524AY | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 100.5925 | 100.9115 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | P7-1_E1>T2682DX | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 100.9013 | 102.7022 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | SKYSLY_CON | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 126.1318 | 123.1947 | -
TCNPE | COAST | COAST | COAST, COAST | FTBEND_C60_8 (44300) -> FLEWLN__B138 (44230) CKT 60 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1217.4559 | - | - | - | - | 104.8929 | - | -
TAEPTN , TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | FTST4A (6630) -> TNLEONCRK_1 (38355) CKT 1 | Pre-contingency | 138 | 138 | Amps | 707.0448 | 104.2765 | - | 157.636 | 152.09 | 152.3032 | 142.643 | -
TSTEC | COAST | COAST | COAST, COAST | FURHMANSW8 ( 5506) -> RAYBURN8 ( 5502) CKT 1 | E5DVA1C1_1_B | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 106.4671 | - | - | -
TSTEC | COAST | COAST | COAST, COAST | FURHMANSW8 ( 5506) -> RAYBURN8 ( 5502) CKT 1 | L_008715RADIANT7A-008728COBRA7AC1 | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 101.8353 | - | - | -
TSTEC | COAST | COAST | COAST, COAST | FURHMANSW8 ( 5506) -> RAYBURN8 ( 5502) CKT 1 | L_008728COBRA7A-081003HABER7AC1 | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 104.6192 | - | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GAMMA_8 (12344) -> TRUMBULL8 ( 221) CKT 1 | ENNIS WEST - STERRETT 138 KV (SINGLE B TO B) A REAGOR SPRINGS | 138 | 138 | Branch Amp | 1004.0873 | - | - | 114.5847 | - | - | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GAMMA_8 (12344) -> TRUMBULL8 ( 221) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 1004.0873 | - | - | 115.9214 | - | - | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GAMMA_8 (12344) -> TRUMBULL8 ( 221) CKT 1 | L_002320WAX_N_8-002321WAX_8C1 | 138 | 138 | Branch Amp | 1004.0873 | - | - | 102.5941 | - | - | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GAMMA_8 (12344) -> TRUMBULL8 ( 221) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 1004.0873 | - | - | 113.7706 | - | - | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GAMMA_8 (12344) -> TRUMBULL8 ( 221) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1004.0873 | - | - | 100.0507 | - | - | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GAMMA_8 (12344) -> TRUMBULL8 ( 221) CKT 1 | WAXAHACHI-WAXAHACHI OFC 69KV/ENNIS-STERRETT 138KV (DOUBLE B TO B) A REAGOR | 138 | 138 | Branch Amp | 1004.0873 | - | - | 114.5582 | - | - | - | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | GANADO4A ( 8117) -> EDNA4A ( 8118) CKT 1 | L_008102EL_CAMPO4A-078104L_RICEBI8_1YC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | 103.5976 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | GARFIELD8 ( 9071) -> EASTON PARK ( 9143) CKT 1 | AEN_OC-PK:SE-SR | 138 | 138 | Branch Amp | 2008.1747 | - | - | - | - | 103.5263 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | GARFIELD8 ( 9071) -> EASTON PARK ( 9143) CKT 1 | AEN_OC-PK¦SE | 138 | 138 | Branch Amp | 2008.1747 | - | - | - | - | 103.5328 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | GARFIELD8 ( 9071) -> EASTON PARK ( 9143) CKT 1 | L_009071GARFIELD8-009237STONEYC1 | 138 | 138 | Branch Amp | 2008.1747 | - | - | - | - | 101.5484 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | GARFIELD8 ( 9071) -> EASTON PARK ( 9143) CKT 1 | L_009237STONEY-009240SOUTHEASTC1 | 138 | 138 | Branch Amp | 2008.1747 | - | - | - | - | 100.4102 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | GARFIELD8 ( 9071) -> EASTON PARK ( 9143) CKT 1 | L_009240SOUTHEAST-009251ONIONCKC1 | 138 | 138 | Branch Amp | 2008.1747 | - | - | - | - | 100.4173 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GARLDPL1_8 ( 2919) -> PLRD1_8 ( 2921) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1986.0011 | - | - | - | - | - | 104.0223 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GARLDPL1_8 ( 2919) -> PLRD1_8 ( 2921) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1986.0011 | - | - | - | 103.3097 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GARLDPL2_8 ( 2920) -> PLRD2_8 ( 2922) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1986.0011 | - | - | - | - | - | 106.6548 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GARLDPL2_8 ( 2920) -> PLRD2_8 ( 2922) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1986.0011 | - | - | - | 105.9551 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | GARROT_B138B (47661) -> MIDTWN_90B8B (47706) CKT 90 | L_047661GARROT_B138B-047708MIDTWN_RCTR2C90 | 138 | 138 | Branch Amp | 1602.356 | 110.2211 | - | - | - | - | - | -
TCNPE | COAST | COAST | COAST, COAST | GARROT_B138B (47661) -> MIDTWN_90B8B (47706) CKT 90 | L_047706MIDTWN_90B8B-047708MIDTWN_RCTR2CR2 | 138 | 138 | Branch Amp | 1602.356 | 110.0847 | - | - | - | - | - | -
TCNPE | COAST | COAST | COAST, COAST | GARROT_B138B (47661) -> MIDTWN_RCTR2 (47708) CKT 90 | L_047661GARROT_B138B-047706MIDTWN_90B8BC90 | 138 | 138 | Branch Amp | 1154.7004 | 147.2886 | - | - | - | 102.9203 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GELLER_8 ( 2263) -> WILMER1_8 ( 3083) CKT 1 | L_002429WATMLL_8-003083WILMER1_8C1 | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | 129.3507 | 132.3125 | 123.5384 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GELLER_8 ( 2263) -> WILMER1_8 ( 3083) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | - | - | 110.406 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GELLER_8 ( 2263) -> WILMER1_8 ( 3083) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | 123.247 | - | - | -
TBTU,TTMPA | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_EAST138 (32896) CKT 1 | BEPC_009 | 138 | 138 | Branch Amp | 1133.782 | - | - | - | - | 100.6793 | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | 3WT_000975JKCREEK1_032859BRYN_JK_CRK_000978JKCREEK3 C 1 | 138 | 138 | Branch Amp | 945.9339 | - | - | 106.8468 | 118.7832 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 100.3557 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 101.3692 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 100.8688 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | BEPC_009 | 138 | 138 | Branch Amp | 945.9339 | - | - | 116.7486 | 129.4893 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | BEPC_205 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 102.4056 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | BEPC_206 | 138 | 138 | Branch Amp | 945.9339 | - | - | 104.2394 | 117.0698 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 100.3445 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | BRYN_1035 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 101.5112 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | BRYN_1036 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 101.3714 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | BRYN_1037 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 105.9791 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | BRYN_1087 DC | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 104.2047 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | BRYN_1088 DC | 138 | 138 | Branch Amp | 945.9339 | - | - | 106.3345 | 118.609 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | BRYN_1092 DC | 138 | 138 | Branch Amp | 945.9339 | - | - | 100.2732 | 112.3038 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | BRYN_1093 DC | 138 | 138 | Branch Amp | 945.9339 | - | - | 107.2689 | 119.586 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | BRYN_9995DC | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 104.9144 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | BRYN_9996DC | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 103.233 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | E5DVA1C1_1_B | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 103.0107 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | E5DVA1C1_1_B_1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 101.8516 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | E5DVA1C1_1_B_2 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 101.1292 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | G_120051DAN_DANSBYG1UN1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 105.9791 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | G_120052DAN_DANSBYG2UN1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 101.3714 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | G_120053DAN_DANSBYG3UN1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 101.5112 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | G_120081TAM_TAM_GTG1UN1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 101.4677 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | JEWETT-ROBERTSON (BEC)_8 (SINGLE B TO B) B | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 102.4054 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | JEWETT-SNGLTN__5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 100.7972 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_000002KEITHSW-000013KEITHC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | 105.018 | 119.3233 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_000002KEITHSW-000964GIBN_CREK_8C1 | 138 | 138 | Branch Amp | 945.9339 | - | - | 105.9164 | 119.4894 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_000002KEITHSW-032879BRYN_STPHLLWC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 103.911 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_000013KEITH-000017CARLOSSWC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | 104.3738 | 118.7098 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_000017CARLOSSW-032000CSSTC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | 104.1556 | 116.8292 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_000032ROBERTSON-000037RIDGEC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 102.3912 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_000033WATSONCHPL-000037RIDGEC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 102.4352 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_000041SKIPPER-000042TIMBERCSTC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 100.0451 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_000041SKIPPER-003394JEWETTA_8C1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 100.1372 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_000964GIBN_CREK_8-032896BRYN_EAST138C1 | 138 | 138 | Branch Amp | 945.9339 | - | - | 106.5481 | 120.1075 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_000967GIBN_CREK_5-000975JKCREEK1C1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 102.1019 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 100.1759 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 100.5724 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_008728COBRA7A-081003HABER7AC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 100.0328 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 100.6262 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032000CSST-032001CSPTC2 | 138 | 138 | Branch Amp | 945.9339 | - | - | 101.8974 | 113.8487 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032000CSST-032004CSSCC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 105.1655 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032000CSST-032882BRYN_TABR138C3 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 103.4556 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032000CSST-032896BRYN_EAST138C1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 105.8328 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032001CSPT-032002CSSVC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 108.719 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032003CSGP-032004CSSCC2 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 102.6389 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032780BRYN_RELLIS-032853BRYN_SMETANAC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 102.3518 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032851BRYN_LENRDRD-032853BRYN_SMETANAC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 102.6782 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032851BRYN_LENRDRD-032862BRYN_ATK138C1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 104.2249 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032854BRYN_TRI_PK-032881BRYN_KURTENC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 105.9372 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032854BRYN_TRI_PK-032897BRYN_DSBY138C1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 104.7028 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032857BRYN_SNOO138-032867BRYN_BRUSCKC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 103.1001 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032859BRYN_JK_CRK-032881BRYN_KURTENC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 106.5711 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032859BRYN_JK_CRK-032882BRYN_TABR138C1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 102.493 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032862BRYN_ATK138-032897BRYN_DSBY138C5 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 102.7936 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032863BRYN_THMP_CK-032867BRYN_BRUSCKC1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 104.0838 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032863BRYN_THMP_CK-032897BRYN_DSBY138C1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 104.9559 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_032879BRYN_STPHLLW-032882BRYN_TABR138C1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 102.5857 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 100.2383 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | P7-1/C5-CTT-13-2 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 100.2578 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | P7-1_E1>>T1827GX_ERC | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 100.724 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | T_032870BRYN_TABOR69-032882BRYN_TABR138C1 | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 100.5087 | - | - | -
TTMPA,TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 ( 964) -> BRYN_GRNPRAI (32878) CKT 1 | TWIN_OAK N__5 - GIBN_CREK_5 & JKCREEK1 - GIBN_CREK_5 (CAT_C)(DOUBLE B TO B) | 138 | 138 | Branch Amp | 945.9339 | - | - | - | 103.8001 | - | - | -
TTMPA , TBTU | EAST | EAST | EAST, EAST | GIBN_CREK_8 (964) -> BRYN_GRNPRAI (32878) CKT 1 | Pre-contingency | 138 | 138 | Amps | 891.1275 | - | - | - | 104.0754 | 121.9706 | 119.0019 | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | GIBSON_5 ( 3706) -> BRANGUS_5 ( 3705) CKT 1 | L_003377LITTLEPOND_5-003687BELL_E_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 110.633 | 116.0448 | -
TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | GIBSON_5 ( 3706) -> BRANGUS_5 ( 3705) CKT 1 | L_003377LITTLEPOND_5-003704HOGCREEK_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.4757 | 106.949 | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | GIRA_TAP2A ( 6151) -> DKEC2A ( 6152) CKT 1 | L_006195ROBY2A-006196ROTN2AC1 | 69 | 69 | Branch Amp | 267.7566 | 116.0679 | - | 112.8165 | 104.151 | 105.8526 | 106.1179 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.6734 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | 3WT_001918SHRYAUTO1_5_001920SHRY_B8_011920SHRY_B_3 C 1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3992 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | 3WT_001934SHRYAUTO2_5_001919SHRY_A8_011921SHRY_A_3 C 2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0589 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0841 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2612 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4896 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.2234 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4946 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.281 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6058 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3536 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7379 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4602 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.62 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3576 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7432 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4644 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLEN-MOSES 345-138 AUTO-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1813 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4613 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.1621 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4586 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.1634 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | B2-COD-1_B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0682 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | BARRETT_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0325 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | BAS_RANCH_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4679 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 105.6243 | - | 107.0328 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.7714 | - | 105.7117 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | BENBROOK-CARMICHAEL BEND*BENBROOK SYCAMORE CRK 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.017 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | BENBROOK-PARKER*CARMICHAEL BEND 345 KV WITH BENBROOK AUTO (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1865 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.8326 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | BEPC_015_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.1414 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | BEPC_22 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2426 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | BEPC_227-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0238 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | BEPC_227-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0238 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | BEPC_301_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5894 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | BEPC_304_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6582 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | BLUBIRD_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.7711 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.866 | - | 104.2877 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | CARMICHAEL BEND-TIMBERVIEW 345 KV*DECORDOVA-CLEBURNE 138 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0457 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | CARTWHEEL_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5022 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | CEDAR HILL - DESOTO/LOOP NINE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.6441 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 114.7433 | - | 102.3038 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | CEDAR HILL SW - FISH CREEK 138 KV (SINGLE B TO B) FISH CREEK 138/69 TRANSFORMER | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0406 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 114.29 | - | 102.1822 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | CLEAR CROSSING - COODY CROSSING/THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6025 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | CLY_PHNT1P7F1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4945 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | CLY_PHNT1P7F1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3901 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | CLY_PHNT2P7F1-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1466 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | CLY_PHNT2P7F1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0398 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2334 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | COODY CROSSING - TECUMSEH AND CLEAR CROSSING - THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8277 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | DES_WILL_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.4676 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | DRY_CREEK_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.5009 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | DUNHAM - KRUMW/RNK DC 345 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1953 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.9851 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | DVCPA1C21B_1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0279 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | DVCPA1C21B_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0097 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_ETCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5384 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_FRNYPP_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.897 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_FRNYPP_CC2_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.9027 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_JACKCNTY_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.2938 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_JCKCNTY2_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3143 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_KMCHI_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.0788 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_KMCHI_CC2_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.0973 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_LPCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.7717 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_LPCCS_CC2_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5497 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_OECCS_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1263 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_OECCS_CC2_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1285 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_PANDA_S_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.7551 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_TEN_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1709 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_TGCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.2875 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_TNSKA_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4463 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_WCPP_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.9419 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_WHCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5921 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E_WHCCS2_CC2_TRAIN | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.848 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E5DVA1C1_1_B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4156 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E5DVA1C1_1_B_1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.1116 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | E5DVA1C1_1_B_2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.844 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | EAGLE MTN-PARKER/HICKS 345 KV (DOUBLE B TO B) A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3259 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | EAST LEVEE - NORWOOD 138 KV & NORWOOD - WEST LEVEE 345 KV DCKT A LUPO | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.3241 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0942 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 131.2707 | - | 121.2502 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0397 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ENNIS - PEBBLE CREEK 138 KV SWITCH (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7427 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ERIKA_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.0346 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.949 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | FORNEY - ROYSE DCKT 345 KV(DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.117 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | FORNEY - SEAGOVILLE SW/TRI CORNER DCKT 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7904 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_000575JCKCNTY5UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.503 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_000579JCKCNTY8UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6123 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_000971PRUITT_8US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1269 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_001777PARIS_8US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0599 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_001877MITCHBND_5UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2986 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_003321REDLAND_5UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5686 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_006100OKLA7AUC0 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.983 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_010012METEOR_5US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0188 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_023909WALLABY_5US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.097 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_079000GRAYUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3803 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_120041MLSES_UNIT1UL1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3988 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_120042MLSES_UNIT2UL2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4495 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_120043MLSES_UNIT3UL3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4702 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_120142SCSES_UNIT2UN2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3731 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_120442BR_ARROW_S2US2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1098 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_120591STAM_SLR_S2US2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0972 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_120821HOPKINS_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0937 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_143701DELILA_1_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0055 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_143702DELILA_1_S2US2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0055 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_143961MISAE2_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1744 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_144211HRNTSLR_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2061 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_144261EIFSLR_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2619 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_144561BAKE_SLR_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2529 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_144562BAKE_SLR_S2US2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2534 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150021MCSES_UNIT6UN6 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3048 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150022MCSES_UNIT7UN7 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3706 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150023MCSES_UNIT8UN8 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.3805 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150041GRSES_UNIT1UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0441 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150042GRSES_UNIT2UN2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3868 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150051HLSES_UNIT3UN3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9646 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150052HLSES_UNIT4UN4 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4214 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150053HLSES_UNIT5UN5 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.1772 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150082OLIN_OLING_2UN2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0925 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150083OLIN_OLING_3UN3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2935 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150091LHSES_UNIT1UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.9976 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150092LH2SES_UNIT2UN2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.7565 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150111CPSES_UNIT1UU1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.9942 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150112CPSES_UNIT2UU2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.0552 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150133MIL_MILLERG3UN3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0032 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150151MDANP_CT1UN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1892 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150152MDANP_CT2UN2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2189 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150153MDANP_CT3UN3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1343 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150154MDANP_CT4UN4 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.132 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150155MDANP_CT5UN5 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2111 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_150156MDANP_CT6UN6 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2148 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_151371LILY_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0124 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_151421STRATEGC_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.1155 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_153141PORT_SLR_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2553 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_153532ELIZA_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1379 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_153911PNGT1_PV_S1US1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9036 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_154411ANOLEBES_B1UB1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0054 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_5920EASTDCTIE | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.0735 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_888839BAS_RANCH_POIUC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4751 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_888845DRY_CREEK_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.006 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_888851TRIFECTA_POIUN1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0198 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_888854PINEFOREST_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5813 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_888874VIKING_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1794 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_888878ERIKA_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3712 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_888879BLUBIRD_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.925 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_888881SOLAC_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0045 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | G_888885GALAC_POIUS1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1846 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | GALAC_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1181 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | GRAHAM UNIT 2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3868 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | HICKS - EAGLE MTN*PARKER 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9081 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | HICKS -ALLIANCE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4992 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | HIGHNOON_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.079 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | HUTTO - PFGRLVIL & HUTTO - RDRSE-GILLELAND CREEK (DOUBLE B TO B )B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1062 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | JEW- LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6439 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | JEWETT-BALE*TWINOAK_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0991 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | KEMP RANCH - SOAP CREEK / SARDIS 138 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3688 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1062 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4054 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4081 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | KRUM WEST - RILEY A 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8325 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | KRUMW-WEST DENT/DUNHAM 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6934 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.2662 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.2882 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_000203SARDIS8-012317STERRETTL_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1078 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_000221TRUMBULL8-002229PEBBLCRK_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6909 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_000221TRUMBULL8-012344GAMMA_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7142 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_000223SAINTPAUL-000404JESSICAC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0057 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_000404JESSICA-000419LILLIAN8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0883 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_000436GRANDVIEW-000443SANDFLATSWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0264 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_000443SANDFLATSW-000444COVINGTONC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0516 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_000444COVINGTON-888859HIGHNOON_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0823 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_000646LEWISVLSW5_1-002361CRLTN_NW1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0088 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_000646LEWISVLSW5_1-021851DUNHAM_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6338 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_000902POES31569-000981SPNCRINT69C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0682 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_000970BENDAVIS_5-002478ROYSE_S5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0769 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001421WILLOWCK_5-011418TECUMSEH_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.142 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001421WILLOWCK_5-011523THOMPRCE_5C2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0743 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001421WILLOWCK_5-031875RAMHORNH_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4137 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001421WILLOWCK_5-031875RAMHORNH_5C2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4137 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001429JACKSBRO_5-011736BIRDDOG_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0427 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001436PARKER_5-001859BASECAMP_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2932 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001436PARKER_5-002081HICKS_SW1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4279 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001685FARMVLSW_5-002461ROYSE_N5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.08 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001685FARMVLSW_5-002478ROYSE_S5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0888 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001685FARMVLSW_5-011689CYCLONE_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2494 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 105.3799 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001695MOSES_5-001697SULSP_SS1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1048 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1812 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001697SULSP_SS1_5-888847CARTWHEEL_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2353 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001730W_KRUM_5-006111RILEY7BC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0892 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001730W_KRUM_5-006111RILEY7BC2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0892 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001730W_KRUM_5-011736BIRDDOG_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3702 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001730W_KRUM_5-152087NOBLESLR_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4517 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.7554 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001880ROCKYCRK_5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0076 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001880ROCKYCRK_5-888879BLUBIRD_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7222 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001895MITCHBND2_5-002285CARMICHL_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3944 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001900COMCHPKW_5-888874VIKING_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0128 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.0409 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.5747 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.6887 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.894 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001906VENUS_S5-015201FORBESR2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.6436 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001906VENUS_S5-888857OYSTER_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 108.8345 | - | 104.1981 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001906VENUS_S5-888880DES_WILL_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.1739 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7889 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.6306 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001907VENUS_N5-011902BRITTNRD2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4369 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001907VENUS_N5-015200FORBESR1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.7445 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001907VENUS_N5-068091NAVARROC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 107.9939 | - | 104.2249 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001911WEBB1_5-001929CENTURY1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3096 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001911WEBB1_5-011902BRITTNRD2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4149 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001918SHRYAUTO1_5-001929CENTURY1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1802 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001919SHRY_A8-002257PARKROW1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3191 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001920SHRY_B8-002258PARKROW2_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.22 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001921LIGGETTA1_5-002632MILLERRD_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.4038 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001928LIGGETT_3T5-002406NORWD1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.975 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.1767 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.8015 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 131.2707 | - | 121.2502 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002257PARKROW1_8-002260POLY_AM1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2409 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002258PARKROW2_8-002259LTV1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1555 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002259LTV1_8-002262GRANDPR1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1021 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002260POLY_AM1_8-012492LAKECRST_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1075 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002263GELLER_8-003079SSWWT2T_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8331 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002263GELLER_8-003083WILMER1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7985 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002285CARMICHL_5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0935 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002286PADERA_8-002310MDLTHTXI2_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2851 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002286PADERA_8-002311MDLTH_N_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1537 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002289SOAPCRK_8-002303KEMPRNCH_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1157 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002289SOAPCRK_8-002310MDLTHTXI2_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.284 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002291CLEBRN_W_8-037810TNHILL_CO_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0467 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1403 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002305AIRPRD_T8-002307MDLTHTXI1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0938 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002313MDLTH_N_8-002314MDLTHBOX_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0786 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.1092 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0677 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002361CRLTN_NW1_5-002387HACKBRY1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1601 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002361CRLTN_NW1_5-033646LEWISVLSW5_2C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0644 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002372COLLINSS1_5-002373ANNASW_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1828 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002406NORWD1_5-012398TOPEKA1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.1688 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002420CHILSW1_5-002431DESSW1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5138 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002420CHILSW1_5-002847LOOP9_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.085 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002421CHILSW_S8-002999DVIL1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0078 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.2666 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.2666 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 110.9386 | - | 103.1608 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 109.7748 | - | 102.3097 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002432TRICRN1_5-888878ERIKA_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5192 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002434SGVLSW1_8-003076SGVL1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0539 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.897 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.9027 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002461ROYSE_N5-002464CASHSW_T5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2163 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002478ROYSE_S5-002485POETRY_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4527 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002491FSHCRK1_8-012492LAKECRST_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1072 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002726KEMP_S_8-002774KNGCRK_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2702 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_002726KEMP_S_8-003264SEVENPTS_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.349 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003076SGVL1_8-003077KLEBRG1T_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9576 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003077KLEBRG1T_8-003079SSWWT2T_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8643 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003100MARTINLK_5-003102TYLERGND_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3231 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.4902 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.2687 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 108.7109 | - | 102.4097 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003127TRINIDAD_8-003260NIPAKTAP_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4947 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003133RICHLND2_5-003381BIGBRNW_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.2068 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003134RICHLND1_5-003380BIGBRNE_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.9335 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 129.0062 | - | 119.4354 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003260NIPAKTAP_8-003265MANKIN_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.493 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003262CEDRCREK_8-003263CEDRCKPU_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4581 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003262CEDRCREK_8-003287WILL_WHT_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4403 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003263CEDRCKPU_8-003265MANKIN_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4736 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003264SEVENPTS_8-003287WILL_WHT_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4145 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.9501 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003374FILESVALY_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.8935 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003377LITTLEPOND_5-003687BELL_E_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9274 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003377LITTLEPOND_5-003704HOGCREEK_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4946 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003384STJOHNS_5-003409LAKE_CRK1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.7821 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003384STJOHNS_5-003711BALE_S5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.1669 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003388FOURBTHRS_5-003405THOUSE__5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4115 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003388FOURBTHRS_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5909 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003390JEWETT_S5-003711BALE_S5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1871 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003390JEWETT_S5-046020LIMEST_POI_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1507 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003403LAKE_HALL_5-003405THOUSE__5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0362 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003409LAKE_CRK1_5-013405THOUSE_A_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3567 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0683 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3404 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003431SDSES_2_8-013430SAND_TXU_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0895 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003518BLUMPUMP1_8-037810TNHILL_CO_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0654 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003687BELL_E_5-003705BRANGUS_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0783 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003704HOGCREEK_5-039950TNTNP_ONE_3C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0866 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003705BRANGUS_5-003706GIBSON_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6826 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_003706GIBSON_5-039950TNTNP_ONE_3C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1764 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3916 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1133 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2008 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_005380SHAULA-005915SO_TEX__345AC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0012 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0215 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.8375 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_006903BOZE-151372LILY_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0828 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_008249ANGSTRM7A-088249SDI7AC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1251 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_008715RADIANT7A-008728COBRA7AC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2931 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_008728COBRA7A-081003HABER7AC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.375 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3606 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_011523THOMPRCE_5-060515CLEARCRO7AC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1405 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_011688THORNTRE_5-143625SAMSON_1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5551 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_011688THORNTRE_5-143705DELILA_1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.441 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_012329SHANKLSW_8-012344GAMMA_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7129 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_013401TIGERCK_5-013405THOUSE_A_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3565 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_013401TIGERCK_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4606 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.4358 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.4604 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_021851DUNHAM_5-033646LEWISVLSW5_2C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5855 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_023920ABERNATH_5-141607AEEC_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0731 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_059909NOVA_138-059998NOVA8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1863 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_068006NAVREACTR-068008LATIMERC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0358 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_068011ASPIRE-068051REATAC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5642 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_068050ROMNEY2_W-068051REATAC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1987 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_068055SKYDANCER-068080KOPPRL2EC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1939 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_068055SKYDANCER-068090SAMSWC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2052 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_068060ROMNEY2_E-068070KOPPRL2WC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1783 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_081003HABER7A-081005ACME7AC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.464 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_143575SAMSON_3_5-143625SAMSON_1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1326 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_143705DELILA_1_5-143757DELILA_2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4931 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.3108 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_888847CARTWHEEL_POI-002464CASHSW_T5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3816 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1812 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_888857OYSTER_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.7797 | - | 102.2312 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2535 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_888874VIKING_POI-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3598 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_888878ERIKA_POI-003105ELKTON_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8923 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_888880DES_WILL_POI-001916LIGGETTA2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.3151 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L_888889MIDPOINT_POI-003518BLUMPUMP1_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0703 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L201000169 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0848 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | L20255426 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0848 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LAKE CREEK - LAKE HALL/TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.8736 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LAKE CREEK - LAKE HALL_5 (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0306 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LAKE CREEK-RATTLESNAKE/ST JOHNS_5 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.782 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LAKE CREEK-ST JOHNS_5 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.7821 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LATIMER_REATA_P7F1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.8978 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LCRA TSC_BAKERS_CEDACA_DC | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0826 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LCRA TSC_T510_T511_3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.013 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LCRA TSC_T510_T738_1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.346 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LCRA TSC_T510_T775 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0525 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4212 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.5559 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.8005 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.9386 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.4753 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.3228 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 107.3711 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | Liggett SW - MillerRoad 345 KV (SINGLE B TO B) New Load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.4038 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LIGGETT-NORWOOD 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.2135 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.8329 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.6529 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.808 | - | 102.6077 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | LOOP NINE-DESOTO/CEDAR HILL 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4319 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MANKIN-KINGSCREEK_8 (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2269 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.0459 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.7355 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MB210140210145-AAAAA | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5738 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MB210140210145-AAAAB | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6878 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MB210140210145-AABA | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4495 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MB210140210145-ABAAA | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3661 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MB210140210145-ABAAB | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2593 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MB210140210145-ABABA | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0328 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MB210140210145-ABABB | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1389 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MB210140210145-ABBA | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1624 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MB210160210165 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5882 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MB255152551420840 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5797 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.7291 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9862 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.7618 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNIT 4 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3526 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8766 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 105.2628 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | MOSES-SULPHUR SPRINGS SW 345-138 KV AUTO SULPHUR SPRINGS SW 345-138 KV AUTO #1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2037 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | NEW-GRAHAM-PARKER 345 KV-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3619 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4688 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.2153 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | NORTHWEST CARROLLTON - LEWISVILLE SW (BEPC) 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.277 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | NORWOOD - LIGGETT/CEDAR HILL DCKT 345 KV (DOUBLE B TO B) NEW_LOAD | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8736 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | NORWOOD - WEST LEVEE 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.2914 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | NORWOOD-LIGGETT 345 & MOUNTAIN CREEK - LIGGETT 138 KV DCKT A BLUBONT | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.6126 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | OYSTER_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 107.6169 | - | 102.748 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | P7-1_E1>>T0976BX | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3258 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | P7-1_E1>>T1827GX_ERC | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6912 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | P7-1_E1>>T1839X1_ERC | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0117 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | P7-1_E1>>T1839X2_ERC | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0301 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | P7-1_E1>>T2222GX | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0402 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | P7-1_E1>>T3944Z_ERC | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.037 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | P7-1_E1>>T4848K | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6056 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | P7-1_E1>>T6472CX1A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0158 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | P7-1_E1>>T8181H | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0122 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | P7-1_E1>T5959A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0878 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | P7-1_E1>T5959B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.137 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | PARKER-COMANCHE PEAK 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3329 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.9626 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV DCKT & EAGLE MOUNTAIN - WEATHERFORD 138 KV LINE | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.8355 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | PINEFOREST_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4432 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | RAMHORN - DUNHAM DC 345 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4537 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | RAMHORN - HICKS 345 AND BASE CAMP - BENNET 138 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2429 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | RAMHORN - HICKS 345 AND BASE CAMP - BENNET 138 (DOUBLE B TO B) CKT 2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2429 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (COMMON TOWER) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.9383 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | RAMHORN - WILLOW CREEK DC 345 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.1179 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | REAT_SKYD_L2F1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1942 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | RICH-BBROWN (DOUBLE B TO B)A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 108.2288 | - | 100.4712 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | RILEY - TESLA & TESLA - SALVARE | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1888 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8039 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.0694 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.769 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 107.8173 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | SCUR_CLY_P7 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5895 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | SEAGOVILLE SW - FORNEY/TRICORNER DCKT 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0066 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | SEAGOVILLE SW-KAUFMAN-TERRELL SW (SINGLE B TO B) A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2355 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | SHERRY-TIMBERVIEW*VENUS 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6322 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2368 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | T_000981SPNCRINT69-000982DN_STEAM_8C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0682 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | T_059908NOVA_345-059998NOVA8CT1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1863 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1303 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.2641 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4751 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | THOUSE-LCRK*PCNCRK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2375 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.7343 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TIMBERVIEW-COMANCHE PEAK*CARMICHAEL BEND 345 KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0084 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TIMBERVIEW-COMANCHE PEAK*DECORDOVA 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7969 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.3623 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TIMBERVIEW-VENUS 345 KV DOUBLE-CIRCUIT LINE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1897 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.9552 | - | 101.2406 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2653 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.5673 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TRICORNER - TYLER GRANDE (single B TO B) new_load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2433 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.5802 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.1265 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.3616 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 116.9756 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TRIFECTA_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0202 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TRINIDAD - MANKIN (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4928 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TRIN-MANKIN*EUSTACE SOUTHEAST(DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.5321 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TRIN-NIP*MA (DOUBLE B TO B)B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3575 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 118.9508 | - | 110.9172 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.369 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 105.1593 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 124.7007 | - | 114.3659 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TULECANYON-TESLA (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0242 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9366 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9526 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.0688 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VALLEY S-ANNA SW 345 KV & VALLEY S-FARMERSVILLE 345 KV | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3607 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VALLEY S-VALLEY SW 345 KV & VALLEY S-PARIS SW 345 KV | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2909 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2526 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 107.6334 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 107.9482 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS - WEBB 345KV (SINGLE B TO B) BRITTONRD2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.403 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 108.8458 | - | 100.2858 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | Venus SW - MillerRoad 345 KV (SINGLE B TO B) New Load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.6306 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 121.7944 | - | 119.988 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 117.6036 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 104.0053 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 105.8776 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.2071 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS-FORT SMITH SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.7128 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.7021 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4973 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4877 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.6221 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.1384 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.9466 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS-NAVARRO 345 KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 119.2319 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VENUS-SAM SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.7902 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | VIKING_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8703 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | WAP - HOUDINI & STP - SHAULA | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0465 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 132.5715 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.8806 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 107.532 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | WILLOW CREEK - CLEAR CROSSING (THOMAS PRICE) & COODY CROSSING - TECUMSEH 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV SUM 2026 - FUTURE (TRIPLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.6196 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | WILLOW CREEK - HENDERSON RANCH 345 KV & WILLOW CREEK - JACKSBORO 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.399 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | WILLOW CREEK - TECUMSEH/THOMAS PRICE 345 KV DCKT WIN 2023 - FUTURE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9687 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | WILLOW CREEK - THOMAS PRICE\TECUMSEH CREEK 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV WIN 2023 - FUTURE (TRIPLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.893 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.9423 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | WINDMILL - AJSWOPE (SINGLE B TO B) SUM 2028 - FUTURE | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0948 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.844 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C2_345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1116 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | WSHACK_LATIMER_L1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0306 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | WSHACK_LATIMER_P7 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.2932 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-ENNSTRAC_8-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.7301 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-ENNSTRAC_8-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2368 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-GRHAMSES1_8-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0441 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-HANDLEYC_8-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.9646 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-HANDLEYC_8-3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.1772 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-HANDLEYD_8-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4214 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-LKHB_1T8-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.9976 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-LKHB_2T8-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.7565 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-MARTINLK_5-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3988 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-MARTINLK_5-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4495 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-MARTINLK_5-3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.4702 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-MDLTHELP_5-5 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2111 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-MDLTHELP_5-6 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2148 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-MDLTHELP_N5-3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1343 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-MDLTHELP_N5-4 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.132 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-MDLTHELP_S5-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1892 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-MDLTHELP_S5-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2189 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-MTCK_6T8-6 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3048 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-MTCK_7T8-7 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3706 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-MTCK_8T8-8 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.3805 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-MTENTRPR_5G-4 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.2312 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-STRYKER_8-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3731 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-WHCCS2_4-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3526 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-WHCCS2_5-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.7119 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-WLFHMDPT_5-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8443 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> BIGONION_5 ( 2466) CKT 1 | XFMR-WLFHOSTR-3 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1111 | - | - | -
TLSTR , TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLASGOW_POI (888877) -> NAVARRO (68091) CKT 1 | Pre-contingency | 345 | 345 | Amps | 2729.4439 | - | - | - | - | 104.2814 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | 3WT_018548PRAIRILND_5_018549PRAIRILND_8_018550PRAIRILND1_3 C 1 | 138 | 138 | Branch Amp | 748.8818 | - | 100.5404 | 103.4931 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | 3WT_018548PRAIRILND_5_018549PRAIRILND_8_018551PRAIRILND2_3 C 2 | 138 | 138 | Branch Amp | 748.8818 | - | 100.5404 | 103.4931 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | 3WT_023875EINSTN_5_023852EINSTN_8_023874EINSTN_3 C 1 | 138 | 138 | Branch Amp | 748.8818 | 130.4821 | 137.924 | 153.8853 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | BIG SPRING WEST SWITCH - BIG SPRING 138 KV WIN 2025 - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | 102.8195 | 106.1488 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | CATCLAW - MCDONALD ROAD 138 KV LINE 2025 WIN - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | 101.3275 | 106.351 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | CATCLAW - MCDONALD ROAD/PECK TAP (DOUBLE B TO B) 2025 WIN - FUTURE | 138 | 138 | Branch Amp | 748.8818 | - | 101.6275 | 106.7719 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | CATCLAW - RINGO CKT 138 KV BEG - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.4039 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | CATTLEMAN - PRAIRIE LAND 345 KV 2026 SUM - 2027 SUM (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | 100.6284 | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | Cattleman-Longshore Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | - | - | 121.2555 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | CATTLMAN - LONGSHORE/PRAIRIE LAND 345 KV WIN 2027 - SUM 2027 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | 110.5332 | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | E_OECCS_CC1_TRAIN | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.0671 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | E_OECCS_CC2_TRAIN | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.1287 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | EINSTEIN - CARTERVILLE 138 KV LINE 2025 SUM - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | 133.0519 | 141.6154 | 148.7138 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | G_010012METEOR_5US1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.4092 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | G_131551OWF_OWFUW1 | 138 | 138 | Branch Amp | 748.8818 | - | 101.4242 | 101.3191 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_000842GPL_KINGMTSW-000843GPL_KINGMTTPC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.3137 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.7194 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_000844GPL_NEVILLSW-076000L_NORTMC5_1YC1 | 138 | 138 | Branch Amp | 748.8818 | - | 100.664 | 102.5695 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_000844GPL_NEVILLSW-076002L_BAKERS5_1YC1 | 138 | 138 | Branch Amp | 748.8818 | - | 100.5741 | 101.0304 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_001021MIDLET_5-010062ROUGH_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.1493 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_001058LONGSHORE_5-010053CATTLEMEN_5C1 | 138 | 138 | Branch Amp | 748.8818 | - | 102.1376 | 104.4358 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_001058LONGSHORE_5-010053CATTLEMEN_5C2 | 138 | 138 | Branch Amp | 748.8818 | - | - | 104.4358 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.1856 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_001189BARBER_LK1_8-010050RANGER_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | 100.3585 | 101.0636 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_001225GARDCITYE_8-001333MCDONALD_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | 101.5454 | 106.7482 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_001225GARDCITYE_8-011218SHIPWRCK_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | 100.153 | 104.3718 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_001322BIGSPRIG_8-010044STEER_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | 102.7019 | 105.8939 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_001328QUARTZSAND_8-010029LILDEWEY_8C1 | 138 | 138 | Branch Amp | 748.8818 | 136.6964 | 144.8068 | 153.1147 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_001328QUARTZSAND_8-018549PRAIRILND_8C2 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.891 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_001328QUARTZSAND_8-018552HOGMNTN_P8C1 | 138 | 138 | Branch Amp | 748.8818 | - | 100.2746 | 103.0864 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_001329SPRABERY_8-001337CRMWDTAP_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 102.2011 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_001331DRUMRIGT_8-001335FORSANTA_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | 103.5967 | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_001331DRUMRIGT_8-131552OWF_1_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | 105.6006 | 104.5881 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_001333MCDONALD_8-011282DESERTWD2_T8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.3896 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_001337CRMWDTAP_8-011394PINMID_P8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.068 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_010018CARTVLRNCH_8-023851CARTRVL_8C1 | 138 | 138 | Branch Amp | 748.8818 | 133.0519 | 141.6152 | 148.7138 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_010018CARTVLRNCH_8-023852EINSTN_8C1 | 138 | 138 | Branch Amp | 748.8818 | 133.0408 | 141.6039 | 148.704 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_010029LILDEWEY_8-011350WRGRN_P8C1 | 138 | 138 | Branch Amp | 748.8818 | 136.6156 | 144.7593 | 153.0229 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_010032LILLUTHER_8-010034LILVLMOOR_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 111.839 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_010032LILLUTHER_8-023831LUTHER_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | 111.1244 | 111.8417 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_010032LILLUTHER_8-023835VLMOOR_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | 111.122 | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_010034LILVLMOOR_8-023835VLMOOR_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 111.7738 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_010041SALEM_8-023832COYOTE_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | 110.2037 | 110.2302 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_010041SALEM_8-023833BULLDOG_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | 110.2056 | 110.2326 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_010044STEER_8-011316BSPGWSW_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | 102.7033 | 105.8959 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_010050RANGER_8-011393FRONTIER_P8C1 | 138 | 138 | Branch Amp | 748.8818 | - | 100.6748 | 101.1815 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_010053CATTLEMEN_5-019000LONGSHRFLY_5C1 | 138 | 138 | Branch Amp | 748.8818 | - | 100.5023 | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_010058CATCLAW_8-011345SLGRLAKE_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.7929 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_010080REDBERRY_8-023833BULLDOG_8C1 | 138 | 138 | Branch Amp | 748.8818 | 114.1665 | 132.1621 | 127.2035 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_010080REDBERRY_8-900043Other_132C1 | 138 | 138 | Branch Amp | 748.8818 | 114.5099 | 132.5465 | 127.4535 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_011028ODESEHV2_5-059901GRELTONC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.002 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_011227THRYSIX_P8-011282DESERTWD2_T8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 102.6441 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_011316BSPGWSW_8-011331BEALSCRK_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | 101.6359 | 103.9119 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_011337POLECAT1_8-011350WRGRN_P8C1 | 138 | 138 | Branch Amp | 748.8818 | 132.8259 | 142.554 | 148.8249 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_011372MEYERSDRW_P8-011394PINMID_P8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.4837 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_018548PRAIRILND_5-019000LONGSHRFLY_5C1 | 138 | 138 | Branch Amp | 748.8818 | - | 100.6197 | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_018549PRAIRILND_8-018552HOGMNTN_P8C1 | 138 | 138 | Branch Amp | 748.8818 | - | 100.2432 | 103.061 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_023831LUTHER_8-023832COYOTE_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | 110.8222 | 111.3059 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_023834ELBOW_8-900043Other_132C1 | 138 | 138 | Branch Amp | 748.8818 | 111.8032 | 130.7835 | 125.0924 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_023834ELBOW_8-900100Other_131C1 | 138 | 138 | Branch Amp | 748.8818 | 109.3549 | 129.0709 | 122.7037 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_023849VLMOOR_5-059900LONG_DRAWC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.1492 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_023851CARTRVL_8-023853EILAND_8C1 | 138 | 138 | Branch Amp | 748.8818 | 128.7015 | 138.8721 | 143.7296 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_023875EINSTN_5-059903BEARKATC1 | 138 | 138 | Branch Amp | 748.8818 | 130.4822 | 137.9244 | 153.8857 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_059900LONG_DRAW-059902SAND_BLUFFC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.7245 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_059901GRELTON-059910VOLTAC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.9661 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_059902SAND_BLUFF-059907BERNOULLIC1 | 138 | 138 | Branch Amp | 748.8818 | - | 104.5402 | 107.41 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_059902SAND_BLUFF-076090L_DIVIDE5_1YC1 | 138 | 138 | Branch Amp | 748.8818 | - | 101.0981 | 102.1527 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_059903BEARKAT-059907BERNOULLIC1 | 138 | 138 | Branch Amp | 748.8818 | - | 106.6476 | 108.5825 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | L_131753PC_SOUTH_1_5-131755PC2_SWYD_1_5C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.0114 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | LCRA TSC_BAKERS_CEDACA_DC | 138 | 138 | Branch Amp | 748.8818 | - | 107.1421 | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-1 | 138 | 138 | Branch Amp | 748.8818 | - | 105.251 | 103.5492 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-2 | 138 | 138 | Branch Amp | 748.8818 | - | 104.4639 | 103.1766 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-1 | 138 | 138 | Branch Amp | 748.8818 | - | 105.2496 | 103.549 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-2 | 138 | 138 | Branch Amp | 748.8818 | - | 104.4627 | 103.1765 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | LCRA TSC_NOELK_SNGTR_NOELK_SNGTR2 | 138 | 138 | Branch Amp | 748.8818 | - | 103.7596 | 103.0321 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | LCRA TSC_SCHNDR_BIGHIL_DC | 138 | 138 | Branch Amp | 748.8818 | - | 100.4748 | 101.4085 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | LCRA TSC_SNGTR_SCHDR_SNGTR_SCHDR2 | 138 | 138 | Branch Amp | 748.8818 | - | 103.1296 | 102.5933 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE CKT 2 (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | 104.4358 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | LONGSHORE - PRAIRIELAND 345 KV SUM 2027 - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | 103.3688 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | LUTHER - VEALMOOR 138 KV LINE 2026 SUM - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | 111.1237 | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | LUTHER - VEALMOOR 138 KV LINE 2027 SUM - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | 111.8403 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | MB2726627277 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.1734 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | MCDONALD ROAD - SHIPWRECK & MCDONALD ROAD - PECK TAP 138 KV DCKT LINE (DOUBLE B TO B) B 2025 WIN - FUTURE (PECK TO DRIVER UPDATE) | 138 | 138 | Branch Amp | 748.8818 | - | 102.9853 | 109.832 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | NATURAL DAM - CALF CREEK - BIG SPRING 138 KV SUM 2026 - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | 103.7766 | 106.5987 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | ODESSA EHV - NORTH MCCAMEY 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.5043 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | P1.2_ROUGH_SWITCH_8_Midland East | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.1493 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | PECK - CATCLAW/MCDONALD ROAD 138 KV LINE (DOUBLE B TO B) WIN 2025 - FUTURE | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.5875 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | PECK - MCDONALD ROAD 138 KV LINE (SINGLE B TO B) WIN 2025 - FUTURE | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.0049 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | PRAIRIELAND_AUTO_2 2024 SUMMER - FUTURE | 138 | 138 | Branch Amp | 748.8818 | - | 100.5404 | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | Prairieland-Quartzsand 1 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | - | 100.2746 | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | Prairieland-Quartzsand 2 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.891 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | Prairieland-Quartzsand Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | 103.8712 | 116.54 | 124.2885 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | QUARTZ SAND - POLECAT CREEK 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | 132.8535 | 142.5684 | 148.8447 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | RANGER CAMP - BARBER LAKE SW CKT 2 138 KV SUM 2026 - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.1659 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | - | 110.8677 | 113.4787 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | STECL_10592 | 138 | 138 | Branch Amp | 748.8818 | - | - | 104.4677 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | STECL_4720 | 138 | 138 | Branch Amp | 748.8818 | - | 103.7727 | 103.0771 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | STECL_4721-1 | 138 | 138 | Branch Amp | 748.8818 | - | 105.2511 | 103.5492 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 ( 1334) -> FORSANTA_8 ( 1335) CKT 1 | STECL_4721-2 | 138 | 138 | Branch Amp | 748.8818 | - | 104.464 | 103.1766 | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GLASSCNTYN_8 (1334) -> FORSANTA_8 (1335) CKT 1 | Pre-contingency | 138 | 138 | Amps | 748.8818 | - | - | - | 104.2318 | 120.1835 | 110.2149 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLNHEIGHTS ( 217) -> STERTRD_8 ( 2237) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 119.2791 | 129.5002 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLNHEIGHTS ( 217) -> STERTRD_8 ( 2237) CKT 1 | ENNIS WEST - STERRETT 138 KV (SINGLE B TO B) A REAGOR SPRINGS | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 100.6934 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLNHEIGHTS ( 217) -> STERTRD_8 ( 2237) CKT 1 | L_002237STERTRD_8-002317STERRETT1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 105.9983 | 100.2119 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLNHEIGHTS ( 217) -> STERTRD_8 ( 2237) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 102.0182 | 126.8286 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLNHEIGHTS ( 217) -> STERTRD_8 ( 2237) CKT 1 | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 107.9154 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLNHEIGHTS ( 217) -> STERTRD_8 ( 2237) CKT 1 | L_002305AIRPRD_T8-002307MDLTHTXI1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 104.3758 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLNHEIGHTS ( 217) -> STERTRD_8 ( 2237) CKT 1 | L_002315WAX_PMP2_8-002319WAX_PMP1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 103.8989 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLNHEIGHTS ( 217) -> STERTRD_8 ( 2237) CKT 1 | L_002315WAX_PMP2_8-002320WAX_N_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 104.6517 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLNHEIGHTS ( 217) -> STERTRD_8 ( 2237) CKT 1 | L_002316MG_IND_T8-002319WAX_PMP1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 101.3668 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLNHEIGHTS ( 217) -> STERTRD_8 ( 2237) CKT 1 | L_002320WAX_N_8-002321WAX_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 120.6943 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLNHEIGHTS ( 217) -> STERTRD_8 ( 2237) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 124.428 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GLNHEIGHTS ( 217) -> STERTRD_8 ( 2237) CKT 1 | WAXAHACHI-WAXAHACHI OFC 69KV/ENNIS-STERRETT 138KV (DOUBLE B TO B) A REAGOR | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 104.1053 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | E_B_DAVIS_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 111.5312 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | E_CCEC_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 104.4813 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | E_INGLCOSW_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 108.5899 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | E_LGE_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.9174 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | E_NEDIN_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.9617 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | E_NUECES_B_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 113.2219 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | G_160101B_D_B_DAVIG1UN1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.7297 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | L_008249ANGSTRM7A-008956WHITEPT7AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.522 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.9862 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | L_008455LONHILL7A-008624GRISSOM7AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 106.8039 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | L_008455LONHILL7A-008956WHITEPT7AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.3887 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | L_008458B_DAVIS4A-160105B_DAVIS_1_8C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.7299 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | L_008458B_DAVIS4A-160106B_DAVIS_2_8C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.548 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | L_008624GRISSOM7A-008673RAPTOR7AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 103.237 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | L_080071ZORILLO7A-080076AJO7AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.6057 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | L_080076AJO7A-085000N_SHARPE7AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 103.6364 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | L_080078REFORZAR7A-084555AMBER7AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.4437 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | L_084555AMBER7A-085000N_SHARPE7AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 105.3142 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | M10000254106503-1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 108.4192 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | M10000271115801 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 105.0544 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | M102253112251-1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 103.2403 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | M105311105321 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.9213 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | M105902106102-1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.3664 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | M115851115803 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.6057 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | MB100002711580 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 105.0544 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | MB106501000025-2 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 108.1111 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | MB1158011585 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.6057 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | MBAM-REFORnew | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 105.4699 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GODDARD7A ( 8606) -> KATOEN7A ( 8579) CKT 1 | SAN_PAT_CON | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 108.4805 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GODLEY_8 ( 2281) -> AIRLIQD_P8 ( 2283) CKT 1 | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | 102.5308 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GODLEY_8 ( 2281) -> AIRLIQD_P8 ( 2283) CKT 1 | L_000442RAILPORT-001908VENUSC1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | 103.4893 | - | - | - | -
TAEPTC | COAST | COAST | COAST, COAST | GOHLKE4A ( 8141) -> DACOSTA4A ( 8722) CKT 1 | L_008140JOSLIN4A-008685COBIA4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 107.1494 | 134.3568 | 111.9577 | -
TAEPTC | COAST | COAST | COAST, COAST | GOHLKE4A ( 8141) -> DACOSTA4A ( 8722) CKT 1 | L_008155SANDCRAB4A-008685COBIA4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 104.867 | 132.0524 | 109.6976 | -
TAEPTC | COAST | COAST | COAST, COAST | GOHLKE4A ( 8141) -> DACOSTA4A ( 8722) CKT 1 | L_008155SANDCRAB4A-008723CANGREJO4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 109.1782 | 136.2295 | 113.9587 | -
TAEPTC | COAST | COAST | COAST, COAST | GOHLKE4A ( 8141) -> DACOSTA4A ( 8722) CKT 1 | M128607128702-1_MODIFIED_BY_MZ | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 108.536 | 137.1274 | 113.0135 | -
TAEPTC | COAST | COAST | COAST, COAST | GOHLKE4A ( 8141) -> DACOSTA4A ( 8722) CKT 1 | MB1287012860-2_MODIFIED_BY_MZ | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 109.706 | 138.6242 | 114.0599 | -
TONCOR | WEST | WEST | WEST, WEST | GOLDENSW_8 ( 1067) -> SUN_8 ( 1064) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 104.8405 | - | -
TONCOR | WEST | WEST | WEST, WEST | GOLDENSW_8 ( 1067) -> SUN_8 ( 1064) CKT 1 | SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 1 & SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 114.6887 | 103.3054 | -
TONCOR | WEST | WEST | WEST, WEST | GOLDENSW_8 ( 1067) -> SUN_8 ( 1064) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 120.9196 | 108.4105 | -
TGAR,TLCRA | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GPL_NEVILLSW ( 844) -> L_NORTMC5_1Y (76000) CKT 1 | SAND LAKE - SOLSTICE 345 KV DCKT LINE (DOUBLE B TO B) WIN 2027 - FUTURE | 345 | 345 | Branch Amp | 2911.853 | - | - | 105.5588 | - | 103.0829 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GRANDPR1_8 ( 2262) -> FSHCRK2_8 (12491) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | 124.6505 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GRANDPR1_8 ( 2262) -> FSHCRK2_8 (12491) CKT 1 | CEDAR HILL SW 345-138 KV AUTO #1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | 108.5853 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GRANDPR1_8 ( 2262) -> FSHCRK2_8 (12491) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | 125.6681 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GRANDPR1_8 ( 2262) -> FSHCRK2_8 (12491) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | 100.5807 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GRANDVIEW ( 436) -> CONLEY ( 432) CKT 1 | L_000394CONCORD8-000398JOSHUAC1 | 138 | 138 | Branch Amp | 1112.8635 | - | - | - | 101.8326 | 107.2329 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GRANDVIEW ( 436) -> CONLEY ( 432) CKT 1 | L_000398JOSHUA-000399CROWLEYC1 | 138 | 138 | Branch Amp | 1112.8635 | - | - | - | - | 102.3512 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | GREENLK2A ( 8159) -> WEAVERRD2A ( 8572) CKT 1 | M100101100271-1A | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.7124 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | GREENLK2A ( 8159) -> WEAVERRD2A ( 8572) CKT 1 | MB1002710010-1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.0813 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GREGORY2A ( 8421) -> ARANSASP2A ( 8427) CKT 1 | L_008422I_DUPSW4A-008425INGLESID4AC1 | 69 | 69 | Branch Amp | 510.4111 | - | - | 107.6533 | 118.1872 | 134.6041 | 116.7028 | -
TAEPTC,TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GRETA2A ( 8409) -> REFUGIO2A ( 8410) CKT 1 | L_008144SEADRFTC4A-008189TUNGSTEN4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.5782 | 145.1504 | - | -
TAEPTC,TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GRETA2A ( 8409) -> REFUGIO2A ( 8410) CKT 1 | L_008144SEADRFTC4A-080065MELNCRK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.2629 | 144.8223 | - | -
TAEPTC,TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GRETA2A ( 8409) -> REFUGIO2A ( 8410) CKT 1 | L_008412REFUGIO4A-008813QUINTANA4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 108.5062 | - | -
TAEPTC,TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GRETA2A ( 8409) -> REFUGIO2A ( 8410) CKT 1 | L_008813QUINTANA4A-080065MELNCRK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 112.3969 | - | -
TAEPTC,TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GRETA2A ( 8409) -> REFUGIO2A ( 8410) CKT 1 | L10011206 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 108.4922 | - | -
TAEPTC,TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GRETA2A ( 8409) -> REFUGIO2A ( 8410) CKT 1 | MB1291012930 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 136.5758 | - | -
TAEPTC,TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GRETA2A ( 8409) -> REFUGIO2A ( 8410) CKT 1 | MB1293012910 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.8018 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GRETA2A ( 8409) -> REFUGIO2A ( 8410) CKT 1 | T_008410REFUGIO2A-008412REFUGIO4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 108.3654 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GRIFFTH_P8 ( 1905) -> FORBESRD_8 ( 1303) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | 108.3298 | 123.3123 | 146.967 | 184.592 | 197.75 | 168.1751 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GRIFFTH_P8 ( 1905) -> FORBESRD_8 ( 1303) CKT 1 | BEPC_306 | 138 | 138 | Branch Amp | 861.8416 | 151.8316 | 198.7834 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GRIFFTH_P8 ( 1905) -> FORBESRD_8 ( 1303) CKT 1 | CLEBURNE-BURLESON 138 KV (SINGLE B TO B) B WILSHIRE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3015 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GRIFFTH_P8 ( 1905) -> FORBESRD_8 ( 1303) CKT 1 | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | 138 | Branch Amp | 861.8416 | 125.2012 | 190.3952 | 205.284 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GRIFFTH_P8 ( 1905) -> FORBESRD_8 ( 1303) CKT 1 | L_000442RAILPORT-001908VENUSC1 | 138 | 138 | Branch Amp | 861.8416 | 127.4365 | 190.6568 | 209.5021 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GRIFFTH_P8 ( 1905) -> FORBESRD_8 ( 1303) CKT 1 | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | 138 | Branch Amp | 861.8416 | 151.8364 | 198.994 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | GRIFFTH_P8 ( 1905) -> FORBESRD_8 ( 1303) CKT 1 | L_002210JOSHUA_8-002279CLEBRNSW_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4192 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GRISSOM7A ( 8624) -> LONHILL7A ( 8455) CKT 1 | L_008249ANGSTRM7A-008956WHITEPT7AC1 | 345 | 345 | Branch Amp | 1989.7664 | - | - | - | - | 112.5099 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GRISSOM7A ( 8624) -> LONHILL7A ( 8455) CKT 1 | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | 345 | Branch Amp | 1989.7664 | - | - | - | - | 104.587 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GRISSOM7A ( 8624) -> LONHILL7A ( 8455) CKT 1 | L_008455LONHILL7A-008956WHITEPT7AC1 | 345 | 345 | Branch Amp | 1989.7664 | - | - | - | - | 105.7521 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GRISSOM7A ( 8624) -> LONHILL7A ( 8455) CKT 1 | L_008579KATOEN7A-008606GODDARD7AC1 | 345 | 345 | Branch Amp | 1989.7664 | - | - | - | - | 100.0531 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GRISSOM7A ( 8624) -> LONHILL7A ( 8455) CKT 1 | M102253112251-1 | 345 | 345 | Branch Amp | 1989.7664 | - | - | - | - | 117.5039 | - | -
TCNPE | COAST | COAST | COAST, COAST | GRNBYU__B345 (40700) -> KING____B345 (40900) CKT 74 | L_040700GRNBYU__B345-040900KING____B345C75 | 345 | 345 | Branch Amp | 1807.3572 | - | - | - | - | 116.8109 | 107.2063 | -
TCNPE | COAST | COAST | COAST, COAST | GRNBYU__B345 (40700) -> KING____B345 (40900) CKT 75 | L_040700GRNBYU__B345-040900KING____B345C74 | 345 | 345 | Branch Amp | 1807.3572 | - | - | - | - | 116.8109 | 107.2063 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GULCH7A ( 8704) -> CANDELA7A ( 8709) CKT 1 | MB10000841000093-1A | 345 | 345 | Branch Amp | 1914.4597 | - | - | 112.4561 | - | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GULCH7A ( 8704) -> CANDELA7A ( 8709) CKT 1 | P7/C5-SHRY-3 | 345 | 345 | Branch Amp | 1914.4597 | - | - | 109.4257 | - | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | GULCH7A (8704) -> CANDELA7A (8709) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1710.2954 | - | - | - | 205.0222 | 203.3227 | 195.4638 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GUNSIGHT_8 ( 1360) -> HIGHPLAIN_P8 ( 1396) CKT 1 | BIG SPRING - BUZZARD DRAW 138 KV (SINGLE B TO B) 2021 WIN - FUTURE | 138 | 138 | Branch Amp | 502.0437 | - | - | - | 101.1666 | 106.1153 | 105.4031 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GUNSIGHT_8 ( 1360) -> HIGHPLAIN_P8 ( 1396) CKT 1 | L_001322BIGSPRIG_8-001358KNOTT_8C1 | 138 | 138 | Branch Amp | 502.0437 | - | - | - | - | 104.4635 | 103.7434 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GUNSIGHT_8 ( 1360) -> HIGHPLAIN_P8 ( 1396) CKT 1 | L_001355BUZZDRAW_8-001358KNOTT_8C1 | 138 | 138 | Branch Amp | 502.0437 | - | - | 100.2501 | 102.0073 | 107.029 | 106.3085 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GUNSIGHT_8 ( 1360) -> HIGHPLAIN_P8 ( 1396) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 502.0437 | - | - | - | - | 100.5803 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | GUNSIGHT_8 ( 1360) -> HIGHPLAIN_P8 ( 1396) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 502.0437 | - | 112.8695 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HANEY ( 213) -> NAVARRO1_8 ( 3478) CKT 1 | HILLSBORO-ASH CREEK 138 KV (SINGLE B TO B) B | 138 | 138 | Branch Amp | 338.8795 | 104.0548 | - | 108.2774 | 109.5484 | 120.5091 | 121.0018 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HANEY ( 213) -> NAVARRO1_8 ( 3478) CKT 1 | L_000234CHATT-003352PECANST_8C1 | 138 | 138 | Branch Amp | 338.8795 | 102.4227 | - | 106.6634 | 107.9062 | 118.8674 | 119.3639 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HANEY ( 213) -> NAVARRO1_8 ( 3478) CKT 1 | L_000234CHATT-003522HILLBORO1_8C1 | 138 | 138 | Branch Amp | 338.8795 | - | - | - | - | 109.7549 | 110.2472 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HANEY ( 213) -> NAVARRO1_8 ( 3478) CKT 1 | L_003352PECANST_8-003473ASHCREEK_8C1 | 138 | 138 | Branch Amp | 338.8795 | 104.0623 | - | 108.2892 | 109.5551 | 120.5098 | 121.007 | -
TAEPTN | WEST | WEST | WEST, WEST | HARGROVE4A ( 6648) -> PUMPJACK4A (60374) CKT 1 | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 107.8826 | - | -
TAEPTN | WEST | WEST | WEST, WEST | HARGROVE4A ( 6648) -> PUMPJACK4A (60374) CKT 1 | L_006536BIGLAKE4B-060414OWLS4AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 106.1076 | - | -
TAEPTN | WEST | WEST | WEST, WEST | HARGROVE4A ( 6648) -> PUMPJACK4A (60374) CKT 1 | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 111.1184 | 101.5445 | -
TAEPTN | WEST | WEST | WEST, WEST | HARGROVE4A ( 6648) -> PUMPJACK4A (60374) CKT 1 | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | 100.873 | 112.8595 | 103.2486 | -
TAEPTN | WEST | WEST | WEST, WEST | HARGROVE4A ( 6648) -> PUMPJACK4A (60374) CKT 1 | L_060723CROSSOVE4A-060728PALOUSE4AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 103.7714 | - | -
TAEPTN | WEST | WEST | WEST, WEST | HARGROVE4A ( 6648) -> PUMPJACK4A (60374) CKT 1 | L_060723CROSSOVE4A-076032L_NORTMC8_1YC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 103.9059 | - | -
TAEPTN | WEST | WEST | WEST, WEST | HARGROVE4A ( 6648) -> PUMPJACK4A (60374) CKT 1 | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | 102.641 | 114.8641 | 105.2106 | -
TAEPTN | WEST | WEST | WEST, WEST | HARGROVE4A ( 6648) -> PUMPJACK4A (60374) CKT 1 | L_076011L_TWINBU8_1Y-900117Other_90_SOC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 103.5915 | - | -
TAEPTN | WEST | WEST | WEST, WEST | HARGROVE4A ( 6648) -> PUMPJACK4A (60374) CKT 1 | L_900110Other_86_MO-900117Other_90_SOC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 101.5678 | - | -
TAEPTN | WEST | WEST | WEST, WEST | HARGROVE4A ( 6648) -> PUMPJACK4A (60374) CKT 1 | L2020944-A | 138 | 138 | Branch Amp | 631.7383 | - | - | - | 100.8137 | 112.7859 | 103.1948 | -
TAEPTN | WEST | WEST | WEST, WEST | HARGROVE4A ( 6648) -> PUMPJACK4A (60374) CKT 1 | L2020944-B | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 103.7653 | - | -
TAEPTN | WEST | WEST | WEST, WEST | HARGROVE4A ( 6648) -> PUMPJACK4A (60374) CKT 1 | LCRA TSC_BAKERS_CEDACA_DC | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 101.9784 | - | -
TAEPTN | WEST | WEST | WEST, WEST | HARGROVE4A ( 6648) -> PUMPJACK4A (60374) CKT 1 | T_006535BIGLAKE4A-006536BIGLAKE4BC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 104.0078 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HARK_HTS1_8 ( 3618) -> KILLTAFD_8 ( 3616) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 106.3994 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HARKHTS_S18 ( 3633) -> KILL_SS__8 ( 3423) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 117.6101 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | BEPC_005_1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 102.6582 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | BEPC_006 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 103.4114 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | BEPC_114 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 105.7779 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | BEPC_242 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 102.3836 | 126.2927 | 117.2152 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | BEPC_243 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 114.9199 | 106.3276 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | BEPC_458 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.3233 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | L_000501HILLTOP8-000508RIKERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 113.4905 | 105.2598 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | L_000508RIKER-000516ZIONHILLC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 113.4883 | 105.2578 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | L_000516ZIONHILL-000543SWIMMERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 114.8433 | 106.5484 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | L_000541RENO-000595KEETERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 100.6853 | 124.6654 | 115.515 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | L_000543SWIMMER-000588WILLOWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 115.4436 | 107.1259 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | L_000579JCKCNTY8-000580WSTBROOKC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 115.7737 | 107.4432 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | L_000579JCKCNTY8-000600BRIDGEPORTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 116.7605 | 108.0396 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | L_000579JCKCNTY8-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 102.2171 | 126.277 | 117.0608 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | L_000580WSTBROOK-000588WILLOWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 115.5579 | 107.2362 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | L_000590PERCHHILL-000600BRIDGEPORTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 114.0508 | 105.3799 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | L_000590PERCHHILL-000608CRAFTONC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 111.7835 | 103.1456 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | L_000595KEETER-000596COTTONDALEC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 101.2383 | 125.2489 | 116.0769 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | L_000596COTTONDALE-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 102.2185 | 126.2786 | 117.0619 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | L_000608CRAFTON-000620BOWIE8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 110.6921 | 102.0724 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIDEOUT ( 571) -> WISECNTY ( 570) CKT 1 | WISE COUNTY (BEC) - ALVORD/BRIDGEPORT(BEC) (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 102.616 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIGHPOINT ( 439) -> LILLIAN8 ( 419) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 962.2503 | - | - | - | - | 101.7206 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIGHPOINT ( 439) -> LILLIAN8 ( 419) CKT 1 | L_000394CONCORD8-000398JOSHUAC1 | 138 | 138 | Branch Amp | 962.2503 | - | - | 102.8508 | 110.076 | 116.2567 | 103.9733 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIGHPOINT ( 439) -> LILLIAN8 ( 419) CKT 1 | L_000398JOSHUA-000399CROWLEYC1 | 138 | 138 | Branch Amp | 962.2503 | - | - | - | 104.7254 | 110.6817 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIGHPOINT ( 439) -> LILLIAN8 ( 419) CKT 1 | L_000399CROWLEY-000405EGANC1 | 138 | 138 | Branch Amp | 962.2503 | - | - | - | - | 104.9317 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HIGHPOINT ( 439) -> LILLIAN8 ( 419) CKT 1 | L_000405EGAN-000412BURLESONC1 | 138 | 138 | Branch Amp | 962.2503 | - | - | - | - | 101.7583 | - | -
TCNPE | COAST | COAST | COAST, COAST | HILAND08T1_8 (40811) -> PSARCO_POI8A (41300) CKT 08 | L_040390CROSBY_B138A-040890DANEK__POI_8C&1-MS | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 100.9441 | 101.5401 | 100.3429 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 1 | Branch MVA | 104 | - | - | 105.2056 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | BEPC_108 | 138 | 1 | Branch MVA | 104 | - | - | 101.049 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | L_000228PEORIA-000243WHITNEYSWC1 | 138 | 1 | Branch MVA | 104 | - | - | 101.1674 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | L_000237BLANTON-888875THRESLR_POIC1 | 138 | 1 | Branch MVA | 104 | - | - | 110.9044 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | L_000237BLANTON-888889MIDPOINT_POIC1 | 138 | 1 | Branch MVA | 104 | - | - | 109.8516 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | 1 | Branch MVA | 104 | - | - | 105.3358 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | L_000442RAILPORT-001908VENUSC1 | 138 | 1 | Branch MVA | 104 | - | - | 105.6378 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | L_002279CLEBRNSW_8-002290CLEBRN_8C1 | 138 | 1 | Branch MVA | 104 | - | - | 101.1789 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | L_002279CLEBRNSW_8-002294KEENE_8C1 | 138 | 1 | Branch MVA | 104 | - | - | 104.789 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | L_002290CLEBRN_8-002291CLEBRN_W_8C1 | 138 | 1 | Branch MVA | 104 | - | - | 106.7794 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | L_002291CLEBRN_W_8-037810TNHILL_CO_8C1 | 138 | 1 | Branch MVA | 104 | - | - | 111.5134 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | L_002294KEENE_8-002297ALVARADO1_8C1 | 138 | 1 | Branch MVA | 104 | - | - | 100.6297 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | L_003518BLUMPUMP1_8-037810TNHILL_CO_8C1 | 138 | 1 | Branch MVA | 104 | - | - | 112.5772 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | L_888875THRESLR_POI-003522HILLBORO1_8C1 | 138 | 1 | Branch MVA | 104 | - | - | 103.379 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | L_888889MIDPOINT_POI-003518BLUMPUMP1_8C1 | 138 | 1 | Branch MVA | 104 | - | - | 112.8244 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-1-2 | 138 | 1 | Branch MVA | 104 | - | - | 102.9559 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-1 | 138 | 1 | Branch MVA | 104 | - | - | 109.36 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-2 | 138 | 1 | Branch MVA | 104 | - | - | 102.9559 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | NEW-HILLSBORO-CLEBURNE_SW_8 (SINGLE B TO B )-1-1 | 138 | 1 | Branch MVA | 104 | - | - | 109.36 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | NEW-SAM - FOURBROTHERS/TRADINGHOUSE_5 (DOUBLE B TO B)-1 | 138 | 1 | Branch MVA | 104 | - | - | 102.0401 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | NEW-SAM - FOURBROTHERS/TRADINGHOUSE_5 (DOUBLE B TO B)-2 | 138 | 1 | Branch MVA | 104 | - | - | 102.2336 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 138 | 1 | Branch MVA | 104 | - | - | 103.1057 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | THRESLR_CON | 138 | 1 | Branch MVA | 104 | - | - | 104.4846 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 ( 3522) -> HILLBSTR (500124) CKT 1 | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | 138 | 1 | Branch MVA | 104 | - | - | 102.9015 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_8 (3522) -> HILLBSTR (500124) CKT 1 | Pre-contingency | 138 | 1 | MVA | 104 | - | - | - | 103.2994 | 111.3381 | 102.8227 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBORO1_9 (3523) -> HILLBSTR (500124) CKT 1 | Pre-contingency | 69 | 1 | MVA | 104 | - | - | - | 102.9221 | 110.613 | 102.2642 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 69 | 1 | Branch MVA | 104 | - | - | 103.1432 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | BEPC_108 | 69 | 1 | Branch MVA | 104 | - | - | 101.049 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | L_000228PEORIA-000243WHITNEYSWC1 | 69 | 1 | Branch MVA | 104 | - | - | 101.1674 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | L_000237BLANTON-888875THRESLR_POIC1 | 69 | 1 | Branch MVA | 104 | - | - | 110.559 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | L_000237BLANTON-888889MIDPOINT_POIC1 | 69 | 1 | Branch MVA | 104 | - | - | 109.5385 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | L_000442RAILPORT-001303FORBESRD_8C1 | 69 | 1 | Branch MVA | 104 | - | - | 101.3191 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | L_000442RAILPORT-001908VENUSC1 | 69 | 1 | Branch MVA | 104 | - | - | 101.544 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | L_002279CLEBRNSW_8-002290CLEBRN_8C1 | 69 | 1 | Branch MVA | 104 | - | - | 100.9879 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | L_002279CLEBRNSW_8-002294KEENE_8C1 | 69 | 1 | Branch MVA | 104 | - | - | 103.6923 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | L_002290CLEBRN_8-002291CLEBRN_W_8C1 | 69 | 1 | Branch MVA | 104 | - | - | 106.4062 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | L_002291CLEBRN_W_8-037810TNHILL_CO_8C1 | 69 | 1 | Branch MVA | 104 | - | - | 111.0378 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | L_002294KEENE_8-002297ALVARADO1_8C1 | 69 | 1 | Branch MVA | 104 | - | - | 100.6052 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | L_003518BLUMPUMP1_8-037810TNHILL_CO_8C1 | 69 | 1 | Branch MVA | 104 | - | - | 112.0682 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | L_888875THRESLR_POI-003522HILLBORO1_8C1 | 69 | 1 | Branch MVA | 104 | - | - | 103.263 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | L_888889MIDPOINT_POI-003518BLUMPUMP1_8C1 | 69 | 1 | Branch MVA | 104 | - | - | 112.3074 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-1-2 | 69 | 1 | Branch MVA | 104 | - | - | 102.7712 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-1 | 69 | 1 | Branch MVA | 104 | - | - | 108.9813 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-2 | 69 | 1 | Branch MVA | 104 | - | - | 102.7712 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | NEW-HILLSBORO-CLEBURNE_SW_8 (SINGLE B TO B )-1-1 | 69 | 1 | Branch MVA | 104 | - | - | 108.9813 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | NEW-SAM - FOURBROTHERS/TRADINGHOUSE_5 (DOUBLE B TO B)-1 | 69 | 1 | Branch MVA | 104 | - | - | 101.0006 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | NEW-SAM - FOURBROTHERS/TRADINGHOUSE_5 (DOUBLE B TO B)-2 | 69 | 1 | Branch MVA | 104 | - | - | 101.177 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 69 | 1 | Branch MVA | 104 | - | - | 101.9897 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | THRESLR_CON | 69 | 1 | Branch MVA | 104 | - | - | 104.3385 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLBSTR (500124) -> HILLBORO1_9 ( 3523) CKT 1 | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | 69 | 1 | Branch MVA | 104 | - | - | 101.7778 | - | - | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 108.9073 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 107.34 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 104.8984 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | DVCPA1C21B_1 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 108.0185 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | DVCPA1C21B_2 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 104.2231 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | E5DVA1C1_1_B | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | 119.3284 | - | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | E5DVA1C1_1_B_1 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | 109.7481 | - | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | E5DVA1C1_1_B_2 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | 103.5471 | - | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | G_888870BTTM_GRSS_POIUS1 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 106.2587 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 115.3194 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 105.7576 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 108.1333 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 102.3252 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | L_005380SHAULA-005915SO_TEX__345AC1 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 102.3838 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 101.698 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 109.9284 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 101.5251 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | P7-1_E1>>T1827GX_ERC | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | 100.437 | - | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | P7-1_E1>>T1839X1_ERC | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 104.0936 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | P7-1_E1>>T1839X2_ERC | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 107.8906 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | P7-1_E1>>T2764Y_ERCa | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 103.862 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | P7-1_E1>>T3944Z_ERC | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 104.1446 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | STP - HOUDINI & STP - SHAULA | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 103.7254 | - | -
TAEN,TCNPE | SOUTH_CE | COAST | SOUTH_CE, COAST | HILLJE__B345 (44200) -> BTTM_GRSS_POI (888870) CKT 1 | WAP - HOUDINI & STP - SHAULA | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 101.1974 | - | -
TCNPE,TAEN | COAST | COAST | COAST, COAST | HILLJE__B345 (44200) -> SO_TEX__345A ( 5915) CKT 1 | L_005915SO_TEX__345A-043990ELMATO_POI_5C64 | 345 | 345 | Branch Amp | 2008.1747 | - | - | - | - | 104.057 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLTOP8 ( 501) -> VEALJNCTN ( 534) CKT 1 | BEPC_242 | 138 | 138 | Branch Amp | 836.7394 | - | - | - | - | 108.4758 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLTOP8 ( 501) -> VEALJNCTN ( 534) CKT 1 | L_000541RENO-000595KEETERC1 | 138 | 138 | Branch Amp | 836.7394 | - | - | - | - | 107.4393 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLTOP8 ( 501) -> VEALJNCTN ( 534) CKT 1 | L_000579JCKCNTY8-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 836.7394 | - | - | - | - | 109.481 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLTOP8 ( 501) -> VEALJNCTN ( 534) CKT 1 | L_000595KEETER-000596COTTONDALEC1 | 138 | 138 | Branch Amp | 836.7394 | - | - | - | - | 108.1754 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | HILLTOP8 ( 501) -> VEALJNCTN ( 534) CKT 1 | L_000596COTTONDALE-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 836.7394 | - | - | - | - | 109.4546 | - | -
TCNPE | COAST | COAST | COAST, COAST | HOFMAN_X02B8 (42810) -> BASF___POI_8 (42150) CKT 02 | L_042370DAMON__S89_8-043380W_COL__POI_8C&1-MS | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 100.3386 | -
TCNPE | COAST | COAST | COAST, COAST | HOFMAN_X02B8 (42810) -> BASF___POI_8 (42150) CKT 02 | L_888852LIATRIS_POI-044010W_A_P__POI8AC02 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 107.3563 | -
TCNPE | COAST | COAST | COAST, COAST | HOFMAN_X02B8 (42810) -> BASF___POI_8 (42150) CKT 02 | P1-2_(42980-44010-02)-2 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 107.3563 | -
TCNPE | COAST | COAST | COAST, COAST | HOFMAN_X02B8 (42810) -> BASF___POI_8 (42150) CKT 02 | P7-1_E1>>T1827K | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 100.3542 | -
TCNPE | COAST | COAST | COAST, COAST | HOFMAN_X02B8 (42810) -> BASF___POI_8 (42150) CKT 02 | P7-1_E1>>T2682EX1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 103.2387 | 120.2989 | -
TCNPE | COAST | COAST | COAST, COAST | HOFMAN_X02B8 (42810) -> BASF___POI_8 (42150) CKT 02 | P7-1_E1>>T2682EX2 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 104.3954 | 121.4279 | -
TCNPE | COAST | COAST | COAST, COAST | HOFMAN_X02B8 (42810) -> BASF___POI_8 (42150) CKT 02 | P7-1_E1>>T2682GY1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 104.5123 | 121.543 | -
TCNPE | COAST | COAST | COAST, COAST | HOFMAN_X02B8 (42810) -> BASF___POI_8 (42150) CKT 02 | P7-1_E1>>T2682GY2 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 104.5116 | 121.5423 | -
TCNPE | COAST | COAST | COAST, COAST | HOFMAN_X02B8 (42810) -> BASF___POI_8 (42150) CKT 02 | P7-1_E1>T2682DX | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 112.0456 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HOGCREEK_5 ( 3704) -> LITTLEPOND_5 ( 3377) CKT 1 | L_003687BELL_E_5-003705BRANGUS_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 106.645 | -
TWETR , TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1725.3568 | - | - | - | - | 110.7193 | 103.7121 | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | BAS_RANCH_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.6126 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | BOWMAN - BYRD\RILEY (AEP) 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.084 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | C5-WETT-2_A-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0332 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | C5-WETT-2_A-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 103.274 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | C5-WETT-2_B-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0604 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | Cattleman-Longshore Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.9141 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | CHINA GROVE SW - AEP PAINT CREEK 138 KV & GRAHAM SES - TONKAWA/COOKFIELD/LONGCREEK 345 KV (DOUBLE B TO B) 2019 SUM - FUTURE-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.3147 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | CLY_PHNT1P7F1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.9337 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | CLY_PHNT1P7F1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.3911 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | CLY_PHNT2P7F1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.17 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | CLY_PHNT2P7F1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.62 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | DERMOTT - BLUFF CREEK SW & DERMOTT - ENNIS CREEK 138 KV (DOUBLE B TO B) 2023 WIN - FUTURE | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.5202 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | DERMOTT - COTTONWOOD/MHOS (WETT) CKT 1 345 KV (SINGLE B TO B) C | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 115.7078 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | E_OECCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.8112 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | E_OECCS_CC2_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.8151 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | G_010012METEOR_5US1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.4142 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | G_888839BAS_RANCH_POIUC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.6386 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | G_888851TRIFECTA_POIUN1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.2815 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0656 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.2529 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | KRUM WEST - RILEY A 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.3171 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0292 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_006076FOXTAIL7A-060791PERIGEE7AC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.1589 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_006235ABMULCW7A-888860RUBICONALPHA_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.11 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_011270DOGHOUSE_5-023876CLEARFRK_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.1477 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_011305DERMOTT_5-011318SCURCNTYS_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.1345 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_011305DERMOTT_5-011318SCURCNTYS_5C2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.1345 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_023901OZARKTRAIL_5-023914TULECNYN_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.9432 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_023913KRESS_5-023914TULECNYN_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.4706 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_023914TULECNYN_5-079001CROSS_W1C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.3226 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_023914TULECNYN_5-079003CROSS_W2C2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.3577 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_023920ABERNATH_5-023922WHITERVR_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.6731 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_023922WHITERVR_5-059904COTTONWOODC1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.2869 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_023922WHITERVR_5-059904COTTONWOODC1-3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.6941 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_023922WHITERVR_5-059904COTTONWOODC2-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.2921 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_023922WHITERVR_5-059904COTTONWOODC2-3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.7019 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_059904COTTONWOOD-060006HYPERION7AC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.534 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_059906LONGDRAW_138-134145JUNO_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.7745 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_059906LONGDRAW_138-134342LGDRAW_S8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0999 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_059908NOVA_345-059911MHOSC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.2273 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_059908NOVA_345-059911MHOSC2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.2273 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_060501TESLA7A-061616FOURCORNERSC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.6023 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_060501TESLA7A-079002CROSS_E1C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.3302 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_060501TESLA7A-079004CROSS_E2C2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.3653 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_060504TESLA7B-060511SALVARE7AC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.5892 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_060504TESLA7B-079491LINE_REACTR1C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0514 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_060504TESLA7B-079492LINE_REACTR2C2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0589 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_060507PENDULO7A-060514CLEARCRO7BC1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.1404 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_060507PENDULO7A-060514CLEARCRO7BC1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.3344 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_060507PENDULO7A-888883QUANT_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.1405 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_068001CLAYTON_345-068014OPENSKYC2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.1405 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_888860RUBICONALPHA_POI-060791PERIGEE7AC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.7643 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_888882BUZIOS_POI-059904COTTONWOODC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.2869 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_888882BUZIOS_POI-059904COTTONWOODC2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.2921 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L_888883QUANT_POI-060514CLEARCRO7BC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.3345 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L2025500 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.337 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L2025501 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.3721 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L2025502 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0496 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L2025503 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0571 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | L2920902 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.8842 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | LONGCREEK SW - COOK FIELD ROAD SW & LONGCREEK SW - GRAHAM SW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0105 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | MALDIVES_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.1907 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | MB210140210145-BAAA-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.893 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | MB210140210145-BAAA-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 103.2591 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | MB210140210145-BAAB-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 106.2156 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | MB210140210145-BABB | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.8269 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | MB210140210145-BBAA-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 103.8596 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | MB210140210145-BBAB-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.9041 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | MB210140210145-BBAB-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.262 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | MB2551220840-2A-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.1007 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | MB2551220840-2A-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.2952 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | MB2552825529 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 109.4887 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | New Meinan - Sweeteast and BitterCreek 345kV Double | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0188 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | OGALLALA-OZARK TRAIL/KRESS (DOUBLE B TO B) SUM 2024 - FUTURE | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.5449 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | OZARK TRAIL-TULECANYON & OGALLALA-KRESS 138 KV (DOUBLE B TO B) SUM 2024 - FUTURE | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 105.2045 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | P1-2/B2-CTT-17 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0496 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | P1-2/B2-CTT-18 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0571 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | P1-2/B2-CTT-4 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.3721 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | P7/C5-ONCOR-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.4827 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | P7-1/C5-CTT-14 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 103.9993 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | P7-WETT-3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.389 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | P7-WETT-4 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 110.9884 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.3027 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | RILEY - TESLA & JIM TREECE - RILEY | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.8383 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | RILEY - TESLA & SALVARE - JIM TREECE | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.9852 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | RILEY - TESLA & TESLA - SALVARE | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 106.9964 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | RUBICONALPHA_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.8802 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | SCUR_CLY_P7 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 103.4123 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 1 & SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 2 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 110.8147 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | TESLA - EDITH CLARKE & TESLA - FOUR CORNERS | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.3097 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | TRIFECTA_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.2795 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | TULECANYON-OZARK TRAIL/KRESS (DOUBLE B TO B) SUM 2024 - FUTURE | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 110.3425 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | TULECANYON-TESLA (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 114.4383 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | TULECANYON-TESLA1 (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.337 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | WHITERIVER-COTTONWOOD (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 116.3159 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | WHITERIVER-COTTONWOOD (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 120.4649 | - | - | -
TWETR,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOLLY_POI (888856) -> LONG_DRAW (59900) CKT 1 | WHITERIVER-COTTONWOOD (DOUBLE B TO B)-3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 116.0674 | - | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HOLMAN ( 9073) -> CISTERN ( 9043) CKT 1 | AEN_FPP-HO¦LY | 345 | 345 | Branch Amp | 1924.5007 | - | - | - | - | 112.8181 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HOLMAN ( 9073) -> CISTERN ( 9043) CKT 1 | AEN_LP-AU¦DL_2013 | 345 | 345 | Branch Amp | 1924.5007 | - | - | - | - | 113.111 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HOLMAN ( 9073) -> CISTERN ( 9043) CKT 1 | AEN_P7 FPP-LP.DC_1 | 345 | 345 | Branch Amp | 1924.5007 | - | - | - | - | 106.7365 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HOLMAN ( 9073) -> CISTERN ( 9043) CKT 1 | AEN_P7 FPP-LP.DC_2 | 345 | 345 | Branch Amp | 1924.5007 | - | - | - | - | 101.484 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HOLMAN ( 9073) -> CISTERN ( 9043) CKT 1 | L_007055L_FPPYD25_1Y-009073HOLMANC1 | 345 | 345 | Branch Amp | 1924.5007 | - | - | - | - | 109.8145 | - | -
TLCRA,TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HOLMAN ( 9073) -> L_FPPYD25_1Y ( 7055) CKT 1 | AEN_LY-FPP¦CIS | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 109.128 | - | -
TLCRA,TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HOLMAN ( 9073) -> L_FPPYD25_1Y ( 7055) CKT 1 | L_009043CISTERN-009073HOLMANC1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 110.2674 | - | -
TLCRA,TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HOLMAN ( 9073) -> L_FPPYD25_1Y ( 7055) CKT 1 | L_009043CISTERN-009074LYTTON5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 121.406 | - | -
TAEN , TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HOLMAN (9073) -> BTTM_GRSS_POI (888870) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1807.3572 | - | - | - | - | 136.7919 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOWD2599_8 (11325) -> BEALSCRK_8 (11331) CKT 1 | BIG SPRING WEST SWITCH - BIG SPRING 138 KV WIN 2025 - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 1648.3767 | 100.9071 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOWD2599_8 (11325) -> BEALSCRK_8 (11331) CKT 1 | L_001322BIGSPRIG_8-010044STEER_8C1 | 138 | 138 | Branch Amp | 1648.3767 | 111.8303 | - | 102.588 | 103.2658 | 106.443 | 103.5171 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HOWD2599_8 (11325) -> BEALSCRK_8 (11331) CKT 1 | L_010044STEER_8-011316BSPGWSW_8C1 | 138 | 138 | Branch Amp | 1648.3767 | 111.8297 | - | 102.5875 | 103.2659 | 106.4423 | 103.5171 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HRSHOEDR1_8 (11172) -> HRSHOEDR1_3 (11171) CKT 1 | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | 38 | Branch MVA | 250 | - | - | - | - | 102.7412 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HRSHOEDR1_8 (11172) -> HRSHOEDR1_3 (11171) CKT 1 | L_001086BARSTOWNW_8-011105PECONE_P8C1 | 138 | 38 | Branch MVA | 250 | - | - | - | - | 103.1682 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HRSHOEDR1_8 (11172) -> HRSHOEDR1_3 (11171) CKT 1 | L_011080THRMIDRW_8-011083RIVERTON_8C1 | 138 | 38 | Branch MVA | 250 | - | - | - | - | 101.9609 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HRSHOEDR1_8 (11172) -> HRSHOEDR1_3 (11171) CKT 1 | L_011180ARYOBLUFF_T8-011199RDRUNNER_T8C1 | 138 | 38 | Branch MVA | 250 | - | - | - | - | 100.9253 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HRSHOEDR1_8 (11172) -> HRSHOEDR1_3 (11171) CKT 1 | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | 38 | Branch MVA | 250 | - | - | - | - | 102.5371 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HRSHOEDR1_8 (11172) -> HRSHOEDR1_3 (11171) CKT 1 | L_011183TUNSTLL_8-011199RDRUNNER_T8C1 | 138 | 38 | Branch MVA | 250 | - | - | - | 103.9899 | 101.5899 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HRSHOEDR1_8 (11172) -> HRSHOEDR1_3 (11171) CKT 1 | RIVERTON - THREE MILE DRAW/HORSESHOE SPRINGS DCKT 138 KV SUM 2022 - FUTURE (DOUBLE B TO B) C | 138 | 38 | Branch MVA | 250 | - | - | - | - | 101.6134 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | HRSHOEDR1_8 (11172) -> HRSHOEDR1_3 (11171) CKT 1 | S_011190HRSHOESPG_81 | 138 | 38 | Branch MVA | 250 | - | - | - | 104.0128 | 104.016 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS__5 ( 3696) -> HUTTOSTR (500126) CKT 2 | LCRA TSC_T510_1 | 345 | 1 | Branch MVA | 750 | - | - | - | 100.7184 | 103.7025 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS__5 ( 3696) -> HUTTOSTR (500126) CKT 2 | LCRA TSC_T510_T512_1 | 345 | 1 | Branch MVA | 750 | - | - | - | 102.0914 | 104.5104 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS__5 ( 3696) -> HUTTOSTR (500126) CKT 2 | LCRATSC_1_HUTTO__LIMMER | 345 | 1 | Branch MVA | 750 | - | - | - | - | 103.7115 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS__5 ( 3696) -> HUTTOSTR (500127) CKT 1 | LCRA TSC_T510_1 | 345 | 1 | Branch MVA | 750 | - | - | - | 101.5487 | 104.5574 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS__5 ( 3696) -> HUTTOSTR (500127) CKT 1 | LCRA TSC_T510_T512_1 | 345 | 1 | Branch MVA | 750 | - | - | - | 102.9331 | 105.372 | 100.3932 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS__5 ( 3696) -> HUTTOSTR (500127) CKT 1 | LCRATSC_1_HUTTO__LIMMER | 345 | 1 | Branch MVA | 750 | - | - | - | - | 104.5665 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS1_8 ( 3666) -> RNDRCKNE2_8 ( 3667) CKT 1 | GABRIEL - BELL COUNTY/GEORGETOWN E_8 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1313.6809 | 108.435 | - | - | - | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS1_8 ( 3666) -> RNDRCKNE2_8 ( 3667) CKT 1 | GABRIEL - BELL COUNTY/GEORGETOWN E_8 (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1313.6809 | - | - | 105.9789 | 108.236 | 109.6174 | 109.5888 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS1_8 ( 3666) -> RNDRCKNE2_8 ( 3667) CKT 1 | GEORGETOWN E - GABRIEL_8 (SINGLE B TO B) B | 138 | 138 | Branch Amp | 1313.6809 | - | - | 105.9911 | 108.1907 | 109.5184 | 109.5433 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS1_8 ( 3666) -> RNDRCKNE2_8 ( 3667) CKT 1 | L_000132BELLCNTY8-003415TEMP_SS__8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 103.3417 | 104.6009 | 103.1071 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS1_8 ( 3666) -> RNDRCKNE2_8 ( 3667) CKT 1 | L_000132BELLCNTY8-003640SALADO1_8C1 | 138 | 138 | Branch Amp | 1313.6809 | 101.0323 | - | - | - | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS1_8 ( 3666) -> RNDRCKNE2_8 ( 3667) CKT 1 | L_003539JONAHT_8-007346L_GABRIE8_1YC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | 112.833 | 114.9267 | 116.2587 | 116.2425 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS1_8 ( 3666) -> RNDRCKNE2_8 ( 3667) CKT 1 | L_003539JONAHT_8-007528L_GEOREA8_1YC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | 106.0249 | 108.2384 | 109.5858 | 109.5873 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS1_8 ( 3666) -> RNDRCKNE2_8 ( 3667) CKT 1 | L_003668RNDROCK1_8-007366L_CHIEBR8_1YC1 | 138 | 138 | Branch Amp | 1313.6809 | 114.9178 | - | 104.2203 | - | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS1_8 ( 3666) -> RNDRCKNE2_8 ( 3667) CKT 1 | L_007343L_GEORGE8_1Y-007347L_RIVERY8_1YC1 | 138 | 138 | Branch Amp | 1313.6809 | 107.2216 | - | - | - | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS1_8 ( 3666) -> RNDRCKNE2_8 ( 3667) CKT 1 | L_007343L_GEORGE8_1Y-007366L_CHIEBR8_1YC1 | 138 | 138 | Branch Amp | 1313.6809 | 111.5028 | - | 100.9782 | - | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS1_8 ( 3666) -> RNDRCKNE2_8 ( 3667) CKT 1 | L_007346L_GABRIE8_1Y-007528L_GEOREA8_1YC1 | 138 | 138 | Branch Amp | 1313.6809 | 108.3342 | - | - | - | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS1_8 ( 3666) -> RNDRCKNE2_8 ( 3667) CKT 1 | LCRA TSC_T223_1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | 105.9911 | 108.1907 | 109.5184 | 109.5433 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSS1_8 ( 3666) -> RNDRCKNE2_8 ( 3667) CKT 1 | LCRA TSC_T378_T642 | 138 | 138 | Branch Amp | 1313.6809 | 118.6427 | - | 107.4553 | 101.9912 | 101.345 | 102.5733 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSTR (500126) -> HUTTOSS1_8 ( 3666) CKT 2 | LCRA TSC_T510_1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | 100.3696 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSTR (500126) -> HUTTOSS1_8 ( 3666) CKT 2 | LCRA TSC_T510_T512_1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | 100.8996 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSTR (500126) -> HUTTOSS1_8 ( 3666) CKT 2 | LCRATSC_1_HUTTO__LIMMER | 138 | 1 | Branch MVA | 750 | - | - | - | - | 100.6405 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSTR (500127) -> HUTTOSS1_8 ( 3666) CKT 1 | LCRA TSC_T510_1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | 101.1971 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSTR (500127) -> HUTTOSS1_8 ( 3666) CKT 1 | LCRA TSC_T510_T512_1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | 101.7315 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | HUTTOSTR (500127) -> HUTTOSS1_8 ( 3666) CKT 1 | LCRATSC_1_HUTTO__LIMMER | 138 | 1 | Branch MVA | 750 | - | - | - | - | 101.4702 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | I_DUPSW4A ( 8422) -> AIRLIQSW4A ( 8979) CKT 1 | L_008818OXY_INGL4A-008968INGLCOSW4AC2 | 138 | 138 | Branch Amp | 891.1276 | 103.7186 | - | 104.532 | 106.135 | 110.884 | 106.7944 | -
TAEPTN,TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | I_DUPSW4A ( 8422) -> I_DUPP14A ( 8817) CKT 1 | E_INGLCOSW_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 111.1869 | 100.6826 | -
TAEPTC,TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | I_DUPSW4A ( 8422) -> I_DUPP14B ( 8819) CKT 2 | E_INGLCOSW_CC1_TRAIN | 138 | 138 | Branch Amp | 882.7601 | 100.0633 | - | 101.9906 | 106.6795 | 118.9639 | 107.7243 | -
TAEPTN , TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | I_DUPSW4A (8422) -> INGLESID4A (8425) CKT 1 | Pre-contingency | 138 | 138 | Amps | 882.7601 | - | - | 142.6256 | 148.816 | 148.0384 | 143.7359 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | ILLN2A ( 6565) -> PANDALE2A ( 6567) CKT 1 | L_006564ILLN4A-076579L_FORTLA8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 113.9684 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | ILLN2A ( 6565) -> PANDALE2A ( 6567) CKT 1 | MB2074220667 | 69 | 69 | Branch Amp | 317.961 | - | - | 102.2941 | - | - | - | -
TAEPTC,TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | INGLESID4A ( 8425) -> SEABIRD (84250) CKT 1 | L_008425INGLESID4A-084250SEABIRDC2 | 138 | 138 | Branch Amp | 861.8416 | - | - | 126.5477 | 127.7841 | 133.33 | 127.8867 | -
TLCRA,TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | JARRELL_E_8 ( 3688) -> L_GABRIE8_1Y ( 7346) CKT 1 | BELLCNTY8-BARTLETTSW (SINGLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1227 | - | -
TLCRA,TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | JARRELL_E_8 ( 3688) -> L_GABRIE8_1Y ( 7346) CKT 1 | BEPC_215_2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2742 | - | -
TLCRA,TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | JARRELL_E_8 ( 3688) -> L_GABRIE8_1Y ( 7346) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 106.5078 | - | - | -
TLCRA,TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | JARRELL_E_8 ( 3688) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_000114BARTLETTSW-000122SCHWERTNERC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.669 | - | -
TLCRA,TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | JARRELL_E_8 ( 3688) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_000114BARTLETTSW-000132BELLCNTY8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4341 | - | -
TLCRA,TONCOR | NORTH_CE | SOUTH_CE | NORTH_CE, SOUTH_CE | JARRELL_E_8 ( 3688) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 114.8042 | - | -
TONCOR | EAST | EAST | EAST, EAST | JAXVLSW_8 ( 3253) -> BULLARD_8 (13253) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 113.3062 | 121.8525 | 112.7912 | -
TONCOR | EAST | EAST | EAST, EAST | JAXVLSW_8 ( 3253) -> BULLARD_8 (13253) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 117.0536 | - | 117.3076 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | BENNETT RD-WISE CTY 138 KV | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 118.168 | 111.6218 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | BEPC_005_1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.0817 | 110.2897 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | BEPC_114 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 108.6203 | 102.5595 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | BEPC_21 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 103.3252 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | BEPC_243 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 109.5575 | 103.6382 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | BEPC_246 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 101.2662 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | BEPC_2541 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 101.0763 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | BEPC_283_1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 131.151 | 123.051 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | E_WHCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.0434 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | E_WHCCS2_CC2_TRAIN | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.1412 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | G_150111CPSES_UNIT1UU1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.1541 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | G_150112CPSES_UNIT2UU2 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.158 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | G_888879BLUBIRD_POIUS1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.0344 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000501HILLTOP8-000508RIKERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 106.0279 | 130.844 | 123.8024 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000508RIKER-000516ZIONHILLC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 106.0288 | 130.8453 | 123.8039 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000516ZIONHILL-000543SWIMMERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | 101.3442 | 108.0776 | 132.9716 | 125.8604 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000543SWIMMER-000588WILLOWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | 102.287 | 109.002 | 133.9222 | 126.7874 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000570WISECNTY-000571HIDEOUTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | 100.3548 | 106.129 | 130.2069 | 122.0629 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000571HIDEOUT-000579JCKCNTY8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | 101.2048 | 106.9937 | 131.1475 | 122.9678 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000579JCKCNTY8-000580WSTBROOKC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | 102.7636 | 109.5063 | 134.4433 | 127.2953 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000579JCKCNTY8-000600BRIDGEPORTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 108.8059 | 102.7706 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000580WSTBROOK-000588WILLOWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | 102.4799 | 109.1971 | 134.1072 | 126.9681 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000590PERCHHILL-000600BRIDGEPORTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 107.2744 | 101.278 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000590PERCHHILL-000608CRAFTONC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 106.1397 | 100.1738 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000608CRAFTON-000620BOWIE8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 105.5566 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000620BOWIE8-000741DYEMOUNDC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 101.3461 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000670KRUM-001568ALLISON_T8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.0688 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000684SPRING-000691VALLEYVIEWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 101.8221 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000690MYRA-000691VALLEYVIEWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 102.1399 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000690MYRA-000695MUENSTERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.5901 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000695MUENSTER-000730WOLFRIDGEC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.9519 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000741DYEMOUND-000762HARDYSWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 101.0315 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_000746STJO8-000762HARDYSWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.8923 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_001565BRDGPORT_8-001590BRDGPORT_T8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.1638 | 110.5564 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_001568ALLISON_T8-888887CONNOLLY_B1C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.3296 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | L_001582BENNETT_8-001590BRDGPORT_T8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.1612 | 110.5538 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.6081 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.0787 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | WISE COUNTY - JACK COUNTY (BEPC) 138 KV (SINGLE B TO B) HIDEOUT | 138 | 138 | Branch Amp | 1606.5397 | - | - | 101.2883 | 107.0819 | - | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | WISE COUNTY (BEC) - ALVORD/BRIDGEPORT(BEC) (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.0802 | 110.2897 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> BALSORA_8 ( 1598) CKT 1 | XFMR-WHCCS2_5-1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.0544 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | BEPC_005_1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 104.9867 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | BEPC_006 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 105.6789 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | BEPC_114 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 108.0713 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | BEPC_242 | 138 | 138 | Branch Amp | 1606.5397 | - | - | 100.0231 | 104.6575 | 128.6185 | 119.521 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | BEPC_243 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.1857 | 108.582 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | BEPC_458 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 102.5823 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | L_000501HILLTOP8-000508RIKERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 115.7814 | 107.5366 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | L_000508RIKER-000516ZIONHILLC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 115.7791 | 107.5347 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | L_000516ZIONHILL-000543SWIMMERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.1381 | 108.8283 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | L_000541RENO-000595KEETERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 102.9557 | 126.9865 | 117.8163 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | L_000543SWIMMER-000588WILLOWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.7399 | 109.4071 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | L_000579JCKCNTY8-000580WSTBROOKC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 118.071 | 109.7251 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | L_000579JCKCNTY8-000600BRIDGEPORTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 119.0258 | 110.2929 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | L_000579JCKCNTY8-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 104.4909 | 128.6029 | 119.3663 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | L_000580WSTBROOK-000588WILLOWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.8546 | 109.5177 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | L_000590PERCHHILL-000600BRIDGEPORTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 116.3067 | 107.6235 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | L_000590PERCHHILL-000608CRAFTONC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 114.0419 | 105.3932 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | L_000595KEETER-000596COTTONDALEC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 103.5099 | 127.5717 | 118.3797 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | L_000596COTTONDALE-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 104.4923 | 128.6046 | 119.3674 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | L_000608CRAFTON-000620BOWIE8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 112.9494 | 104.3192 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV DCKT & EAGLE MOUNTAIN - WEATHERFORD 138 KV LINE | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 101.509 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> HIDEOUT ( 571) CKT 1 | WISE COUNTY (BEC) - ALVORD/BRIDGEPORT(BEC) (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 104.9443 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> WSTBROOK ( 580) CKT 1 | BEPC_242 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 119.426 | 113.1722 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> WSTBROOK ( 580) CKT 1 | BEPC_283_1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 103.1126 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> WSTBROOK ( 580) CKT 1 | L_000541RENO-000595KEETERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.7713 | 111.4442 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> WSTBROOK ( 580) CKT 1 | L_000570WISECNTY-000571HIDEOUTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 102.3045 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> WSTBROOK ( 580) CKT 1 | L_000571HIDEOUT-000579JCKCNTY8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 103.1006 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> WSTBROOK ( 580) CKT 1 | L_000579JCKCNTY8-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 119.8711 | 113.4807 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> WSTBROOK ( 580) CKT 1 | L_000595KEETER-000596COTTONDALEC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 118.5305 | 112.1821 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JCKCNTY8 ( 579) -> WSTBROOK ( 580) CKT 1 | L_000596COTTONDALE-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 119.8624 | 113.472 | -
TCNPE | COAST | COAST | COAST, COAST | JENETA__B138 (47310) -> WESTWD_T25_8 (47461) CKT 25 | P7-1_E1>>T9899A | 138 | 138 | Branch Amp | 2196.4409 | - | - | - | - | 108.1016 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | JESSICA ( 404) -> SAINTPAUL ( 223) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 962.2503 | - | - | - | 106.3774 | 113.6992 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 121.1982 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 119.1252 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.1456 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 116.1281 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6876 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | E_FREC_CC2_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.2122 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | E_FRNYPP_CC1_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.2856 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | E_FRNYPP_CC2_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.322 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | E_TGCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.1907 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | E_WHCCS2_CC2_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.0323 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | G_003321REDLAND_5UN1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3549 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | G_120041MLSES_UNIT1UL1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.083 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | G_120042MLSES_UNIT2UL2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.1406 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | G_120043MLSES_UNIT3UL3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.1425 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | G_150111CPSES_UNIT1UU1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.5892 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | G_150112CPSES_UNIT2UU2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.7461 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.5264 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.0333 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_001906VENUS_S5-015201FORBESR2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5981 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.1954 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.2998 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.2985 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_003109STRYKER_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.6136 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 106.6441 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_003133RICHLND2_5-003199CALFRESTN_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.2282 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.0182 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.7092 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_003386OUTLAW_5-046020LIMEST_POI_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 118.6678 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_003386OUTLAW_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 121.3453 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.2835 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.5571 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.4958 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.9507 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | L_046020LIMEST_POI_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 118.9136 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | LAKE CREEK - LAKE HALL/TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.1836 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | LIMESTONE - OUTLAW / NAVARRO_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 119.9995 | - | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 112.011 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.5071 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | 105.282 | 127.2429 | 173.963 | 124.4266 | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 345 | 345 | Branch Amp | 1725.3568 | - | - | 102.1852 | - | 169.8606 | 118.6118 | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 113.6503 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 111.4243 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.9231 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 108.812 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 108.0348 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | TRIN-SK*ME (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.662 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.091 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.0108 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.4541 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.1684 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | VENUS-FORT SMITH SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.253 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | XFMR-MARTINLK_5-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.083 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | XFMR-MARTINLK_5-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.1406 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_N5 ( 3391) -> BIGBRNW_5 ( 3381) CKT 1 | XFMR-MARTINLK_5-3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.1425 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | JEWETT_S5 ( 3390) -> BALE_S5 ( 3711) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.995 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | JEWETT_S5 ( 3390) -> BALE_S5 ( 3711) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.2331 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_S5 ( 3390) -> BIGBRNE_5 ( 3380) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.6412 | - | -
TONCOR | EAST | EAST | EAST, EAST | JEWETT_S5 ( 3390) -> BIGBRNE_5 ( 3380) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.9604 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | JONAHT_8 ( 3539) -> L_GEOREA8_1Y ( 7528) CKT 1 | HUTTO - ROUND ROCK/GEORGETOWN SOUTH (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.2465 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | JONAHT_8 ( 3539) -> L_GEOREA8_1Y ( 7528) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 100.9468 | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | JONAHT_8 ( 3539) -> L_GEOREA8_1Y ( 7528) CKT 1 | L_003664RNDRCKWH_T_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | 133.5044 | 140.2182 | 142.7407 | 142.0775 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | JONAHT_8 ( 3539) -> L_GEOREA8_1Y ( 7528) CKT 1 | L_003664RNDRCKWH_T_8-003669RNDRCKWH1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | 133.5667 | 140.2809 | 142.8035 | 142.1404 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | JONAHT_8 ( 3539) -> L_GEOREA8_1Y ( 7528) CKT 1 | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | 161.3508 | 169.295 | 172.255 | 171.3181 | -
TAEPTC | COAST | COAST | COAST, COAST | JOSLIN4A ( 8140) -> FORMOSA4A ( 8126) CKT 1 | E_FORMOSA_CC1_TRAIN | 138 | 138 | Branch Amp | 903.6786 | - | - | - | - | - | 107.2539 | -
TAEPTC | COAST | COAST | COAST, COAST | JOSLIN4A ( 8140) -> GOHLKE4A ( 8141) CKT 1 | L_008140JOSLIN4A-008685COBIA4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 107.8614 | 135.0337 | 112.6672 | -
TAEPTC | COAST | COAST | COAST, COAST | JOSLIN4A ( 8140) -> GOHLKE4A ( 8141) CKT 1 | L_008155SANDCRAB4A-008685COBIA4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 105.5807 | 132.7317 | 110.4086 | -
TAEPTC | COAST | COAST | COAST, COAST | JOSLIN4A ( 8140) -> GOHLKE4A ( 8141) CKT 1 | L_008155SANDCRAB4A-008723CANGREJO4AC1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 109.8855 | 136.8852 | 114.6643 | -
TAEPTC | COAST | COAST | COAST, COAST | JOSLIN4A ( 8140) -> GOHLKE4A ( 8141) CKT 1 | M128607128702-1_MODIFIED_BY_MZ | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 109.248 | 137.8065 | 113.723 | -
TAEPTC | COAST | COAST | COAST, COAST | JOSLIN4A ( 8140) -> GOHLKE4A ( 8141) CKT 1 | MB1287012860-2_MODIFIED_BY_MZ | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 110.4142 | 139.2873 | 114.7664 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KAUFMN_8 ( 2724) -> FORNEYS_8 (12715) CKT 1 | 3WT_002433SGVLSW1_5_002434SGVLSW1_8_012434SGVLSW1_3 C 2 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 106.104 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KAUFMN_8 ( 2724) -> FORNEYS_8 (12715) CKT 1 | L_002723ROSEHILL1_8-002731TERRL_S1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 103.2468 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KAUFMN_8 ( 2724) -> FORNEYS_8 (12715) CKT 1 | SEAGOVILLE SW - FORNEY/TRICORNER DCKT 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 106.1886 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KAUFMN_S_8 ( 2728) -> KAUFMN_8 ( 2724) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 120.2414 | 100.3548 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KAUFMN_S_8 ( 2728) -> KAUFMN_8 ( 2724) CKT 1 | L_006821I20_RC-006902TALTY_RCC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.7458 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KAUFMN_S_8 ( 2728) -> KAUFMN_8 ( 2724) CKT 1 | L_006821I20_RC-006904COMBINRC1C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 108.8729 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KAUFMN_S_8 ( 2728) -> KAUFMN_8 ( 2724) CKT 1 | L_006903BOZE-006904COMBINRC1C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 111.0436 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KAUFMN_S_8 ( 2728) -> KAUFMN_8 ( 2724) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.5225 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KAUFMN_S_8 ( 2728) -> KAUFMN_8 ( 2724) CKT 1 | RYBRN_P1-2_ROSEHILRC-ROSEHIL | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 108.6862 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KAUFMN_S_8 ( 2728) -> KAUFMN_8 ( 2724) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1799 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KAUFMN_S_8 ( 2728) -> KAUFMN_8 ( 2724) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 109.9075 | - | 108.6406 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEENE_8 ( 2294) -> ALVARADO1_8 ( 2297) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | 116.0551 | 118.0815 | 151.6492 | 186.1016 | 196.9433 | 169.1447 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEENE_8 ( 2294) -> ALVARADO1_8 ( 2297) CKT 1 | 3WT_003522HILLBORO1_8_003523HILLBORO1_9_003519HILLBORO1_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.782 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEENE_8 ( 2294) -> ALVARADO1_8 ( 2297) CKT 1 | BEPC_306 | 138 | 138 | Branch Amp | 861.8416 | 159.048 | 185.6834 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEENE_8 ( 2294) -> ALVARADO1_8 ( 2297) CKT 1 | CLEBURNE-BURLESON 138 KV (SINGLE B TO B) B WILSHIRE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.5459 | 107.4405 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEENE_8 ( 2294) -> ALVARADO1_8 ( 2297) CKT 1 | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | 138 | Branch Amp | 861.8416 | 133.668 | 178.16 | 207.7533 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEENE_8 ( 2294) -> ALVARADO1_8 ( 2297) CKT 1 | L_000442RAILPORT-001908VENUSC1 | 138 | 138 | Branch Amp | 861.8416 | 135.7639 | 178.4034 | 211.7947 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEENE_8 ( 2294) -> ALVARADO1_8 ( 2297) CKT 1 | L_001908VENUS-002303KEMPRNCH_8C1 | 138 | 138 | Branch Amp | 861.8416 | 158.856 | 185.7747 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEENE_8 ( 2294) -> ALVARADO1_8 ( 2297) CKT 1 | L_002203MNTVALLY_P8-002210JOSHUA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 100.9923 | 105.9176 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEENE_8 ( 2294) -> ALVARADO1_8 ( 2297) CKT 1 | L_002210JOSHUA_8-002279CLEBRNSW_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.6294 | 107.5459 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | BENNETT RD-WISE CTY 138 KV | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 114.0516 | 107.5357 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | BEPC_005_1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 112.9658 | 106.205 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | BEPC_114 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 104.5311 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | BEPC_243 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 105.4674 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | BEPC_283_1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 126.9844 | 118.9257 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | L_000501HILLTOP8-000508RIKERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 101.8588 | 126.7475 | 119.7327 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | L_000508RIKER-000516ZIONHILLC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 101.8601 | 126.7492 | 119.7345 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | L_000516ZIONHILL-000543SWIMMERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 103.9025 | 128.8673 | 121.7839 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | L_000543SWIMMER-000588WILLOWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 104.8248 | 129.8147 | 122.7082 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | L_000570WISECNTY-000571HIDEOUTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 101.9211 | 126.0442 | 117.9415 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | L_000571HIDEOUT-000579JCKCNTY8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 102.7831 | 126.9806 | 118.8423 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | L_000579JCKCNTY8-000580WSTBROOKC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 105.3278 | 130.3339 | 123.2145 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | L_000579JCKCNTY8-000600BRIDGEPORTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 104.7175 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | L_000580WSTBROOK-000588WILLOWC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 105.0196 | 129.9994 | 122.8886 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | L_000590PERCHHILL-000600BRIDGEPORTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 103.1906 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | L_000590PERCHHILL-000608CRAFTONC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 102.0597 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | L_000608CRAFTON-000620BOWIE8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 101.4783 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | L_001565BRDGPORT_8-001590BRDGPORT_T8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 113.0509 | 106.4734 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | L_001582BENNETT_8-001590BRDGPORT_T8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 113.0482 | 106.4708 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | WISE COUNTY - JACK COUNTY (BEPC) 138 KV (SINGLE B TO B) HIDEOUT | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | 102.8713 | - | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEETER ( 595) -> RENO ( 541) CKT 1 | WISE COUNTY (BEC) - ALVORD/BRIDGEPORT(BEC) (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 112.9644 | 106.205 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.9596 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.3375 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | G_151371LILY_S1US1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.0062 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.5344 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.6991 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.3565 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.0023 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 103.4105 | 129.1891 | 104.4677 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | L_006903BOZE-151372LILY_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.4814 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.617 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.2085 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.2848 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 107.341 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.2647 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.5486 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 104.0618 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMP_S_8 ( 2726) -> KNGCRK_8 ( 2774) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 116.9133 | - | 114.7721 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KEMPRNCH_8 (2303) -> VENUSSTR (500057) CKT 1 | Pre-contingency | 138 | 1 | MVA | 695 | - | - | - | 108.2916 | 111.0766 | 103.2411 | -
TAEPTC,TCPSE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | KENEDYSW4A ( 8186) -> FALLSCTY ( 5145) CKT 1 | L_008186KENEDYSW4A-078584L_HELENA8_1YC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | 103.7879 | - | - | - | -
TAEPTC,TCPSE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | KENEDYSW4A ( 8186) -> FALLSCTY ( 5145) CKT 1 | L_078573L_RUNGE_8_1Y-078576L_NORDWE8_1YC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | 100.1812 | - | - | - | -
TAEPTC,TCPSE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | KENEDYSW4A ( 8186) -> FALLSCTY ( 5145) CKT 1 | L_078581L_MAGNTA8_1Y-078583L_MILTON8_1YC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | 100.9875 | - | - | - | -
TAEPTC,TCPSE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | KENEDYSW4A ( 8186) -> FALLSCTY ( 5145) CKT 1 | L_078581L_MAGNTA8_1Y-078584L_HELENA8_1YC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | 101.8214 | - | - | - | -
TAEPTC,TCPSE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | KENEDYSW4A ( 8186) -> FALLSCTY ( 5145) CKT 1 | LCRA TSC_T580_T630 | 138 | 138 | Branch Amp | 656.8405 | - | - | 101.6012 | - | - | - | -
TAEPTC,TCPSE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | KENEDYSW4A ( 8186) -> FALLSCTY ( 5145) CKT 1 | LCRA TSC_T630 | 138 | 138 | Branch Amp | 656.8405 | - | - | 101.7922 | - | - | - | -
RSHER2,TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | KEO_2_8 (131453) -> FTBLOCKS_8 ( 9424) CKT 1 | G_135591BRP_PAVO_BTUBT | 138 | 138 | Branch Amp | 2133.6855 | - | - | 103.3852 | 103.0686 | 102.9714 | 102.4784 | -
RSHER2,TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | KEO_2_8 (131453) -> FTBLOCKS_8 ( 9424) CKT 1 | L_038340TNAIRPORT41-038355TNLEONCRK_1C1 | 138 | 138 | Branch Amp | 2133.6855 | - | - | - | - | 100.0722 | - | -
RSHER2,TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | KEO_2_8 (131453) -> FTBLOCKS_8 ( 9424) CKT 1 | L_038430TNWHITEBKR1-038445TNGIRVIN__1C1 | 138 | 138 | Branch Amp | 2133.6855 | - | - | 104.2408 | 104.1701 | 104.1039 | 103.5034 | -
RSHER2,TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | KEO_2_8 (131453) -> FTBLOCKS_8 ( 9424) CKT 1 | L_038430TNWHITEBKR1-135592BRP_PAVO_8C1 | 138 | 138 | Branch Amp | 2133.6855 | - | - | 103.3855 | 103.0689 | 102.9717 | 102.4787 | -
RSHER2,TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | KEO_2_8 (131453) -> FTBLOCKS_8 ( 9424) CKT 1 | L_131453KEO_2_8-131454KEO_3_8CS2 | 138 | 138 | Branch Amp | 2133.6855 | - | - | 103.2176 | 102.9389 | 102.8455 | 102.4691 | -
RSHER2,TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | KEO_2_8 (131453) -> FTBLOCKS_8 ( 9424) CKT 1 | MB2095020951 | 138 | 138 | Branch Amp | 2133.6855 | - | - | 100.0169 | - | - | - | -
RSHER2,TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | KEO_2_8 (131453) -> FTBLOCKS_8 ( 9424) CKT 1 | New Girvin - Whitebk Ckt 2 | 138 | 138 | Branch Amp | 2133.6855 | - | - | 104.2408 | 104.1689 | 104.1039 | 103.5034 | -
RSHER2,TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | KEO_2_8 (131453) -> FTBLOCKS_8 ( 9424) CKT 1 | New Shunt 9424 | 138 | 138 | Branch Amp | 2133.6855 | - | - | 106.1514 | 105.8769 | 105.7831 | 105.4275 | -
RSHER2,TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | KEO_2_8 (131453) -> FTBLOCKS_8 ( 9424) CKT 1 | S_038430TNWHITEBKR11 | 138 | 138 | Branch Amp | 2133.6855 | - | - | 101.9541 | 101.6862 | 101.5936 | 101.2486 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KILLTAFD_8 ( 3616) -> KILELMR2_T_8 (13427) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 106.3765 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KLEBRG1T_8 ( 3077) -> SSWWT2T_8 ( 3079) CKT 1 | L_002429WATMLL_8-003083WILMER1_8C1 | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | 131.1795 | 134.1493 | 125.2554 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KLEBRG1T_8 ( 3077) -> SSWWT2T_8 ( 3079) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | - | - | 111.949 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KLEBRG1T_8 ( 3077) -> SSWWT2T_8 ( 3079) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | 124.9175 | - | - | -
TONCOR | WEST | WEST | WEST, WEST | KMCCS_2_8 (1065) -> SPPKM_8 (180444) CKT 1 | Pre-contingency | 138 | 138 | Amps | 778.1677 | - | - | - | - | 101.0414 | 101.0797 | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | 3WT_001302WILLOWVAL_5_001301WILLOWVAL_8_018537WILLOWVAL_3 C 3 | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.6816 | 104.55 | 125.0134 | 109.4608 | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | BAS_RANCH_CON | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 106.2359 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | BLUFF CREEK SW - WILLOW VALLEY SW 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 102.9037 | 119.8859 | 109.0485 | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | C5-WETT-2_A-1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 107.6895 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | C5-WETT-2_A-2 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 113.3027 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | CHINA GROVE SW - SNYDER 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 100.0037 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | CLY_PHNT1P7F1-1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 102.7053 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | CLY_PHNT1P7F1-2 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 102.0372 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | CLY_PHNT2P7F1-1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 100.6266 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | ENNIS CREEK - GOLDEN SW 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 114.5659 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | G_888839BAS_RANCH_POIUC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 106.2631 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | HOLLY_CON | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 115.0808 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001064SUN_8-001067GOLDENSW_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 116.5895 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001064SUN_8-001311SACROC_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 100.5333 | 115.2401 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001067GOLDENSW_8-001315BRAND_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 113.6812 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001298ONC900014_TAP-001305SNYDER_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 103.2229 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001300EXSHARNR_8-001309BLUFCKTA_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 102.9457 | 119.9303 | 108.9851 | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001300EXSHARNR_8-901303ONC900119_TAPC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 104.0516 | 107.1492 | 124.0616 | 113.1878 | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001301WILLOWVAL_8-901303ONC900119_TAPC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 106.3317 | 109.6425 | 126.5826 | 115.7894 | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001304DEEPCRK_8-001305SNYDER_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 112.9877 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001304DEEPCRK_8-001311SACROC_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 113.4906 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001313ENISCKTA_8-001314ENNISCK_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 115.0818 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001313ENISCKTA_8-001315BRAND_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 114.6265 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_001314ENNISCK_8-011306DERMOTT_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.7203 | 103.5262 | 130.3616 | 113.2171 | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 101.0186 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_010049RANGER_5-011048TONKAWAW_5C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 100.4302 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_010049RANGER_5-011048TONKAWAW_5C2 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 100.4302 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_011048TONKAWAW_5-011318SCURCNTYS_5C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 100.0774 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_011048TONKAWAW_5-011318SCURCNTYS_5C2 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 100.0774 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_011305DERMOTT_5-011318SCURCNTYS_5C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 109.9772 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_011305DERMOTT_5-011318SCURCNTYS_5C2 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 109.9772 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_011318SCURCNTYS_5-059905FARADAYC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 101.6522 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_023920ABERNATH_5-023928DBLMTN_5C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 102.342 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_023924FARMLAND_5-023930FIDLWD_5C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 105.0524 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_023924FARMLAND_5-888856HOLLY_POIC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 107.872 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_059904COTTONWOOD-060006HYPERION7AC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 101.0247 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_060017HODLRAN27A-060515CLEARCRO7AC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 101.9798 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | L_888856HOLLY_POI-059900LONG_DRAWC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 118.6032 | 100.6849 | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 100.9992 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | MB2552825529 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 100.9747 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | New Meinan - Sweeteast and BitterCreek 345kV Double | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 102.745 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | New Sweeteast - Meinan and BitterCreek 345kV Double | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 101.5674 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 111.228 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 116.8194 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | SCUR_CLY_P7 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 103.2875 | - | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 1 & SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | 100.9635 | - | 114.4597 | 128.1049 | 158.6456 | 137.425 | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 107.169 | 129.5335 | 110.986 | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | WILLOW VALLEY TRANSFORMER 1 (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | 101.6817 | 104.55 | 125.0135 | 109.4609 | -
TONCOR | WEST | WEST | WEST, WEST | KNAPP_8 ( 1310) -> BLUFCKTA_8 ( 1309) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 748.8818 | - | 103.2579 | - | - | - | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | 3WT_001302WILLOWVAL_5_001301WILLOWVAL_8_018537WILLOWVAL_3 C 3 | 138 | 138 | Branch Amp | 778.1677 | 100.0623 | - | 105.0102 | 107.4051 | 127.0237 | 111.9561 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | BAS_RANCH_CON | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 108.8381 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.4604 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.258 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | BITTER CREEK SW (LCRA) - CATTLEMEN SW & BITTER CREEK SW (LCRA) - SWEETWATER EAST 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.5014 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | BLUFF CREEK SW - WILLOW VALLEY SW 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | 102.767 | 105.7123 | 122.0051 | 111.4281 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.0034 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | C5-WETT-2_A-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 110.2634 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | C5-WETT-2_A-2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 115.6886 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | CATTLEMAN - CHAMPION CREEK & MORGAN CREEK SW - BITTER CREEK SW (LCRA) 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.9524 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | CHINA GROVE SW - AEP PAINT CREEK 138 KV & GRAHAM SES - TONKAWA/COOKFIELD/LONGCREEK 345 KV (DOUBLE B TO B) 2019 SUM - FUTURE-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.7823 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | CHINA GROVE SW - AEP PAINT CREEK 138 KV & GRAHAM SES - TONKAWA/COOKFIELD/LONGCREEK 345 KV (DOUBLE B TO B) 2019 SUM - FUTURE-2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.9431 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | CHINA GROVE SW - SNYDER 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.8061 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | CLEAR CROSSING - COODY CROSSING/THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.0811 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | CLY_PHNT1P7F1-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 105.4407 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | CLY_PHNT1P7F1-2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 104.7935 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | CLY_PHNT2P7F1-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 103.4267 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | CLY_PHNT2P7F1-2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.787 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | COODY CROSSING - TECUMSEH AND CLEAR CROSSING - THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.0323 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | E_OECCS_CC1_TRAIN | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.3806 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | E_OECCS_CC2_TRAIN | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.3981 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | E_QALSW_CC1_TRAIN | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.0014 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | ENNIS CREEK - GOLDEN SW 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 116.8826 | 100.6826 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | ENNIS CREEK SW - SALT CREEK SW (BRAZOS) 138 KV 2021 WIN - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.1808 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | FALCON SOUTH - RANGER CAMP 345 KV SUM 2027 - FUTURE(DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.4426 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | G_010012METEOR_5US1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.8115 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | G_888839BAS_RANCH_POIUC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 108.8643 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | G_888851TRIFECTA_POIUN1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.7651 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | G_888856HOLLY_POIUS1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.8009 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | GRAHAM PLANT SWITCH-TONKAWA SWITCH/COOK FIELD ROAD SWITCH 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.5876 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | HART_CON | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.3832 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | HOLLY_CON | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 117.4056 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_000842GPL_KINGMTSW-000843GPL_KINGMTTPC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.3394 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.9987 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_000844GPL_NEVILLSW-076000L_NORTMC5_1YC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.2427 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001064SUN_8-001067GOLDENSW_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 118.8363 | 102.5176 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001064SUN_8-001311SACROC_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | 101.2057 | 103.3508 | 117.4874 | 101.8335 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001067GOLDENSW_8-001315BRAND_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 116.0297 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.7405 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001141HOLTSS_8-132313ECEC_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.4697 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001163LAMESA_8-132883LMESASLR_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.6284 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001189BARBER_LK1_8-010050RANGER_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.3768 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001298ONC900014_TAP-001305SNYDER_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 105.9049 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001298ONC900014_TAP-001318CHINAGRV_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.1571 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001300EXSHARNR_8-001309BLUFCKTA_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | 102.8115 | 105.7532 | 122.0482 | 111.3665 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001300EXSHARNR_8-901303ONC900119_TAPC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | 107.1836 | 109.8076 | 126.0366 | 115.4239 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001301WILLOWVAL_8-901303ONC900119_TAPC1 | 138 | 138 | Branch Amp | 778.1677 | 101.4589 | - | 109.3875 | 112.2154 | 128.4719 | 117.9392 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001304DEEPCRK_8-001305SNYDER_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 101.1187 | 115.3138 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001304DEEPCRK_8-001311SACROC_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 101.616 | 115.7982 | 100.1333 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001313ENISCKTA_8-001314ENNISCK_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 117.3811 | 101.127 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001313ENISCKTA_8-001315BRAND_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 116.942 | 100.6891 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001314ENNISCK_8-011306DERMOTT_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | 104.0006 | 106.3287 | 132.1352 | 115.5209 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001314ENNISCK_8-011403LLOYDCRK_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.1106 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_001355BUZZDRAW_8-023829KOCHTAP_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.0333 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 103.7966 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.3925 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_006076FOXTAIL7A-006100OKLA7AC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.0541 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_006076FOXTAIL7A-060791PERIGEE7AC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.4819 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_006235ABMULCW7A-888860RUBICONALPHA_POIC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.4084 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_010049RANGER_5-011048TONKAWAW_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 103.2166 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_010049RANGER_5-011048TONKAWAW_5C2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 103.2166 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_010050RANGER_8-011393FRONTIER_P8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.6491 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_011048TONKAWAW_5-011318SCURCNTYS_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.8771 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_011048TONKAWAW_5-011318SCURCNTYS_5C2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.8771 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_011270DOGHOUSE_5-023876CLEARFRK_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.4944 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_011305DERMOTT_5-011318SCURCNTYS_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 112.4567 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_011305DERMOTT_5-011318SCURCNTYS_5C2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 112.4567 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_011318SCURCNTYS_5-059905FARADAYC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 104.4207 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_011402ROUGHCRK_8-011403LLOYDCRK_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.0123 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_023829KOCHTAP_8-023835VLMOOR_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.0957 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_023849VLMOOR_5-059900LONG_DRAWC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.3682 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_023912OGALLALA_5-888884HART_POIC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.3625 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_023920ABERNATH_5-023928DBLMTN_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 105.0827 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_023924FARMLAND_5-023930FIDLWD_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 107.7052 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_023924FARMLAND_5-888856HOLLY_POIC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 110.4325 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_023928DBLMTN_5-023930FIDLWD_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.4728 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_059904COTTONWOOD-060006HYPERION7AC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 103.8035 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_059906LONGDRAW_138-134145JUNO_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.3629 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_060017HODLRAN27A-060515CLEARCRO7AC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 104.7252 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_068001CLAYTON_345-068014OPENSKYC2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.9357 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_888856HOLLY_POI-059900LONG_DRAWC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 102.1972 | 120.813 | 103.4529 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_888860RUBICONALPHA_POI-060791PERIGEE7AC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.0534 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_888865MALDIVES_POI-059900LONG_DRAWC2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.3672 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L_888884HART_POI-023920ABERNATH_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.5781 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | L2920902 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.6154 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | LCRA TSC_BAKERS_CEDACA_DC | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.6937 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.8887 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.5619 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.8887 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.5618 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | LCRA TSC_NOELK_SNGTR_NOELK_SNGTR2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.4636 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | LCRA TSC_SNGTR_SCHDR_SNGTR_SCHDR2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.0815 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | LCRA TSC_T422_T550 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.1429 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | LCRA TSC_T423_T551_A | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.4962 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | LCRA TSC_T424_T551_A_1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.9174 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | LONGCREEK SW - COOK FIELD ROAD SW & LONGCREEK SW - GRAHAM SW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.0463 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | LONGCREEK SW - SWEETWATER EAST & MULBERRY CREEK 345 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.4783 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 103.775 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | MALDIVES_CON | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.3501 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | MB2552825529 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 103.7553 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | MB2726627277 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.251 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | New Cattleman - Meinan and Champion 345kV Double | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.7983 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | New Meinan - Champion and Cattleman 345kV Double | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.6057 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | New Meinan - Sweeteast and BitterCreek 345kV Double | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 105.4546 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | New Sweeteast - Meinan and BitterCreek 345kV Double | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 104.32 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | ODESSA EHV - NORTH MCCAMEY 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.2898 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | PHNT_WSHACK_P7-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.4552 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | PHNT_WSHACK_P7-2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.8172 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 113.3443 | 100.2942 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | Ranger Camp-Morgan Creek CT Yard Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.6564 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 119.0429 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | RILEY - TESLA & TESLA - SALVARE | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.2066 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | Rockhound-Prong Moss Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.9082 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | RUBICONALPHA_CON | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.2536 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | SCUR_CLY_P7 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 106.0046 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 1 & SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | 104.3302 | - | 117.3 | 130.0903 | 159.4626 | 138.9376 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | STECL_10594 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.0909 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | STECL_4720 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.6957 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | STECL_4721-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.8887 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | STECL_4721-2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.5618 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 109.8059 | 131.3236 | 113.3419 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | TRIFECTA_CON | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.7845 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | WILLOW CREEK - CLEAR CROSSING (THOMAS PRICE) & COODY CROSSING - TECUMSEH 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV SUM 2026 - FUTURE (TRIPLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.9019 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | WILLOW CREEK - TECUMSEH/THOMAS PRICE 345 KV DCKT WIN 2023 - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.0114 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | WILLOW CREEK - THOMAS PRICE\TECUMSEH CREEK 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV WIN 2023 - FUTURE (TRIPLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.5928 | - | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | WILLOW VALLEY TRANSFORMER 1 (SINGLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | 100.0624 | - | 105.0103 | 107.4051 | 127.0238 | 111.9562 | -
1 | WEST | WEST | WEST, WEST | KNDRSACRC_8 (11130) -> ONC900041_TAP ( 1366) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 778.1677 | - | 102.7425 | - | - | 101.9933 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | 3WT_002433SGVLSW1_5_002434SGVLSW1_8_012434SGVLSW1_3 C 2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.9282 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.2869 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 104.8525 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 104.9976 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 105.122 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 104.0748 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.8044 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 104.6558 | 125.6593 | 105.7495 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.6628 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | L_006821I20_RC-006902TALTY_RCC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 107.1285 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | L_006821I20_RC-006904COMBINRC1C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 100.4578 | 114.2712 | 102.2925 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | L_006894ROSHILRC-006902TALTY_RCC2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.7104 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | L_006903BOZE-006904COMBINRC1C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 102.6878 | 116.4452 | 104.4599 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.7552 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.4527 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.1266 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 107.9022 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | RYBRN_P1-2_ROSEHILRC-ROSEHIL | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 114.1761 | 102.1587 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | SEAGOVILLE SW - FORNEY/TRICORNER DCKT 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.6013 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 104.8212 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.8571 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.0183 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 105.646 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGCRK_8 ( 2774) -> KAUFMN_S_8 ( 2728) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 115.4313 | - | 114.0266 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGSCRK1_5 (15202) -> TRICRN1_5 ( 2432) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.7738 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGSCRK1_5 (15202) -> TRICRN1_5 ( 2432) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.3275 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNGSCRK2_5 (15203) -> TRICRN1_5 ( 2432) CKT 1 | TRIN-SK*ME (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.1514 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNOBCRKSS_5 ( 3413) -> SALADOSS_5 ( 3699) CKT 1 | LCRATSC_5_HORNSB_EUCLID | 345 | 345 | Branch Amp | 3199.6917 | - | - | 100.4298 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNOBCRKSS_5 ( 3413) -> SALADOSS_5 ( 3699) CKT 1 | LCRATSC_6_EUCLID_JOHNDU | 345 | 345 | Branch Amp | 3199.6917 | 102.0943 | - | 105.3657 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KNOBCRKSS_5 (3413) -> SALADOSS_5 (3699) CKT 1 | Pre-contingency | 345 | 345 | Amps | 3199.6917 | - | - | - | 113.2188 | 132.8282 | 104.4024 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | KOCHTAP_8 (23829) -> BUZZDRAW_8 ( 1355) CKT 1 | IRON_BELT_CON | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 109.0227 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | KOCHTAP_8 (23829) -> BUZZDRAW_8 ( 1355) CKT 1 | L_059900LONG_DRAW-888842IRON_BELT_POIC1 | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 106.6482 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | KOCHTAP_8 (23829) -> BUZZDRAW_8 ( 1355) CKT 1 | L_888842IRON_BELT_POI-059910VOLTAC1 | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 110.6382 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | KOCHTAP_8 (23829) -> BUZZDRAW_8 ( 1355) CKT 1 | WETT LONG DRAW - WETT VOLTA 345 KV LINE (SINGLE B TO B)-2 | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 110.6382 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KRUM_T8 ( 1986) -> ARGYLEN_8 (11986) CKT 1 | L_000612BLUHORSE-000680NRTHSANGERC1 | 138 | 138 | Branch Amp | 878.5764 | - | - | - | - | 109.6511 | 101.0462 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | KRUM_T8 ( 1986) -> ARGYLEN_8 (11986) CKT 1 | L_000612BLUHORSE-000684SPRINGC1 | 138 | 138 | Branch Amp | 878.5764 | - | - | - | 101.8127 | 112.8491 | 104.2091 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_ALUMCR8_1Y ( 7318) -> L_SIMGID8_1Y ( 7310) CKT 1 | AEN_LP-AU¦DL_2013 | 138 | 138 | Branch Amp | 799.0861 | - | - | - | 102.0156 | 122.23 | 106.3756 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_ALUMCR8_1Y ( 7318) -> L_SIMGID8_1Y ( 7310) CKT 1 | AEN_P7 FPP-LP.DC_2 | 138 | 138 | Branch Amp | 799.0861 | - | - | - | - | 101.33 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_AUSSTR (500154) -> AUSTROP8 ( 9328) CKT 1 | 3WT_007040L_AUSTRO5_1Y_009328AUSTROP8_009330AUSTROP_T2 C 2 | 138 | 1 | Branch MVA | 480 | - | - | - | - | 109.5819 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_AUSSTR (500154) -> AUSTROP8 ( 9328) CKT 1 | AEN_DL-AU¦LP_2013 | 138 | 1 | Branch MVA | 480 | - | - | - | 100.1753 | 109.7638 | 100.9241 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_AUSSTR (500155) -> AUSTROP8 ( 9328) CKT 2 | 3WT_007040L_AUSTRO5_1Y_009328AUSTROP8_009329AUSTROP_T1 C 1 | 138 | 1 | Branch MVA | 480 | - | - | - | - | 109.6123 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_AUSSTR (500155) -> AUSTROP8 ( 9328) CKT 2 | AEN_DL-AU¦LP_2013 | 138 | 1 | Branch MVA | 480 | - | - | - | - | 108.4286 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_AUSTRO5_1Y ( 7040) -> L_AUSSTR (500154) CKT 1 | 3WT_007040L_AUSTRO5_1Y_009328AUSTROP8_009330AUSTROP_T2 C 2 | 345 | 1 | Branch MVA | 480 | - | - | - | - | 109.5819 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_AUSTRO5_1Y ( 7040) -> L_AUSSTR (500154) CKT 1 | AEN_DL-AU¦LP_2013 | 345 | 1 | Branch MVA | 480 | - | - | - | 100.3181 | 109.7638 | 102.3225 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_AUSTRO5_1Y ( 7040) -> L_AUSSTR (500155) CKT 2 | 3WT_007040L_AUSTRO5_1Y_009328AUSTROP8_009329AUSTROP_T1 C 1 | 345 | 1 | Branch MVA | 480 | - | - | - | - | 109.6123 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_AUSTRO5_1Y ( 7040) -> L_AUSSTR (500155) CKT 2 | AEN_DL-AU¦LP_2013 | 345 | 1 | Branch MVA | 480 | - | - | - | - | 108.4286 | 100.2797 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_AUSTRO5_1Y ( 7040) -> L_GARFIE5_1Y ( 7048) CKT 1 | AEN_LY-FPP:CIS-HO | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 119.0984 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_AUSTRO5_1Y ( 7040) -> L_GARFIE5_1Y ( 7048) CKT 1 | AEN_LY-FPP¦CIS | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 128.724 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_AUSTRO5_1Y ( 7040) -> L_GARFIE5_1Y ( 7048) CKT 1 | LCRA TSC_T255_TAE3121_1 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 127.4815 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_BASTCI8_2Y ( 7319) -> L_SWIFTE8_1Y ( 7326) CKT 1 | AEN_AU-DG¦DL_2013 | 138 | 138 | Branch Amp | 932.9645 | 103.5921 | - | - | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_BEBACK8_1Y ( 7187) -> L_MCCALA8_1Y ( 7182) CKT 1 | L_007180L_ZORN__8_1Y-007182L_MCCALA8_1YC2 | 138 | 138 | Branch Amp | 1928.6844 | - | - | 104.1966 | - | - | - | -
TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_BELLSO8_1Y (7270) -> PETERS__B138 (46220) CKT 1 | Pre-contingency | 138 | 138 | Amps | 1598.1723 | - | - | - | - | 117.0922 | 109.7123 | -
TBBEC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_BRENNO8_1Y ( 7294) -> L_SANDHI8_1Y ( 7570) CKT 1 | L_007289L_SALEM_8_1Y-007564L_GUYBUR8_1YC1 | 138 | 138 | Branch Amp | 527.1458 | 100.8204 | - | 101.467 | 107.9695 | 118.7766 | 113.64 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_COLTON8_1Y ( 7208) -> L_ELROY_8_1Y ( 7209) CKT 1 | L_007310L_SIMGID8_1Y-007555L_BASTWE8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 104.1422 | 107.9962 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_COLTON8_1Y ( 7208) -> L_ELROY_8_1Y ( 7209) CKT 1 | LCRA TSC_T410_T648 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 104.3064 | 101.7147 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_ELROY_8_1Y ( 7209) -> L_WOLFLA8_1Y ( 7212) CKT 1 | L_007310L_SIMGID8_1Y-007555L_BASTWE8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.7705 | 106.5767 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_ELROY_8_1Y ( 7209) -> L_WOLFLA8_1Y ( 7212) CKT 1 | LCRA TSC_T410_T648 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.9326 | 100.3732 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_FLATON8_1Y ( 7248) -> L_MOULTO8_1Y ( 7236) CKT 1 | L_007235L_SWEEHO8_1Y-007249L_MONT__8_1YC1 | 138 | 138 | Branch Amp | 970.6177 | - | - | - | - | 100.0316 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_FLATON8_1Y ( 7248) -> L_MOULTO8_1Y ( 7236) CKT 1 | L_007246L_HALLET8_1Y-007248L_FLATON8_1YC1 | 138 | 138 | Branch Amp | 970.6177 | - | - | - | - | 104.4803 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_FLATON8_1Y ( 7248) -> L_MOULTO8_1Y ( 7236) CKT 1 | L_007246L_HALLET8_1Y-007249L_MONT__8_1YC1 | 138 | 138 | Branch Amp | 970.6177 | - | - | - | - | 101.8298 | - | -
TAEN,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_FPPYD15_1Y ( 7056) -> LOSTPINES ( 9041) CKT 1 | AEN_LY-FPP¦CIS | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 101.24 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_FPPYD15_1Y ( 7056) -> WINCHES ( 9042) CKT 1 | AEN_LY-FPP:CIS-HO | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 114.71 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_FPPYD15_1Y ( 7056) -> WINCHES ( 9042) CKT 1 | AEN_LY-FPP¦CIS | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 121.5014 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_FPPYD15_1Y ( 7056) -> WINCHES ( 9042) CKT 1 | LCRA TSC_T255_TAE3121_1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 117.9435 | - | -
TLCRA,TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_FPPYD25_1Y ( 7055) -> LYTTON5 ( 9074) CKT 1 | AEN_LP-AU¦DL_2013 | 345 | 345 | Branch Amp | 1713.6423 | - | - | - | - | 113.8391 | - | -
TLCRA,TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_FPPYD25_1Y ( 7055) -> LYTTON5 ( 9074) CKT 1 | AEN_P7 FPP-LP.DC_1 | 345 | 345 | Branch Amp | 1713.6423 | - | - | - | - | 106.4023 | - | -
TONCOR,TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | L_FRESNO4A ( 8333) -> STILLMAN (79601) CKT 1 | P7/C5-SHRY-1 | 138 | 138 | Branch Amp | 874.3926 | - | - | - | 140.751 | 142.3102 | 141.522 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GABRIE8_1Y ( 7346) -> JONAHT_8 ( 3539) CKT 1 | GEORGETOWN S - HUTTO_8 (SINGLE B TO B) B | 138 | 138 | Branch Amp | 895.3112 | - | - | 101.7225 | - | 107.6054 | 107.3121 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GABRIE8_1Y ( 7346) -> JONAHT_8 ( 3539) CKT 1 | HUTTO - ROUND ROCK/GEORGETOWN SOUTH (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 895.3112 | - | - | 102.3399 | 107.415 | 108.9462 | 108.5599 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GABRIE8_1Y ( 7346) -> JONAHT_8 ( 3539) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 110.2909 | - | 100.0598 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GABRIE8_1Y ( 7346) -> JONAHT_8 ( 3539) CKT 1 | L_003664RNDRCKWH_T_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | 142.2894 | 149.0432 | 151.5416 | 150.8387 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GABRIE8_1Y ( 7346) -> JONAHT_8 ( 3539) CKT 1 | L_003664RNDRCKWH_T_8-003669RNDRCKWH1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | 142.3521 | 149.1064 | 151.6049 | 150.9021 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GABRIE8_1Y ( 7346) -> JONAHT_8 ( 3539) CKT 1 | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | 170.2604 | 178.2574 | 181.2003 | 180.217 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GABRIE8_1Y ( 7346) -> JONAHT_8 ( 3539) CKT 1 | L_003669RNDRCKWH1_8-007532L_GEORSO8_1YC1 | 138 | 138 | Branch Amp | 895.3112 | - | - | 101.9116 | 106.4546 | 107.9665 | 107.5707 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GABRIE8_1Y ( 7346) -> JONAHT_8 ( 3539) CKT 1 | LCRA TSC_T650_1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 106.1959 | - | - | -
1,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GABRIE8_1Y ( 7346) -> L_GEOREA8_1Y ( 7528) CKT 1 | GEORGETOWN S - HUTTO_8 (SINGLE B TO B) B | 138 | 138 | Branch Amp | 861.8416 | 102.8549 | - | - | - | - | - | -
1,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GABRIE8_1Y ( 7346) -> L_GEOREA8_1Y ( 7528) CKT 1 | HUTTO - ROUND ROCK/GEORGETOWN SOUTH (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | 103.8567 | - | - | - | - | - | -
1,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GABRIE8_1Y ( 7346) -> L_GEOREA8_1Y ( 7528) CKT 1 | L_003664RNDRCKWH_T_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 861.8416 | 144.6537 | - | - | - | - | - | -
1,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GABRIE8_1Y ( 7346) -> L_GEOREA8_1Y ( 7528) CKT 1 | L_003664RNDRCKWH_T_8-003669RNDRCKWH1_8C1 | 138 | 138 | Branch Amp | 861.8416 | 144.7216 | - | - | - | - | - | -
1,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GABRIE8_1Y ( 7346) -> L_GEOREA8_1Y ( 7528) CKT 1 | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 861.8416 | 174.1138 | 114.9499 | - | - | - | - | -
1,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GABRIE8_1Y ( 7346) -> L_GEOREA8_1Y ( 7528) CKT 1 | L_003669RNDRCKWH1_8-007532L_GEORSO8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | 103.0524 | - | - | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GARFIE5_1Y ( 7048) -> LYTTON5 ( 9074) CKT 1 | AEN_LY-FPP:CIS-HO | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 111.5328 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GARFIE5_1Y ( 7048) -> LYTTON5 ( 9074) CKT 1 | AEN_LY-FPP¦CIS | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 122.0046 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GARFIE5_1Y ( 7048) -> LYTTON5 ( 9074) CKT 1 | LCRA TSC_T255_TAE3121_1 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 121.0959 | - | -
TONCOR,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GEOREA8_1Y ( 7528) -> MIDNIGHT_8 ( 3677) CKT 1 | L_003664RNDRCKWH_T_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 861.8416 | 120.2904 | - | 113.8306 | 120.0392 | 122.4324 | 121.8612 | -
TONCOR,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GEOREA8_1Y ( 7528) -> MIDNIGHT_8 ( 3677) CKT 1 | L_003664RNDRCKWH_T_8-003669RNDRCKWH1_8C1 | 138 | 138 | Branch Amp | 861.8416 | 120.3518 | - | 113.8888 | 120.0977 | 122.4909 | 121.9197 | -
TONCOR,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GEOREA8_1Y ( 7528) -> MIDNIGHT_8 ( 3677) CKT 1 | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 861.8416 | 149.2037 | 104.3202 | 142.2783 | 149.7106 | 152.5299 | 151.6953 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GEORGE8_1Y ( 7343) -> L_RIVERY8_1Y ( 7347) CKT 1 | GEORGETOWN S - HUTTO_8 (SINGLE B TO B) B | 138 | 138 | Branch Amp | 907.8623 | 108.5917 | - | - | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GEORGE8_1Y ( 7343) -> L_RIVERY8_1Y ( 7347) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 138 | Branch Amp | 907.8623 | 100.29 | - | 106.8103 | 100.8932 | - | 100.9582 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GEORGE8_1Y ( 7343) -> L_RIVERY8_1Y ( 7347) CKT 1 | L_000132BELLCNTY8-003415TEMP_SS__8C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 102.2916 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GEORGE8_1Y ( 7343) -> L_RIVERY8_1Y ( 7347) CKT 1 | L_000132BELLCNTY8-003640SALADO1_8C1 | 138 | 138 | Branch Amp | 907.8623 | 100.4134 | - | - | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GEORGE8_1Y ( 7343) -> L_RIVERY8_1Y ( 7347) CKT 1 | L_003664RNDRCKWH_T_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 907.8623 | 133.2175 | - | 112.7851 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GEORGE8_1Y ( 7343) -> L_RIVERY8_1Y ( 7347) CKT 1 | L_003664RNDRCKWH_T_8-003669RNDRCKWH1_8C1 | 138 | 138 | Branch Amp | 907.8623 | 133.2619 | - | 112.8285 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GEORGE8_1Y ( 7343) -> L_RIVERY8_1Y ( 7347) CKT 1 | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 907.8623 | 151.9268 | - | 129.8164 | 117.4189 | 115.7287 | 117.7599 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GEORGE8_1Y ( 7343) -> L_RIVERY8_1Y ( 7347) CKT 1 | L_003669RNDRCKWH1_8-007532L_GEORSO8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | 107.2422 | - | - | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GEORGE8_1Y ( 7343) -> L_RIVERY8_1Y ( 7347) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 138 | Branch Amp | 907.8623 | - | - | 102.3741 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_GLIDDE8_1Y ( 7258) -> L_WEIMAR8_1Y ( 7254) CKT 1 | L_007248L_FLATON8_1Y-007279L_MULDOO8_1YC1 | 138 | 138 | Branch Amp | 970.6177 | - | - | - | - | 109.4623 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_HALLET8_1Y ( 7246) -> L_MONT__8_1Y ( 7249) CKT 1 | L_007236L_MOULTO8_1Y-007237L_MOULSO8_1YC1 | 138 | 138 | Branch Amp | 543.8806 | - | - | - | 125.9728 | 147.5379 | 114.9503 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_HALLET8_1Y ( 7246) -> L_MONT__8_1Y ( 7249) CKT 1 | L_007236L_MOULTO8_1Y-007248L_FLATON8_1YC1 | 138 | 138 | Branch Amp | 543.8806 | - | - | - | 126.9327 | 148.4975 | 115.8977 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_HALLET8_1Y ( 7246) -> L_MONT__8_1Y ( 7249) CKT 1 | L_007237L_MOULSO8_1Y-007238L_SHINER8_1YC1 | 138 | 138 | Branch Amp | 543.8806 | - | - | - | 114.1512 | 133.6153 | 103.6658 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_HALLET8_1Y ( 7246) -> L_MONT__8_1Y ( 7249) CKT 1 | L_007238L_SHINER8_1Y-007242L_YOAKUM8_1YC1 | 138 | 138 | Branch Amp | 543.8806 | - | - | - | 109.6722 | 129.108 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_HALLET8_1Y ( 7246) -> L_MONT__8_1Y ( 7249) CKT 1 | LCRA TSC_T134_1 | 138 | 138 | Branch Amp | 543.8806 | - | - | - | 126.3046 | 147.8665 | 115.2807 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_HOWALA8_1Y ( 7335) -> L_WELLBR8_1Y ( 7288) CKT 1 | HUTTO - ROUND ROCK/GEORGETOWN SOUTH (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1870.1125 | 106.3981 | - | - | - | - | - | -
TCPSE,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_MARION5_1Y ( 7044) -> HILLCTY_5 ( 5211) CKT 1 | E5P4A1C1_B | 345 | 345 | Branch Amp | 1778.9081 | - | - | - | - | 112.073 | - | -
TCPSE,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_MARION5_1Y ( 7044) -> HILLCTY_5 ( 5211) CKT 2 | E5P4A1C1_B | 345 | 345 | Branch Amp | 1778.9081 | - | - | - | - | 112.3265 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_MENDOZ8_1Y ( 7325) -> L_COLTON8_1Y ( 7208) CKT 1 | L_007310L_SIMGID8_1Y-007555L_BASTWE8_1YC1 | 138 | 138 | Branch Amp | 970.6177 | - | - | - | - | 104.2883 | 108.1121 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_MENDOZ8_1Y ( 7325) -> L_COLTON8_1Y ( 7208) CKT 1 | LCRA TSC_T410_T648 | 138 | 138 | Branch Amp | 970.6177 | - | - | - | - | 104.4512 | 101.8778 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_MENDOZ8_1Y ( 7325) -> L_LOCKHA8_1Y ( 7216) CKT 1 | AEN_LY-BF¦TV_2017 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 114.8152 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_MENDOZ8_1Y ( 7325) -> L_LOCKHA8_1Y ( 7216) CKT 1 | LCRA TSC_T185_T246 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 111.8886 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_MOULSO8_1Y ( 7237) -> L_MOULSO9_1Y ( 7587) CKT 1 | L_007242L_YOAKUM8_1Y-007244L_CUERO_8_1YC1 | 69 | 138 | Branch MVA | 50 | - | - | - | - | 109.1327 | - | -
TGVEC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_MOULSO9_1Y ( 7587) -> L_SHINGV9_1Y ( 7590) CKT 1 | L_007242L_YOAKUM8_1Y-007244L_CUERO_8_1YC1 | 69 | 69 | Branch Amp | 384.9001 | - | - | - | - | 115.5058 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_MOULTO8_1Y ( 7236) -> L_MOULSO8_1Y ( 7237) CKT 1 | L_007246L_HALLET8_1Y-007248L_FLATON8_1YC1 | 138 | 138 | Branch Amp | 970.6177 | - | - | - | - | 103.4746 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_MOULTO8_1Y ( 7236) -> L_MOULSO8_1Y ( 7237) CKT 1 | L_007246L_HALLET8_1Y-007249L_MONT__8_1YC1 | 138 | 138 | Branch Amp | 970.6177 | - | - | - | - | 100.8294 | - | -
TLCRA | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | L_NORTMC8_2Y (76595) -> L_OXTASW8_1Y (76600) CKT 1 | L_006601RIOPECOS4A-076595L_NORTMC8_2YC1 | 138 | 138 | Branch Amp | 1895.2148 | - | - | 109.9913 | 112.7621 | 118.0413 | 112.3892 | -
TLCRA,TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | L_NORTMC8_2Y (76595) -> RIOPECOS4A ( 6601) CKT 1 | L_006601RIOPECOS4A-076600L_OXTASW8_1YC1 | 138 | 138 | Branch Amp | 1895.2148 | - | - | 110.2014 | 112.9685 | 118.2502 | 112.5743 | -
TLCRA,TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | L_NORTMC8_2Y (76595) -> RIOPECOS4A ( 6601) CKT 1 | L_076595L_NORTMC8_2Y-076600L_OXTASW8_1YC1 | 138 | 138 | Branch Amp | 1895.2148 | - | - | 110.3618 | 113.1401 | 118.4356 | 112.7596 | -
TLCRA,TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | L_NORTMC8_2Y (76595) -> RIOPECOS4A ( 6601) CKT 1 | L2020951 | 138 | 138 | Branch Amp | 1895.2148 | - | - | - | 113.0035 | 118.2871 | 112.6132 | -
TLCRA,TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | L_NORTMC8_2Y (76595) -> RIOPECOS4A ( 6601) CKT 1 | LCRA TSC_T484 | 138 | 138 | Branch Amp | 1895.2148 | - | - | 110.2328 | - | - | - | -
TLCRA,TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | L_OXTASW8_1Y (76600) -> RIOPECOS4A ( 6601) CKT 1 | L_006601RIOPECOS4A-076595L_NORTMC8_2YC1 | 138 | 138 | Branch Amp | 1874.2964 | - | - | 110.9164 | 113.6968 | 119.0092 | 113.2946 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_PAIGE_8_1Y ( 7308) -> L_SIMGID8_1Y ( 7310) CKT 2 | AEN_LP-AU¦DL_2013 | 138 | 138 | Branch Amp | 970.6177 | - | - | - | 111.5401 | 133.8862 | 116.6018 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_PAIGE_8_1Y ( 7308) -> L_SIMGID8_1Y ( 7310) CKT 2 | AEN_LY-FPP:CIS-HO | 138 | 138 | Branch Amp | 970.6177 | - | - | - | - | 101.0043 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_PAIGE_8_1Y ( 7308) -> L_SIMGID8_1Y ( 7310) CKT 2 | AEN_LY-FPP¦CIS | 138 | 138 | Branch Amp | 970.6177 | - | - | - | - | 105.4463 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_PAIGE_8_1Y ( 7308) -> L_SIMGID8_1Y ( 7310) CKT 2 | AEN_P7 FPP-LP.DC_2 | 138 | 138 | Branch Amp | 970.6177 | - | - | - | - | 110.9009 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_PAIGE_8_1Y ( 7308) -> L_SIMGID8_1Y ( 7310) CKT 2 | LCRA TSC_T255_TAE3121_1 | 138 | 138 | Branch Amp | 970.6177 | - | - | - | - | 103.2762 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_RIVERY8_1Y ( 7347) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003664RNDRCKWH_T_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 907.8623 | 103.8011 | - | - | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_RIVERY8_1Y ( 7347) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003664RNDRCKWH_T_8-003669RNDRCKWH1_8C1 | 138 | 138 | Branch Amp | 907.8623 | 103.8431 | - | - | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_RIVERY8_1Y ( 7347) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 907.8623 | 122.1676 | - | - | - | - | - | -
TBBEC | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANDHI8_1Y ( 7570) -> L_GAYHIL8_1Y ( 7572) CKT 1 | L_007289L_SALEM_8_1Y-007564L_GUYBUR8_1YC1 | 138 | 138 | Branch Amp | 527.1458 | - | - | - | - | 106.9281 | 101.913 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | AEN_DL-AU¦LP_2013 | 138 | 138 | Branch Amp | 907.8623 | - | - | 102.1691 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | AEN_GF-SR: EP-HC | 138 | 138 | Branch Amp | 907.8623 | - | - | 105.1985 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | AEN_GF-SR¦EP | 138 | 138 | Branch Amp | 907.8623 | - | - | 105.4717 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | AEN_HC-EP¦PK | 138 | 138 | Branch Amp | 907.8623 | - | - | 105.1367 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | AEN_LY-BF¦TV_2017 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | 102.7295 | - | 109.0213 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | E_FERGCC_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | 103.2119 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_005056CAGNON_5-007046L_KENDAL5_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 100.105 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_007041L_JOHNDU5_1Y-007047L_HORNSB5_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 107.2311 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_007041L_JOHNDU5_1Y-007050L_CLEASP5_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 102.2367 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_007042L_ZORN__5_1Y-007510L_EUCLID5_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 105.0147 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_007042L_ZORN__5_1Y-009074LYTTON5C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 101.9408 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_007043L_HAYSEN5_1Y-007770L_BERGHE5_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 100.4596 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_007047L_HORNSB5_1Y-007738L_WHISVA5_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 103.9921 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_007170L_BERGHE8_1Y-070493P_DEVIHI8_1_C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 101.2524 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_007182L_MCCALA8_1Y-070491P_HUNTER8_1_C1 | 138 | 138 | Branch Amp | 907.8623 | 105.9298 | - | 120.4846 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_007192L_SANMAR8_1Y-070502P_KYLE__8_1_C1 | 138 | 138 | Branch Amp | 907.8623 | 108.3302 | - | 130.0877 | - | - | 103.5216 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_007340L_GILLCR5_1Y-007738L_WHISVA5_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 101.9865 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_007341L_LIMMER5_1Y-007510L_EUCLID5_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 101.8135 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_007500L_TURNER8_1Y-009075LYTTON8C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 115.7757 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_009071GARFIELD8-009143EASTONPARKC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 101.949 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_009143EASTONPARK-009147HICROS_DB1C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 101.7261 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_070198P_LEHIGH8_1_-070498P_BUDA__8_1_C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 118.1943 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_070198P_LEHIGH8_1_-070502P_KYLE__8_1_C1 | 138 | 138 | Branch Amp | 907.8623 | 103.2691 | - | 124.1178 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_070487P_CANYHY8_1_-070488P_SATTLE8_1_C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 115.7883 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_070487P_CANYHY8_1_-070492P_FISCHE8_1_C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 115.7804 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_070488P_SATTLE8_1_-070489P_PURGRO8_1_C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 115.376 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_070489P_PURGRO8_1_-070491P_HUNTER8_1_C1 | 138 | 138 | Branch Amp | 907.8623 | 102.6721 | - | 117.7948 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | L_070492P_FISCHE8_1_-070546P_HIGH328_1_C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 105.8194 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRA TSC_T148_T459 | 138 | 138 | Branch Amp | 907.8623 | - | - | 100.5303 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRA TSC_T185_T246 | 138 | 138 | Branch Amp | 907.8623 | - | - | 111.3877 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRA TSC_T185_T352 | 138 | 138 | Branch Amp | 907.8623 | - | - | 102.2025 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRA TSC_T237_T389_1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 106.3265 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRA TSC_T244_T459 | 138 | 138 | Branch Amp | 907.8623 | - | - | 100.613 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRA TSC_T382_T987_1 | 138 | 138 | Branch Amp | 907.8623 | 106.9626 | - | 124.6802 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRA TSC_T389_T493_1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 102.6853 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRA TSC_T389_T518 | 138 | 138 | Branch Amp | 907.8623 | - | - | 105.7281 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRA TSC_T389_T610 | 138 | 138 | Branch Amp | 907.8623 | - | - | 104.1008 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRA TSC_T510_1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 104.1986 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRA TSC_T510_T511_3 | 138 | 138 | Branch Amp | 907.8623 | - | - | 113.8169 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRA TSC_T510_T512_1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 104.7947 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRA TSC_T510_T738_1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 114.8472 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRA TSC_T510_T775 | 138 | 138 | Branch Amp | 907.8623 | - | - | 120.1439 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRA TSC_T511_T625_2 | 138 | 138 | Branch Amp | 907.8623 | - | - | 102.2542 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRATSC_2_LIMMER_GILLCR | 138 | 138 | Branch Amp | 907.8623 | - | - | 102.0375 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRATSC_3_GILLCR_WHISVA | 138 | 138 | Branch Amp | 907.8623 | - | - | 111.1429 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRATSC_4_WHISVA_HORNSB | 138 | 138 | Branch Amp | 907.8623 | - | - | 113.7689 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRATSC_5_HORNSB_EUCLID | 138 | 138 | Branch Amp | 907.8623 | - | - | 117.8627 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRATSC_6_EUCLID_JOHNDU | 138 | 138 | Branch Amp | 907.8623 | - | - | 122.2805 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRATSC_7_JOHNDU_ZORN__ | 138 | 138 | Branch Amp | 907.8623 | - | - | 115.766 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LCRATSC_8_ZORN___CLEASP | 138 | 138 | Branch Amp | 907.8623 | - | - | 103.5184 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | LIMMER SS - GILLELAND/ZORN_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 907.8623 | - | - | 104.0233 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | PEC_T319 | 138 | 138 | Branch Amp | 907.8623 | - | - | 115.7807 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | PEC_T324_T699_1 | 138 | 138 | Branch Amp | 907.8623 | 100.4602 | - | 113.6915 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | PEC_T466_T524 | 138 | 138 | Branch Amp | 907.8623 | - | - | 116.3808 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | PEC_T466_T524_A | 138 | 138 | Branch Amp | 907.8623 | - | - | 116.3808 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | R4LCA2C1_B | 138 | 138 | Branch Amp | 907.8623 | - | - | 100.5278 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SANMAR8_1Y ( 7192) -> L_CANYON8_1Y ( 7200) CKT 1 | R4LCA3C11B | 138 | 138 | Branch Amp | 907.8623 | - | - | 100.8569 | - | - | - | -
TGVEC | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SCHERT8_1Y ( 7610) -> L_PARKWA8_1Y ( 7611) CKT 1 | E5T5A1C1_B | 138 | 138 | Branch Amp | 1497.7635 | - | - | - | - | 101.5215 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SHINGV9_1Y ( 7590) -> L_KOKERN9_1Y ( 7591) CKT 1 | L_007242L_YOAKUM8_1Y-007244L_CUERO_8_1YC1 | 69 | 69 | Branch Amp | 384.9001 | - | - | - | - | 115.4014 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | AEN_DL-AU¦LP_2013 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 109.4414 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | AEN_LP-AU¦DL_2013 | 138 | 138 | Branch Amp | 907.8623 | - | - | 101.1523 | 122.1377 | 138.8022 | 124.0564 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | AEN_LY-FPP:CIS-HO | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.0408 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | AEN_LY-FPP¦CIS | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 105.7215 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | AEN_P7 FPP-LP.DC_2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | 103.4313 | 118.7023 | 105.7397 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | L_007310L_SIMGID8_1Y-007319L_BASTCI8_2YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 108.8089 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | L_007310L_SIMGID8_1Y-007327L_SETTLE8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 111.0804 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | L_007310L_SIMGID8_1Y-007555L_BASTWE8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.1619 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | L_007319L_BASTCI8_2Y-007326L_SWIFTE8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 108.8239 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | L_007326L_SWIFTE8_1Y-007331L_CEDAHI8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 106.7879 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | L_007328L_SETTLE8_2Y-007329L_WEBBER8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | 105.0312 | 112.7672 | 104.7234 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | L_007329L_WEBBER8_1Y-009328AUSTROP8C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 105.8204 | 117.8803 | 120.0561 | 118.9207 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | L_007330L_MANOR_8_1Y-007331L_CEDAHI8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.0518 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | LCRA TSC_T150_T608 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.1131 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | LCRA TSC_T150_T608_A | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.2493 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | LCRA TSC_T171_1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.1886 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | LCRA TSC_T255_TAE3121_1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 104.9492 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | LCRA TSC_T410_T648 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | 101.8445 | 113.9465 | 101.332 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_1Y ( 7322) CKT 1 | LCRA TSC_T608 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 108.8121 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_BASTCI8_2Y ( 7319) CKT 1 | AEN_AU-DG¦DL_2013 | 138 | 138 | Branch Amp | 932.9645 | 103.5783 | - | - | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_SETTLE8_1Y ( 7327) CKT 1 | AEN_DL-AU¦LP_2013 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.503 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_SETTLE8_1Y ( 7327) CKT 1 | AEN_LP-AU¦DL_2013 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | 110.1616 | 123.4956 | 111.5655 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_SETTLE8_1Y ( 7327) CKT 1 | AEN_P7 FPP-LP.DC_2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 108.2534 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_SETTLE8_1Y ( 7327) CKT 1 | L_007310L_SIMGID8_1Y-007319L_BASTCI8_2YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.6658 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_SETTLE8_1Y ( 7327) CKT 1 | L_007310L_SIMGID8_1Y-007322L_BASTCI8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 104.1637 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_SETTLE8_1Y ( 7327) CKT 1 | L_007319L_BASTCI8_2Y-007326L_SWIFTE8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.6755 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_SETTLE8_1Y ( 7327) CKT 1 | L_007327L_SETTLE8_1Y-009328AUSTROP8C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0157 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_SETTLE8_1Y ( 7327) CKT 1 | LCRA TSC_T410_T648 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 104.5374 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SIMGID8_1Y ( 7310) -> L_SETTLE8_1Y ( 7327) CKT 1 | LCRA TSC_T608 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.6685 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_SMITHV8_1Y ( 7314) -> L_ALUMCR8_1Y ( 7318) CKT 1 | AEN_LP-AU¦DL_2013 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 111.1611 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_STRAHA8_1Y ( 7193) -> L_SANMAR8_1Y ( 7192) CKT 1 | L_007182L_MCCALA8_1Y-007184L_RATTLE8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 109.1423 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_STRAHA8_1Y ( 7193) -> L_SANMAR8_1Y ( 7192) CKT 1 | L_007184L_RATTLE8_1Y-007188L_REDWOO8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | 106.4223 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_STRAHA8_1Y ( 7193) -> L_SANMAR8_1Y ( 7192) CKT 1 | LCRA TSC_BF_BUS7184 | 138 | 138 | Branch Amp | 907.8623 | - | - | 107.2745 | - | - | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | BAS_RANCH_CON | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 102.113 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | G_136101BLUESKY_S1US1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 101.7079 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | G_888839BAS_RANCH_POIUC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 102.0394 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_000844GPL_NEVILLSW-076000L_NORTMC5_1YC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 101.8615 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_006450CONCHO2A-006527SANW2AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 102.6886 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_006477SAMATHIS2A-006527SANW2AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 102.0402 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_006477SAMATHIS2A-006528TANK2AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 100.8868 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_006490SANTIAGO4A-006500LVOK4AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 100.354 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_006500LVOK4A-060412CARVER4AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 102.1462 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_006525ESMERALD4A-006562FDRAN4AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | 103.8828 | 113.5968 | 105.3664 | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_006526MERR2A-006529MERT2AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 100.5008 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_006528TANK2A-006529MERT2AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 100.8605 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_006536BIGLAKE4B-060414OWLS4AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 111.79 | 100.2364 | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_006562FDRAN4A-060412CARVER4AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 102.2838 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_006562FDRAN4A-136103BLUESKY_8C1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 101.7369 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_059902SAND_BLUFF-059907BERNOULLIC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 100.1801 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_059903BEARKAT-059907BERNOULLIC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 100.7413 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_060361SANTARIT4A-060414OWLS4AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | 104.7631 | 116.8786 | 107.2183 | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | 106.3384 | 118.635 | 108.936 | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_060723CROSSOVE4A-060728PALOUSE4AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 109.402 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_060723CROSSOVE4A-076032L_NORTMC8_1YC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 109.537 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | 108.1199 | 120.659 | 110.9147 | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_076011L_TWINBU8_1Y-900117Other_90_SOC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 109.2188 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_076032L_NORTMC8_1Y-900113Other_81_SOC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 100.4118 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L_900110Other_86_MO-900117Other_90_SOC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 107.1735 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L2020562 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 102.0482 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L2020574 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 102.8724 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L2020933-B | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 100.0462 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L2020944-A | 138 | 138 | Branch Amp | 631.7383 | - | - | - | 106.2786 | 118.5608 | 108.8818 | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | L2020944-B | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 109.3958 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | LCRA TSC_BAKERS_CEDACA_DC | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 107.5763 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 105.2588 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-2 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 104.3152 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 105.2586 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-2 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 104.3151 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | LCRA TSC_NOELK_SNGTR_NOELK_SNGTR2 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 104.0308 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | LCRA TSC_SNGTR_SCHDR_SNGTR_SCHDR2 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 102.9432 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | LCRA TSC_T422_T550 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 100.951 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 105.368 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | MB2056220574 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 102.2346 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | STECL_10594 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 100.0231 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | STECL_4720 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 103.7226 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | STECL_4721-1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 105.2588 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | STECL_4721-2 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 104.3153 | - | -
TAEPTN,TLCRA | WEST | WEST | WEST, WEST | L_TWINBU8_1Y (76011) -> HARGROVE4A ( 6648) CKT 1 | T_006535BIGLAKE4A-006536BIGLAKE4BC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 109.6736 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WEIMAR8_1Y ( 7254) -> L_SCHULE8_1Y ( 7252) CKT 1 | L_007248L_FLATON8_1Y-007279L_MULDOO8_1YC1 | 138 | 138 | Branch Amp | 970.6177 | - | - | - | - | 103.485 | - | -
TSTEC,TLCRA | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | L_WESER_9_1Y ( 7239) -> CHARCOSUB9 ( 5732) CKT 1 | L_005502RAYBURN8-005730FORCORNERSB8C1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 102.1105 | - | -
TSTEC,TLCRA | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | L_WESER_9_1Y ( 7239) -> CHARCOSUB9 ( 5732) CKT 1 | L_005728CHOATESUB8-005730FORCORNERSB8C1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.5958 | - | -
TSTEC,TLCRA | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | L_WESER_9_1Y ( 7239) -> CHARCOSUB9 ( 5732) CKT 1 | STECL_10131 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 101.0305 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | 3WT_007040L_AUSTRO5_1Y_009328AUSTROP8_009329AUSTROP_T1 C 1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 104.1968 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | 3WT_007040L_AUSTRO5_1Y_009328AUSTROP8_009330AUSTROP_T2 C 2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 104.0589 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | 3WT_009044DUNLAP5_009045DUNLAP8_090001DUNLAP_TR C 1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 103.2471 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | 3WT_009044DUNLAP5_009045DUNLAP8_090007DUNLAP_TR2 C 2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 103.2471 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | 3WT_009074LYTTON5_009075LYTTON8_009078LYTTON_T1 C 1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.2764 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | 3WT_009074LYTTON5_009075LYTTON8_009081LYTTON_T2 C 2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.962 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | 3WT_009074LYTTON5_009075LYTTON8_077075L_LYTTSP2_1Y C 3 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.9847 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | AEN_DL-AU¦LP_2013 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | 106.0033 | 119.9707 | 109.0596 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | AEN_DP-SK¦MC | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.2251 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | AEN_FPP-HO¦LY | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.4816 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | AEN_GF-SR: EP-HC | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.7971 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | AEN_GF-SR¦EP | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.9258 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | AEN_HC-EP¦PK | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0876 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | AEN_LP-AU¦DL_2013 | 138 | 138 | Branch Amp | 907.8623 | 120.5983 | - | 106.1019 | 144.3019 | 169.1201 | 149.2897 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | AEN_LY-FPP:CIS-HO | 138 | 138 | Branch Amp | 907.8623 | - | - | - | 111.4274 | 133.4165 | 113.441 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | AEN_LY-FPP¦CIS | 138 | 138 | Branch Amp | 907.8623 | - | - | - | 115.5663 | 138.7041 | 117.4237 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | AEN_P1-1_GEN_SH5A+5C | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.4738 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | AEN_P7 FPP-LP.DC_2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | 120.4291 | 143.9212 | 126.0724 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | BAS_RANCH_CON | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 103.5651 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | BAY5_BF | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.5013 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 108.2028 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 106.7064 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.6407 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | BLUBIRD_CON | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.6586 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 105.6382 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | DVCPA1C21B_1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 103.7192 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | DVCPA1C21B_2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 103.0554 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_B_DAVIS_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.3612 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_BASTEN_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.7776 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_BRAUNIG_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.3231 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_FERGCC_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.6258 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_FRNYPP_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.8243 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_FRNYPP_CC2_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.8332 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_GUADG_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.4256 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_GUADG_CC2_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.4136 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_INGLCOSW_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0473 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_JACKCNTY_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0168 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_JCKCNTY2_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.1723 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_KMCHI_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0023 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_KMCHI_CC2_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0117 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_NEDIN_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.5118 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_NUECES_B_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.5545 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_OECCS_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.3392 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_OECCS_CC2_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.3447 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_PANDA_S_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.2561 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_PANDA_T1_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.1997 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_PANDA_T2_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.1832 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_TGCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.1347 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_WCPP_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.6882 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_WHCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.5265 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | E_WHCCS2_CC2_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.5113 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_000575JCKCNTY5UN1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.2893 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_000579JCKCNTY8UN1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.1176 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_006100OKLA7AUC0 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.4482 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_007044L_MARION5_1YUN1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.3234 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_007048L_GARFIE5_1YUN1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.4825 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_010012METEOR_5US1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0765 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_120041MLSES_UNIT1UL1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0522 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_120042MLSES_UNIT2UL2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0691 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_120043MLSES_UNIT3UL3 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0784 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_150023MCSES_UNIT8UN8 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.1019 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_150111CPSES_UNIT1UU1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.8116 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_150112CPSES_UNIT2UU2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.826 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_150741SCES_UNIT1UL1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.9053 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_170071GID_GIDEONG1UN1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 104.6917 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_170072GID_GIDEONG2UN2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 104.8885 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_170073GID_GIDEONG3UN3 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | 100.7278 | 114.7962 | 103.3169 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_170126CALAVER_JKS2UL2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.5265 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_888839BAS_RANCH_POIUC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 103.5616 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_888851TRIFECTA_POIUN1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0138 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_888879BLUBIRD_POIUS1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.6135 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | G_RIO_TRAIN | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.0491 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | HOLLY_CON | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.4481 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 907.8623 | - | - | - | 101.7044 | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | J5LCA1C1_B | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.0631 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_000132BELLCNTY8-003415TEMP_SS__8C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.171 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.5579 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.2491 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.0943 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.8316 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.8274 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_003377LITTLEPOND_5-003687BELL_E_5C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.4651 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_003384STJOHNS_5-003409LAKE_CRK1_5C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.1344 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.0248 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 121.276 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_003541BRUSHYCRK_8-003712TORTOISE_8C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.2542 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_003687BELL_E_5-003705BRANGUS_5C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.6337 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.5881 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.5881 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_003705BRANGUS_5-003706GIBSON_5C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.3055 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 110.0566 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 103.9225 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 105.6396 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.7647 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_005380SHAULA-005915SO_TEX__345AC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.7713 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.9546 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 106.2912 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007040L_AUSTRO5_1Y-009041LOSTPINESC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 111.7499 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007041L_JOHNDU5_1Y-007047L_HORNSB5_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.592 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007042L_ZORN__5_1Y-007510L_EUCLID5_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.0208 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007042L_ZORN__5_1Y-009074LYTTON5C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.3539 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007047L_HORNSB5_1Y-007738L_WHISVA5_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.2632 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.7786 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007055L_FPPYD25_1Y-009074LYTTON5C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 110.2606 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007056L_FPPYD15_1Y-009041LOSTPINESC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 104.6222 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007208L_COLTON8_1Y-007209L_ELROY_8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.2014 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007208L_COLTON8_1Y-007325L_MENDOZ8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.9449 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007209L_ELROY_8_1Y-007212L_WOLFLA8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0659 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007236L_MOULTO8_1Y-007237L_MOULSO8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.6682 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007236L_MOULTO8_1Y-007248L_FLATON8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.6979 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007242L_YOAKUM8_1Y-007244L_CUERO_8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.5427 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007248L_FLATON8_1Y-007279L_MULDOO8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 105.662 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007306L_WINCHE8_1Y-007310L_SIMGID8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | 101.9032 | 118.3257 | 105.6177 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007306L_WINCHE8_1Y-007314L_SMITHV8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 113.8068 | 101.8244 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007310L_SIMGID8_1Y-007318L_ALUMCR8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 110.4182 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007314L_SMITHV8_1Y-007318L_ALUMCR8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 111.1611 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007325L_MENDOZ8_1Y-009075LYTTON8C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 103.1239 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007327L_SETTLE8_1Y-009328AUSTROP8C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0379 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007328L_SETTLE8_2Y-007329L_WEBBER8_1YC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.8183 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_007329L_WEBBER8_1Y-009328AUSTROP8C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.5758 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_009041LOSTPINES-009042WINCHESC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 114.9033 | 102.5968 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_009041LOSTPINES-009044DUNLAP5C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 108.7976 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_009043CISTERN-009073HOLMANC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 111.0349 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_009043CISTERN-009074LYTTON5C1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 114.0769 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_009071GARFIELD8-009143EASTONPARKC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0548 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_040600ROANS__POI_5-044645SNGLTN__B345C75 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0476 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | L_080071ZORILLO7A-080076AJO7AC1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0559 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LAKE CREEK - RATTLE SNAKE 345 KV WITH SANDY UNIT (SINGLE B TO B) | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.9054 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LAKE CREEK-RATTLESNAKE/ST JOHNS_5 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.1351 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LCRA TSC_T134_1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.7124 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LCRA TSC_T150 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 110.7537 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LCRA TSC_T150_T344 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 111.5341 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LCRA TSC_T150_T344_A | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 111.1308 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LCRA TSC_T185_T246 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 103.6968 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LCRA TSC_T255_TAE3121_1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | 112.8553 | 136.4889 | 114.2458 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LCRA TSC_T510_1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.7952 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LCRA TSC_T510_T512_1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.8838 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LCRA TSC_T510_T775 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.6612 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LCRATSC_1_HUTTO__LIMMER | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.2672 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LCRATSC_4_WHISVA_HORNSB | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.3903 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LCRATSC_5_HORNSB_EUCLID | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.9417 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LCRATSC_6_EUCLID_JOHNDU | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 106.1494 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LCRATSC_7_JOHNDU_ZORN__ | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.9375 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 104.2512 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | M10000271115801 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.4576 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | M115851115803 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0559 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | MB100002711580 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.4576 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | MB1158011585 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0559 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | MB210140210145-AAAAA | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0705 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | MB210140210145-AAAAB | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.1943 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.7479 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.6588 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | N5GSU2_B | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.5265 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.213 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | P7-1_E1>>T1839X1_ERC | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 103.0022 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | P7-1_E1>>T1839X2_ERC | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 103.6717 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | P7-1_E1>>T1850A1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.3544 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | P7-1_E1>>T2764Y_ERCa | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 103.0266 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | P7-1_E1>>T3944Z_ERC | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.2184 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | P7-1_E1>>T4848K | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.3118 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | P7-1_E1>>T7475A | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.5041 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | P7-1_E1>>T7498C_ERC | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.5804 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.833 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | R4U2A5C1_1_B | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.3649 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | RAT_SNAKE-SNDY_CREEK_5 (SINGLE B TO B) | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.9053 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | STP - HOUDINI & STP - SHAULA | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.9755 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 104.0969 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.259 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 103.2089 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | TRIFECTA_CON | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0151 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.3625 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.1536 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 101.9947 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.1226 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.1013 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0209 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.5625 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | WAP - HOUDINI & STP - SHAULA | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 102.57 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.6883 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | XFMR-MARTINLK_5-1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0522 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | XFMR-MARTINLK_5-2 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0691 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | XFMR-MARTINLK_5-3 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.0784 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | XFMR-MTCK_8T8-8 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.1019 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | XFMR-SANDYCRK_5-01 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.9053 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_PAIGE_8_1Y ( 7308) CKT 1 | XFMR-WHCCS2_5-1 | 138 | 138 | Branch Amp | 907.8623 | - | - | - | - | 100.6374 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | AEN_DL-AU¦LP_2013 | 138 | 138 | Branch Amp | 790.7188 | - | - | - | 109.3954 | - | 113.0239 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | AEN_LP-AU¦DL_2013 | 138 | 138 | Branch Amp | 790.7188 | 126.1528 | - | 109.3685 | 153.6389 | - | 159.6073 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | AEN_LY-FPP:CIS-HO | 138 | 138 | Branch Amp | 790.7188 | - | - | - | 115.5461 | - | 118.1715 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | AEN_LY-FPP¦CIS | 138 | 138 | Branch Amp | 790.7188 | - | - | - | 120.3969 | - | 122.8625 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | AEN_P7 FPP-LP.DC_2 | 138 | 138 | Branch Amp | 790.7188 | 102.4064 | - | - | 126.0493 | - | 132.7968 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | G_170073GID_GIDEONG3UN3 | 138 | 138 | Branch Amp | 790.7188 | - | - | - | 102.7458 | - | 105.9908 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 790.7188 | - | - | - | 103.6959 | - | 102.041 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | L_007040L_AUSTRO5_1Y-009041LOSTPINESC1 | 138 | 138 | Branch Amp | 790.7188 | - | - | - | - | - | 102.1483 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | L_007306L_WINCHE8_1Y-007308L_PAIGE_8_1YC1 | 138 | 138 | Branch Amp | 790.7188 | - | - | - | 107.2786 | - | 111.7799 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | L_007306L_WINCHE8_1Y-007314L_SMITHV8_1YC1 | 138 | 138 | Branch Amp | 790.7188 | - | - | - | 100.422 | - | 104.8473 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | L_007308L_PAIGE_8_1Y-007310L_SIMGID8_1YC2 | 138 | 138 | Branch Amp | 790.7188 | - | - | - | 100.8379 | - | 105.6047 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | L_007310L_SIMGID8_1Y-007318L_ALUMCR8_1YC1 | 138 | 138 | Branch Amp | 790.7188 | - | - | - | - | - | 101.1766 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | L_007314L_SMITHV8_1Y-007318L_ALUMCR8_1YC1 | 138 | 138 | Branch Amp | 790.7188 | - | - | - | - | - | 101.9942 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | L_009041LOSTPINES-009042WINCHESC1 | 138 | 138 | Branch Amp | 790.7188 | - | - | - | - | - | 105.6704 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | L_009043CISTERN-009074LYTTON5C1 | 138 | 138 | Branch Amp | 790.7188 | - | - | - | - | - | 102.1512 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | LCRA TSC_T150 | 138 | 138 | Branch Amp | 790.7188 | - | - | - | - | - | 101.5449 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | LCRA TSC_T150_T344 | 138 | 138 | Branch Amp | 790.7188 | - | - | - | - | - | 102.401 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | LCRA TSC_T150_T344_A | 138 | 138 | Branch Amp | 790.7188 | - | - | - | - | - | 101.9505 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SIMGID8_1Y ( 7310) CKT 1 | LCRA TSC_T255_TAE3121_1 | 138 | 138 | Branch Amp | 790.7188 | - | - | - | 117.2713 | - | 119.0555 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y ( 7306) -> L_SMITHV8_1Y ( 7314) CKT 1 | AEN_LP-AU¦DL_2013 | 138 | 138 | Branch Amp | 970.6177 | - | - | - | - | 116.001 | 102.2516 | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_WINCHE8_1Y (7306) -> L_SIMGID8_1Y (7310) CKT 1 | Pre-contingency | 138 | 138 | Amps | 790.7188 | - | - | - | - | 100.7599 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_ZORN__8_1Y ( 7180) -> L_BEBACK8_1Y ( 7187) CKT 1 | L_007180L_ZORN__8_1Y-007182L_MCCALA8_1YC2 | 138 | 138 | Branch Amp | 1999.8074 | - | - | 103.4178 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_ZORN__8_1Y ( 7180) -> L_MCCALA8_1Y ( 7182) CKT 2 | L_007180L_ZORN__8_1Y-007187L_BEBACK8_1YC1 | 138 | 138 | Branch Amp | 1928.6844 | - | - | 109.6949 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_ZORN__8_1Y ( 7180) -> L_MCCALA8_1Y ( 7182) CKT 2 | L_007182L_MCCALA8_1Y-007187L_BEBACK8_1YC1 | 138 | 138 | Branch Amp | 1928.6844 | - | - | 107.9617 | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | L_ZORN__8_1Y ( 7180) -> L_MCCALA8_1Y ( 7182) CKT 2 | LCRA TSC_T201 | 138 | 138 | Branch Amp | 1928.6844 | - | - | 108.497 | - | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LA_PALMA4A ( 8314) -> CAVAZOS4A (80229) CKT 1 | P7/C5-SHRY-1 | 138 | 138 | Branch Amp | 978.9851 | - | - | - | 109.2233 | 109.8427 | 110.021 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LA_PALMA4A ( 8314) -> L_FRESNO4A ( 8333) CKT 1 | P7/C5-SHRY-1 | 138 | 138 | Branch Amp | 945.5156 | - | - | - | 146.2393 | 147.6228 | 146.8764 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LA_PALMA7A ( 8317) -> CANDELA7A ( 8709) CKT 1 | L_008704GULCH7A-08709CANDELA7AC1 | 345 | 345 | Branch Amp | 1914.4597 | - | - | 101.5236 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKE_CRK2_5 ( 3402) -> LAKE_HALL_5 ( 3403) CKT 1 | L_003404BELFALLS_8-003414TEMP_SS__5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 102.8069 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKE_CRK2_5 ( 3402) -> LAKE_HALL_5 ( 3403) CKT 1 | L_003409LAKE_CRK1_5-013405THOUSE_A_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4561 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKE_CRK2_5 ( 3402) -> LAKE_HALL_5 ( 3403) CKT 1 | L_013401TIGERCK_5-013405THOUSE_A_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.4345 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKE_CRK2_5 ( 3402) -> LAKE_HALL_5 ( 3403) CKT 1 | L_013401TIGERCK_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 114.9686 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKE_CRK2_5 ( 3402) -> LAKE_HALL_5 ( 3403) CKT 1 | TEMPLE - BELFALLS_5 (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 102.8069 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKE_HALL_5 ( 3403) -> THOUSE__5 ( 3405) CKT 1 | L_003306STEKLY_DAM_5-003404BELFALLS_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.8429 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKE_HALL_5 ( 3403) -> THOUSE__5 ( 3405) CKT 1 | L_003404BELFALLS_8-003414TEMP_SS__5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.3462 | 108.3845 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKE_HALL_5 ( 3403) -> THOUSE__5 ( 3405) CKT 1 | L_003409LAKE_CRK1_5-013405THOUSE_A_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 106.0808 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKE_HALL_5 ( 3403) -> THOUSE__5 ( 3405) CKT 1 | L_013401TIGERCK_5-013405THOUSE_A_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 106.0754 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKE_HALL_5 ( 3403) -> THOUSE__5 ( 3405) CKT 1 | L_013401TIGERCK_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 120.7804 | 100.6881 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKE_HALL_5 ( 3403) -> THOUSE__5 ( 3405) CKT 1 | TEMPLE - BELFALLS_5 (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.3462 | 108.3845 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKE_HALL_5 ( 3403) -> THOUSE__5 ( 3405) CKT 1 | TEMPLE PECAN CREEK/BELFALLS - TEMPLE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.9012 | 100.5208 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKECRST_8 (12492) -> FSHCRK1_8 ( 2491) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 101.0994 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKECRST_8 (12492) -> FSHCRK1_8 ( 2491) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 120.2062 | 130.9093 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKECRST_8 (12492) -> FSHCRK1_8 ( 2491) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 122.1518 | 132.6877 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKECRST_8 (12492) -> FSHCRK1_8 ( 2491) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.9465 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKECRST_8 (12492) -> FSHCRK1_8 ( 2491) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.779 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LAKECRST_8 (12492) -> FSHCRK1_8 ( 2491) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.5924 | - | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 100.9075 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | E5DVA1C1_1_B | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 108.0812 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | E5DVA1C1_1_B_2 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 100.9917 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | G_113161TEXANA_S1US1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 104.5597 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | G8DVA1C1_B | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 103.8031 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_005521GALOWSW8-111583MUSTNGCK_8C1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 102.2796 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_007270L_BELLSO8_1Y-046220PETERS__B138C1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 101.3436 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_008111MAGILL4A-008113BAY_CITY4AC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 102.3401 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_008111MAGILL4A-008668CHALMERS4AC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 104.1261 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_008113BAY_CITY4A-080124BLKCAT4AC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 100.1867 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_008121BLESSING4A-008614PAVLOV4BC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 110.106 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_008127LAN_CTY4A-008608PAVLOV4AC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 110.7229 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_008127LAN_CTY4A-008668CHALMERS4AC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 104.6782 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_008192PULSAR4A-008675TEXNAPOI4AC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 104.5597 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_008715RADIANT7A-008728COBRA7AC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 101.5434 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_008728COBRA7A-081003HABER7AC1 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 103.2889 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_042420BEASLY_POI_8-044541ORCHRD_T60_8C60 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 104.7703 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_042985DYANN__POI_8-043570WHARTN__60B8C&1-MS | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 129.7211 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_043090PYTHIA_POI_8-043110SANBER_POI_8C60 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 106.3556 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_043090PYTHIA_POI_8-043380W_COL__POI_8C60 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 108.5473 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_043110SANBER_POI_8-043340GLFTIE_POI_8C&1-MS | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 102.1403 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_043570WHARTN__60B8-044150HNGFRD_POI_8C&1-MS | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 125.7784 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_044150HNGFRD_POI_8-044190E_BERN__B138C60 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 142.424 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_044190E_BERN__B138-044740WALLIS_S65_8C65 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 101.3671 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_044280FTBEND__B138-044615ROSNBG_S60_8C60 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 102.0068 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_044540ORCHRD_S60_8-044615ROSNBG_S60_8C&1-MS | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 104.5731 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_044640SEALY__S65_8-044700GEBHRT_X65B8C65 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 112.1919 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_044640SEALY__S65_8-046220PETERS__B138C65 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 110.1027 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_044700GEBHRT_X65B8-888872SKYSLY_POIC65 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 112.8868 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L_888872SKYSLY_POI-044740WALLIS_S65_8C65 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 101.1403 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L10010009 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 110.7354 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L10010024 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 100.3485 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | L10010074 | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 104.7417 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | LCRA TSC_T698_T217_A | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 101.382 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | P1-2_(21.2_SODG_44541) | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 104.7221 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | P7-1_E1>>T6060D | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 129.8361 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | P7-1_E1>>T6472CX1A | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 101.3545 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | P7-1_E1>>T6472CX1B | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 100.462 | -
TAEPTN,TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> LANCTYPM4A ( 8104) CKT 1 | SKYSLY_CON | 138 | 138 | Branch Amp | 882.7601 | - | - | - | - | - | 101.4216 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> PAVLOV4A ( 8608) CKT 1 | L_005915SO_TEX__345A-008123BLESSING7AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 102.8702 | - | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> PAVLOV4A ( 8608) CKT 1 | L_008102EL_CAMPO4A-008679ARROZ4AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 133.5879 | 130.867 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> PAVLOV4A ( 8608) CKT 1 | L_008104LANCTYPM4A-008127LAN_CTY4AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 124.8018 | 122.2471 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> PAVLOV4A ( 8608) CKT 1 | L_008104LANCTYPM4A-008679ARROZ4AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 124.4841 | 121.9342 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> PAVLOV4A ( 8608) CKT 1 | L_008111MAGILL4A-008668CHALMERS4AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | - | 100.1152 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> PAVLOV4A ( 8608) CKT 1 | L_008127LAN_CTY4A-008668CHALMERS4AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | - | 101.2875 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> PAVLOV4A ( 8608) CKT 1 | L_042985DYANN__POI_8-043570WHARTN__60B8C&1-MS | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 103.5587 | 116.2286 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> PAVLOV4A ( 8608) CKT 1 | L_043570WHARTN__60B8-044150HNGFRD_POI_8C&1-MS | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | - | 112.027 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> PAVLOV4A ( 8608) CKT 1 | L_044150HNGFRD_POI_8-044190E_BERN__B138C60 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 112.2936 | 129.8198 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> PAVLOV4A ( 8608) CKT 1 | L10006-1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 125.7002 | 122.8124 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> PAVLOV4A ( 8608) CKT 1 | L10010006-1B | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 124.7683 | 122.2254 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> PAVLOV4A ( 8608) CKT 1 | L10010074 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | - | 100.9628 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> PAVLOV4A ( 8608) CKT 1 | P7-1_E1>>T6060D | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 103.4636 | 116.3462 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> PAVLOV4A ( 8608) CKT 1 | T_008121BLESSING4A-008123BLESSING7AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 102.859 | - | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4A ( 8127) -> PAVLOV4A ( 8608) CKT 1 | T100002 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 133.0618 | 130.838 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4B ( 8130) -> LAN_CTY4A ( 8127) CKT S1 | L_042985DYANN__POI_8-043570WHARTN__60B8C&1-MS | 138 | 138 | Branch Amp | 2200.6248 | - | - | - | - | 121.9278 | 115.4032 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4B ( 8130) -> LAN_CTY4A ( 8127) CKT S1 | L_043090PYTHIA_POI_8-043110SANBER_POI_8C60 | 138 | 138 | Branch Amp | 2200.6248 | - | - | - | - | 102.9237 | - | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4B ( 8130) -> LAN_CTY4A ( 8127) CKT S1 | L_043090PYTHIA_POI_8-043380W_COL__POI_8C60 | 138 | 138 | Branch Amp | 2200.6248 | - | - | - | - | 109.1515 | - | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4B ( 8130) -> LAN_CTY4A ( 8127) CKT S1 | L_043570WHARTN__60B8-044150HNGFRD_POI_8C&1-MS | 138 | 138 | Branch Amp | 2200.6248 | - | - | - | - | 118.1988 | 111.7097 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4B ( 8130) -> LAN_CTY4A ( 8127) CKT S1 | L_044150HNGFRD_POI_8-044190E_BERN__B138C60 | 138 | 138 | Branch Amp | 2200.6248 | - | - | - | - | 128.931 | 127.5686 | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4B ( 8130) -> LAN_CTY4A ( 8127) CKT S1 | L_044640SEALY__S65_8-044700GEBHRT_X65B8C65 | 138 | 138 | Branch Amp | 2200.6248 | - | - | - | - | 101.7672 | - | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4B ( 8130) -> LAN_CTY4A ( 8127) CKT S1 | L_044700GEBHRT_X65B8-888872SKYSLY_POIC65 | 138 | 138 | Branch Amp | 2200.6248 | - | - | - | - | 102.3849 | - | -
TAEPTC | COAST | COAST | COAST, COAST | LAN_CTY4B ( 8130) -> LAN_CTY4A ( 8127) CKT S1 | P7-1_E1>>T6060D | 138 | 138 | Branch Amp | 2200.6248 | - | - | - | - | 121.8309 | 115.5094 | -
TAEPTN , TAEPTC | COAST | COAST | COAST, COAST | LANCTYPM4A (8104) -> LAN_CTY4A (8127) CKT 1 | Pre-contingency | 138 | 138 | Amps | 882.7601 | - | - | - | - | 118.9754 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LGE4A (160205) -> I_DUPSW4A ( 8422) CKT 1 | L_008422I_DUPSW4A-160205LGE4AC2 | 138 | 138 | Branch Amp | 1380.62 | - | - | - | 110.2197 | 115.0372 | 109.6676 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 103.342 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | 3WT_001926LIGGETT_1T5_001923LIGGETTA1_8_011926LIGGETTA1_3 C 1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 106.9015 | 112.2613 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | 3WT_001927LIGGETT_2T5_001925LIGGETTA2_8_011927LIGGETTA2_3 C 2 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 103.1043 | 110.2519 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 128.2471 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 121.9787 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | BEPC_015_2 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 101.8274 | 105.7774 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 102.1633 | 110.5311 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 1999.8073 | - | - | 115.4074 | 153.0348 | 163.6535 | 116.4804 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1999.8073 | - | - | 118.8466 | 156.1099 | 167.059 | 119.7283 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 102.1054 | 106.1321 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 101.0738 | 109.1318 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | GLASGOW_CON | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 101.1416 | 109.2813 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | GreenRD Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 101.7196 | 108.4279 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 116.003 | 124.5913 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 118.2461 | 126.9929 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 119.4926 | 128.2194 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 104.9492 | 111.1603 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 107.7766 | 114.0829 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 102.1633 | 110.5311 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 101.0738 | 109.1318 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | L_002361CRLTN_NW1_5-002387HACKBRY1_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 101.5518 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | L_002410NORWD_1T5-015204MRRFLD_RD1_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 101.184 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | L_002420CHILSW1_5-015204MRRFLD_RD1_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 106.1992 | 113.6359 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 101.7562 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 102.9238 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 101.1753 | 109.2934 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 101.7951 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 100.1486 | 108.2504 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 107.41 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 100.1071 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | NORTHWEST CARROLLTON - LEWISVILLE SW (BEPC) 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 100.574 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 106.0498 | 111.9044 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 108.6302 | 114.8148 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | - | 110.4638 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 104.5797 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 123.5914 | 132.6111 | 100.2732 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 117.3355 | 125.7408 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 122.1352 | 132.0768 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 106.9394 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 119.5597 | 128.5564 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIGGETT_3T5 ( 1928) -> NORWD1_5 ( 2406) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 1999.8073 | - | - | - | 122.4171 | 131.5001 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LILLIAN8 ( 419) -> JESSICA ( 404) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 962.2503 | - | - | 102.7008 | 115.3807 | 123.2495 | 103.7246 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LILLIAN8 ( 419) -> JESSICA ( 404) CKT 1 | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | 138 | Branch Amp | 962.2503 | - | - | - | 101.1967 | 108.7276 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LILLIAN8 ( 419) -> JESSICA ( 404) CKT 1 | L_002305AIRPRD_T8-002307MDLTHTXI1_8C1 | 138 | 138 | Branch Amp | 962.2503 | - | - | - | - | 107.1726 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LILLIAN8 ( 419) -> JESSICA ( 404) CKT 1 | L_002307MDLTHTXI1_8-012307NEWBRCH_8C1 | 138 | 138 | Branch Amp | 962.2503 | - | - | - | - | 102.5886 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LILLIAN8 ( 419) -> JESSICA ( 404) CKT 1 | L_002308MDLTH_S_8-012307NEWBRCH_8C1 | 138 | 138 | Branch Amp | 962.2503 | - | - | - | - | 101.3646 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LILLIAN8 (419) -> HIGHPOINT (439) CKT 1 | Pre-contingency | 138 | 138 | Amps | 694.4937 | - | - | - | 105.0889 | 113.5156 | 101.2897 | -
TONCOR,TCNPE,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIMEST_POI_5 (46020) -> NAVARRO (68091) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | 103.0738 | - | -
TONCOR,TCNPE,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIMEST_POI_5 (46020) -> NAVARRO (68091) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | 101.5108 | - | -
TONCOR,TCNPE,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIMEST_POI_5 (46020) -> NAVARRO (68091) CKT 1 | BIGBRN__5-JEWETT_S5 & BIGBRN__5-JEWETT_N5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | 105.7258 | - | -
TONCOR,TCNPE,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIMEST_POI_5 (46020) -> NAVARRO (68091) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | 109.7725 | - | -
TONCOR,TCNPE,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIMEST_POI_5 (46020) -> NAVARRO (68091) CKT 1 | L_003386OUTLAW_5-046020LIMEST_POI_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | 109.979 | - | -
TONCOR,TCNPE,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIMEST_POI_5 (46020) -> NAVARRO (68091) CKT 1 | L_003386OUTLAW_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | 112.9215 | - | -
TCNPE,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIMEST_POI_5 (46020) -> OUTLAW_5 ( 3386) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 105.9137 | - | -
TCNPE,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIMEST_POI_5 (46020) -> OUTLAW_5 ( 3386) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 104.3002 | - | -
TCNPE,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIMEST_POI_5 (46020) -> OUTLAW_5 ( 3386) CKT 1 | BIGBRN__5-JEWETT_S5 & BIGBRN__5-JEWETT_N5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 108.8507 | - | -
TCNPE,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIMEST_POI_5 (46020) -> OUTLAW_5 ( 3386) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 112.9501 | - | -
TCNPE,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIMEST_POI_5 (46020) -> OUTLAW_5 ( 3386) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 101.9451 | - | -
TCNPE,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIMEST_POI_5 (46020) -> OUTLAW_5 ( 3386) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 100.2656 | - | -
TCNPE,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIMEST_POI_5 (46020) -> OUTLAW_5 ( 3386) CKT 1 | L_046020LIMEST_POI_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 113.4548 | - | -
TCNPE,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LIMEST_POI_5 (46020) -> OUTLAW_5 ( 3386) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 101.1005 | - | -
TONCOR | SOUTH_CE | NORTH_CE | SOUTH_CE, NORTH_CE | LITTLEPOND_5 ( 3377) -> BELL_E_5 ( 3687) CKT 1 | L_003687BELL_E_5-003705BRANGUS_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 119.5045 | 130.2604 | -
TONCOR | SOUTH_CE | NORTH_CE | SOUTH_CE, NORTH_CE | LITTLEPOND_5 ( 3377) -> BELL_E_5 ( 3687) CKT 1 | L_003705BRANGUS_5-003706GIBSON_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 113.9624 | 121.8973 | -
TONCOR | SOUTH_CE | NORTH_CE | SOUTH_CE, NORTH_CE | LITTLEPOND_5 ( 3377) -> BELL_E_5 ( 3687) CKT 1 | L_003706GIBSON_5-039950TNTNP_ONE_3C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 101.8661 | 111.1887 | -
TONCOR | SOUTH_CE | NORTH_CE | SOUTH_CE, NORTH_CE | LITTLEPOND_5 ( 3377) -> BELL_E_5 ( 3687) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | - | 100.4617 | -
TCNPE | COAST | COAST | COAST, COAST | LKJACK_S02_8 (42880) -> HOFMAN_X02B8 (42810) CKT 02 | L_042370DAMON__S89_8-042380NEEDVL__B138C89 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 100.6086 | -
TCNPE | COAST | COAST | COAST, COAST | LKJACK_S02_8 (42880) -> HOFMAN_X02B8 (42810) CKT 02 | L_042370DAMON__S89_8-043380W_COL__POI_8C&1-MS | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 101.1268 | -
TCNPE | COAST | COAST | COAST, COAST | LKJACK_S02_8 (42880) -> HOFMAN_X02B8 (42810) CKT 02 | L_888852LIATRIS_POI-044010W_A_P__POI8AC02 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 108.1426 | -
TCNPE | COAST | COAST | COAST, COAST | LKJACK_S02_8 (42880) -> HOFMAN_X02B8 (42810) CKT 02 | P1-2_(42980-44010-02)-2 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 108.1426 | -
TCNPE | COAST | COAST | COAST, COAST | LKJACK_S02_8 (42880) -> HOFMAN_X02B8 (42810) CKT 02 | P7-1_E1>>T1827K | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 101.1476 | -
TCNPE | COAST | COAST | COAST, COAST | LKJACK_S02_8 (42880) -> HOFMAN_X02B8 (42810) CKT 02 | P7-1_E1>>T2682EX1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 104.0096 | 121.0842 | -
TCNPE | COAST | COAST | COAST, COAST | LKJACK_S02_8 (42880) -> HOFMAN_X02B8 (42810) CKT 02 | P7-1_E1>>T2682EX2 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 105.1667 | 122.2136 | -
TCNPE | COAST | COAST | COAST, COAST | LKJACK_S02_8 (42880) -> HOFMAN_X02B8 (42810) CKT 02 | P7-1_E1>>T2682GY1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 105.2837 | 122.3287 | -
TCNPE | COAST | COAST | COAST, COAST | LKJACK_S02_8 (42880) -> HOFMAN_X02B8 (42810) CKT 02 | P7-1_E1>>T2682GY2 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 105.283 | 122.328 | -
TCNPE | COAST | COAST | COAST, COAST | LKJACK_S02_8 (42880) -> HOFMAN_X02B8 (42810) CKT 02 | P7-1_E1>T2682DX | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 112.8342 | -
TCNPE | COAST | COAST | COAST, COAST | LKJACK_S02_8 (42880) -> RETREV_T02B8 (43172) CKT 02 | Pre-contingency | 138 | 138 | Amps | 1840.8268 | - | - | - | - | - | 104.9401 | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | BAS_RANCH_CON | 69 | 138 | Branch MVA | 63 | - | - | - | 100.9937 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | BOWMAN - BYRD\RILEY (AEP) 345 KV (DOUBLE B TO B) | 69 | 138 | Branch MVA | 63 | 102.2327 | - | - | 101.3672 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | CHINA GROVE SW - AEP PAINT CREEK 138 KV & GRAHAM SES - TONKAWA/COOKFIELD/LONGCREEK 345 KV (DOUBLE B TO B) 2019 SUM - FUTURE-1 | 69 | 138 | Branch MVA | 63 | - | - | - | 100.1671 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | CLY_PHNT1P7F1-1 | 69 | 138 | Branch MVA | 63 | - | - | - | 100.2943 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | CLY_PHNT1P7F1-2 | 69 | 138 | Branch MVA | 63 | - | - | - | 100.0694 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | DERMOTT - BLUFF CREEK SW & DERMOTT - ENNIS CREEK 138 KV (DOUBLE B TO B) 2023 WIN - FUTURE | 69 | 138 | Branch MVA | 63 | 106.383 | - | 103.4272 | 105.8275 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | DERMOTT - COTTONWOOD/MHOS (WETT) CKT 1 345 KV (SINGLE B TO B) C | 69 | 138 | Branch MVA | 63 | 102.6988 | - | 100.3833 | 103.2574 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | ENNIS CREEK SW - SALT CREEK SW (BRAZOS) 138 KV 2021 WIN - FUTURE (SINGLE B TO B) | 69 | 138 | Branch MVA | 63 | - | - | - | 100.1689 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | G_140081WEC_WECG1UW1 | 69 | 138 | Branch MVA | 63 | 102.8839 | - | 100.5616 | 102.6358 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | G_140181MWEC_G1UW1 | 69 | 138 | Branch MVA | 63 | - | - | - | 100.1369 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | G_141662SOLARA_UNIT1US1 | 69 | 138 | Branch MVA | 63 | 101.4389 | - | - | 101.0503 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | G_888839BAS_RANCH_POIUC1 | 69 | 138 | Branch MVA | 63 | - | - | - | 100.9975 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | GRAHAM SES - PAINT CREEK/BRECKENRIDGE 138 KV (DOUBLE B TO B) B | 69 | 138 | Branch MVA | 63 | 102.6188 | - | - | 101.8453 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | GRAHAM SW - PAINT CREEK (WTU) 138 KV (SINGLE B TO B) | 69 | 138 | Branch MVA | 63 | 102.5121 | - | - | 101.7462 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | HOLLY_CON | 69 | 138 | Branch MVA | 63 | 100.6856 | - | - | 101.5971 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | KRUM WEST - RILEY A 345 KV (DOUBLE B TO B) | 69 | 138 | Branch MVA | 63 | 101.844 | - | - | 101.4198 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | KRUMW-WEST DENT/DUNHAM 345 KV (DOUBLE B TO B) | 69 | 138 | Branch MVA | 63 | 100.0279 | - | - | 100.3769 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_000720SLTCRKRCTR-000731SLTCRKSWC1 | 69 | 138 | Branch MVA | 63 | 101.5223 | - | - | 102.1821 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_000720SLTCRKRCTR-006150SPUR4AC1 | 69 | 138 | Branch MVA | 63 | 101.5216 | - | - | 102.1818 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_000731SLTCRKSW-000752CLAIRMONTC1 | 69 | 138 | Branch MVA | 63 | 100.0414 | - | - | 100.2776 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_000752CLAIRMONT-900073Other_124C1 | 69 | 138 | Branch MVA | 63 | 100.3882 | - | - | 100.61 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_000792MURRAY-001431GRHAMSES1_8C1 | 69 | 138 | Branch MVA | 63 | 102.2973 | - | - | 101.8574 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_000792MURRAY-006169PAINTCRE4BC1 | 69 | 138 | Branch MVA | 63 | 102.51 | - | - | 101.7442 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_001314ENNISCK_8-011306DERMOTT_8C1 | 69 | 138 | Branch MVA | 63 | 104.9525 | - | 102.5929 | 104.683 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_001314ENNISCK_8-011403LLOYDCRK_8C1 | 69 | 138 | Branch MVA | 63 | 100.9474 | - | - | 101.1366 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_001318CHINAGRV_8-011330DUNN_8C1 | 69 | 138 | Branch MVA | 63 | 101.3333 | - | - | 100.2639 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006005STAMFPMP2A-006159PAINTCRE2AC1 | 69 | 138 | Branch MVA | 63 | 100.8984 | - | - | 100.3558 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006005STAMFPMP2A-006174HSKLTAP22AC1 | 69 | 138 | Branch MVA | 63 | 100.76 | - | - | 100.2148 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006030CHLD4A-006135PADU4AC1 | 69 | 138 | Branch MVA | 63 | 125.9743 | - | 123.9813 | 124.8782 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006037BOBWHITE4A-006050LKPAULS4AC1 | 69 | 138 | Branch MVA | 63 | 118.8968 | - | 114.8764 | 118.7805 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006037BOBWHITE4A-006110EASTMUND4AC1 | 69 | 138 | Branch MVA | 63 | 113.895 | - | 109.7016 | 113.1922 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006076FOXTAIL7A-006100OKLA7AC1 | 69 | 138 | Branch MVA | 63 | 101.1655 | - | - | 100.6139 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006076FOXTAIL7A-060791PERIGEE7AC1 | 69 | 138 | Branch MVA | 63 | 101.8247 | - | - | 101.3322 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006085TRUS2A-006086BENJTAP2AC1 | 69 | 138 | Branch MVA | 63 | 100.442 | - | - | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006086BENJTAP2A-006107MUNDAYST2AC1 | 69 | 138 | Branch MVA | 63 | 100.4721 | - | - | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006107MUNDAYST2A-006108EASTMUND2AC1 | 69 | 138 | Branch MVA | 63 | 104.7125 | - | 102.3219 | 104.5537 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006117EASTMUND4B-006320TARDIS4AC1 | 69 | 138 | Branch MVA | 63 | 112.7404 | - | 110.213 | 112.3574 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006135PADU4A-006320TARDIS4AC1 | 69 | 138 | Branch MVA | 63 | 117.6254 | - | 115.6998 | 116.8102 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006140MATA2A-006141ROARINGS2AC1 | 69 | 138 | Branch MVA | 63 | 101.3548 | - | - | 101.6214 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006140MATA2A-140082WEC_1_8C1 | 69 | 138 | Branch MVA | 63 | 102.53 | - | - | 102.0361 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006141ROARINGS2A-006142AFTON2AC1 | 69 | 138 | Branch MVA | 63 | 104.1559 | - | 101.4885 | 103.821 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006142AFTON2A-006143ESPU2AC1 | 69 | 138 | Branch MVA | 63 | 104.974 | - | 102.3029 | 104.631 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006143ESPU2A-006148SPUR2AC1 | 69 | 138 | Branch MVA | 63 | 105.6216 | - | 102.948 | 105.2706 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006150SPUR4A-140182MWEC_8C1 | 69 | 138 | Branch MVA | 63 | - | - | - | 100.1583 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006169PAINTCRE4B-060387HENDRICK4AC1 | 69 | 138 | Branch MVA | 63 | 101.1091 | - | - | 100.1723 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006216BLF_CRK4A-006260SOUTHABI4AC1 | 69 | 138 | Branch MVA | 63 | 101.195 | - | - | 100.4873 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006235ABMULCW7A-060791PERIGEE7AC1 | 69 | 138 | Branch MVA | 63 | 102.659 | - | - | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_006235ABMULCW7A-888860RUBICONALPHA_POIC1 | 69 | 138 | Branch MVA | 63 | - | - | - | 102.7685 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_011402ROUGHCRK_8-011403LLOYDCRK_8C1 | 69 | 138 | Branch MVA | 63 | 100.7905 | - | - | 100.9908 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_011402ROUGHCRK_8-900073Other_124C1 | 69 | 138 | Branch MVA | 63 | 100.5635 | - | - | 100.7793 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_023924FARMLAND_5-023930FIDLWD_5C1 | 69 | 138 | Branch MVA | 63 | - | - | - | 100.0237 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_023924FARMLAND_5-888856HOLLY_POIC1 | 69 | 138 | Branch MVA | 63 | - | - | - | 100.6569 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_060387HENDRICK4A-141663SOLARA_8C1 | 69 | 138 | Branch MVA | 63 | 101.7643 | - | - | 101.0356 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_060507PENDULO7A-060514CLEARCRO7BC1-2 | 69 | 138 | Branch MVA | 63 | - | - | - | 100.3946 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_888856HOLLY_POI-059900LONG_DRAWC1 | 69 | 138 | Branch MVA | 63 | 102.571 | - | 100.0812 | 103.0446 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_888860RUBICONALPHA_POI-060791PERIGEE7AC1 | 69 | 138 | Branch MVA | 63 | - | - | - | 102.2466 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L_888883QUANT_POI-060514CLEARCRO7BC1 | 69 | 138 | Branch MVA | 63 | - | - | - | 100.3946 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L2020094 | 69 | 138 | Branch MVA | 63 | 101.1804 | - | - | 101.4482 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L2020811 | 69 | 138 | Branch MVA | 63 | 117.4556 | - | 113.3968 | 117.2103 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L2020822-1 | 69 | 138 | Branch MVA | 63 | 101.5215 | - | - | 102.1819 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L2020975 | 69 | 138 | Branch MVA | 63 | 100.4819 | - | - | 100.4275 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L2021251 | 69 | 138 | Branch MVA | 63 | 100.1925 | - | - | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | L2920902 | 69 | 138 | Branch MVA | 63 | 100.4459 | - | - | 100.5842 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | LONGCREEK SW - COOK FIELD ROAD SW & LONGCREEK SW - GRAHAM SW 345 KV (DOUBLE B TO B) | 69 | 138 | Branch MVA | 63 | - | - | - | 100.1781 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | M2011320114 | 69 | 138 | Branch MVA | 63 | 100.6186 | - | - | 100.0787 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB2084520840 | 69 | 138 | Branch MVA | 63 | 101.8087 | - | - | 100.909 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB2089220893 | 69 | 138 | Branch MVA | 63 | 101.3938 | - | - | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB2089320892 | 69 | 138 | Branch MVA | 63 | - | - | - | 100.7162 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB210130210135 | 69 | 138 | Branch MVA | 63 | - | - | 100.7538 | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB210140210145-AAABA | 69 | 138 | Branch MVA | 63 | 100.4629 | - | - | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB210140210145-AABB | 69 | 138 | Branch MVA | 63 | 100.7034 | - | - | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB210140210145-ABABB | 69 | 138 | Branch MVA | 63 | 100.2454 | - | - | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB210140210145-BAAA-1 | 69 | 138 | Branch MVA | 63 | 101.2939 | - | - | 100.0822 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB210140210145-BAAA-2 | 69 | 138 | Branch MVA | 63 | 102.7024 | - | - | 101.6025 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB210140210145-BAAB-2 | 69 | 138 | Branch MVA | 63 | - | - | - | 103.5689 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB210140210145-BABB | 69 | 138 | Branch MVA | 63 | 101.8637 | - | - | 100.7388 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB210140210145-BBAA-1 | 69 | 138 | Branch MVA | 63 | 103.0749 | - | - | 102.0547 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB210140210145-BBAA-2 | 69 | 138 | Branch MVA | 63 | 104.798 | - | - | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB210140210145-BBAB-1 | 69 | 138 | Branch MVA | 63 | 101.9153 | - | - | 100.7802 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB210140210145-BBAB-2 | 69 | 138 | Branch MVA | 63 | 103.318 | - | - | 102.3018 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB210140210145-BBBA | 69 | 138 | Branch MVA | 63 | 100.0701 | - | - | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB2551220811-2 | 69 | 138 | Branch MVA | 63 | 113.8379 | - | 108.998 | 111.5683 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB2551220815-1A | 69 | 138 | Branch MVA | 63 | 100.2225 | - | - | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB2551220840-2A-1 | 69 | 138 | Branch MVA | 63 | 102.0715 | - | - | 101.4455 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB2551220840-2A-2 | 69 | 138 | Branch MVA | 63 | 102.7668 | - | - | 102.194 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB2551320811-A | 69 | 138 | Branch MVA | 63 | 114.4514 | - | - | 112.1422 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB2551320811-B | 69 | 138 | Branch MVA | 63 | - | - | 108.4879 | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB2551320815-A | 69 | 138 | Branch MVA | 63 | 100.5883 | - | - | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB2551320840-1A | 69 | 138 | Branch MVA | 63 | 101.8349 | - | - | 100.096 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | MB2552825529 | 69 | 138 | Branch MVA | 63 | - | - | - | 103.203 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | New Meinan - Sweeteast and BitterCreek 345kV Double | 69 | 138 | Branch MVA | 63 | 100.0344 | - | - | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | P7-WETT-4 | 69 | 138 | Branch MVA | 63 | 100.8321 | - | - | 101.9302 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 69 | 138 | Branch MVA | 63 | - | - | - | 100.3563 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | RILEY (AEP) - BYRD\BOWMAN 345 KV (DOUBLE B TO B) | 69 | 138 | Branch MVA | 63 | 101.8253 | - | - | 100.9017 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | RUBICONALPHA_CON | 69 | 138 | Branch MVA | 63 | - | - | - | 102.4128 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | SCUR_CLY_P7 | 69 | 138 | Branch MVA | 63 | - | - | - | 100.4875 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 1 & SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 2 345 KV (DOUBLE B TO B) | 69 | 138 | Branch MVA | 63 | - | - | - | 100.034 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | T_006028CHLD2A-006030CHLD4AC1 | 69 | 138 | Branch MVA | 63 | 125.7791 | - | 123.7785 | 124.2237 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | T_006108EASTMUND2A-006110EASTMUND4AC1 | 69 | 138 | Branch MVA | 63 | 104.7135 | - | 102.3224 | 104.5543 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | T_006148SPUR2A-006150SPUR4AC1 | 69 | 138 | Branch MVA | 63 | 107.6189 | - | 105.2208 | 107.5441 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | T_006156ASPM2A-006158ASPM4AC1 | 69 | 138 | Branch MVA | 63 | 100.0678 | - | - | 100.3597 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | T200004 | 69 | 138 | Branch MVA | 63 | 110.5258 | - | 108.0621 | 110.5641 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | T200005 | 69 | 138 | Branch MVA | 63 | 100.7222 | - | - | 100.3926 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | T200014 | 69 | 138 | Branch MVA | 63 | 130.7604 | - | 128.6848 | 129.3673 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 69 | 138 | Branch MVA | 63 | 101.73 | - | - | 102.7841 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | TULECANYON-WHITERIVER (DOUBLE B TO B) | 69 | 138 | Branch MVA | 63 | 100.0161 | - | - | - | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | WHITERIVER-COTTONWOOD (DOUBLE B TO B)-2 | 69 | 138 | Branch MVA | 63 | - | - | - | 100.1545 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | WILLOW CREEK - CLEAR CROSSING (THOMAS PRICE) & COODY CROSSING - TECUMSEH 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV SUM 2026 - FUTURE (TRIPLE B TO B) | 69 | 138 | Branch MVA | 63 | 102.3015 | - | - | 101.4513 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | WILLOW CREEK - THOMAS PRICE\TECUMSEH CREEK 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV WIN 2023 - FUTURE (TRIPLE B TO B) | 69 | 138 | Branch MVA | 63 | 102.2315 | - | - | 101.39 | - | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | LKPAULS4A ( 6050) -> PAUL2A ( 6048) CKT 1 | XFMR-RANGER_5 | 69 | 138 | Branch MVA | 63 | 100.4231 | - | - | - | - | - | -
TAEPTC,RLASMA | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LMJDSW_5 (162745) -> RIOHONDO7A ( 8318) CKT 1 | E_NEDIN_CC1_TRAIN | 345 | 345 | Branch Amp | 1999.9746 | - | - | - | 161.4719 | - | - | -
TAEPTC,RLASMA | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LMJDSW_5 (162745) -> RIOHONDO7A ( 8318) CKT 1 | E5DVA1C1_1_B | 345 | 345 | Branch Amp | 1999.9746 | - | - | - | 162.4469 | - | - | -
TAEPTC,RLASMA | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LMJDSW_5 (162745) -> RIOHONDO7A ( 8318) CKT 1 | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | 345 | Branch Amp | 1999.9746 | - | - | - | 166.8011 | 165.042 | - | -
RLASMA | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LMJDSW_W1 (162741) -> LMJDSW_5 (162745) CKT T2 | E_NEDIN_CC1_TRAIN | 345 | 34.5 | Branch MVA | 218.8 | - | - | - | 352.2721 | - | - | -
RLASMA | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LMJDSW_W1 (162741) -> LMJDSW_5 (162745) CKT T2 | E5DVA1C1_1_B | 345 | 34.5 | Branch MVA | 218.8 | - | - | - | 356.6809 | - | - | -
RLASMA | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LMJDSW_W1 (162741) -> LMJDSW_5 (162745) CKT T2 | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | 34.5 | Branch MVA | 218.8 | - | - | - | 376.6775 | 368.5323 | - | -
RLASMA | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LMJDSW_W2 (162742) -> LMJDSW_5 (162745) CKT T1 | E_NEDIN_CC1_TRAIN | 345 | 34.5 | Branch MVA | 218.8 | - | - | - | 354.7959 | - | - | -
RLASMA | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LMJDSW_W2 (162742) -> LMJDSW_5 (162745) CKT T1 | E5DVA1C1_1_B | 345 | 34.5 | Branch MVA | 218.8 | - | - | - | 359.2168 | - | - | -
RLASMA | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LMJDSW_W2 (162742) -> LMJDSW_5 (162745) CKT T1 | STILLMAN - POMPANO & CHALYBE - POMPANO | 345 | 34.5 | Branch MVA | 218.8 | - | - | - | 379.2688 | 371.1012 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_1_5 (150315) -> LNCRK2_2_8 (150314) CKT 1 | Pre-contingency | 345 | 138 | MVA | 235 | - | - | - | - | 107.4449 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_1_8 (150313) -> LNCRK2_G871 (150311) CKT 3 | G_150311LNCRK2_G871UW1 | 138 | 34.5 | Branch MVA | 151.3 | 108.4237 | - | 108.3037 | 108.6841 | 109.5789 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_1_8 (150313) -> LNCRK2_G871 (150311) CKT 3 | Pre-contingency | 138 | 34.5 | MVA | 121 | 104.8408 | - | 103.2921 | 108.3422 | 120.5582 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_1_8 (150313) -> LNCRK2_G872 (150312) CKT 2 | G_150312LNCRK2_G872UW2 | 138 | 34.5 | Branch MVA | 151.3 | 108.5061 | - | 108.3908 | 108.7578 | 109.6211 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_1_8 (150313) -> LNCRK2_G872 (150312) CKT 2 | Pre-contingency | 138 | 34.5 | MVA | 121 | 104.3487 | - | 102.7832 | 107.909 | 120.3114 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G871 (150311) -> LNCRK2_1_8 (150313) CKT 3 | BAS_RANCH_CON | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 104.2498 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G871 (150311) -> LNCRK2_1_8 (150313) CKT 3 | G_888839BAS_RANCH_POIUC1 | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 104.2625 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G871 (150311) -> LNCRK2_1_8 (150313) CKT 3 | HOLLY_CON | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 100.798 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G871 (150311) -> LNCRK2_1_8 (150313) CKT 3 | L_001435LONGCREK_5-001442COKFIELD_5C1 | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 100.7385 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G871 (150311) -> LNCRK2_1_8 (150313) CKT 3 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 100.9314 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G871 (150311) -> LNCRK2_1_8 (150313) CKT 3 | L_006235ABMULCW7A-060040BLF_CRK7AC1 | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 103.0299 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G871 (150311) -> LNCRK2_1_8 (150313) CKT 3 | L_006235ABMULCW7A-888860RUBICONALPHA_POIC1 | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 105.6619 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G871 (150311) -> LNCRK2_1_8 (150313) CKT 3 | L_888856HOLLY_POI-059900LONG_DRAWC1 | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 100.8645 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G871 (150311) -> LNCRK2_1_8 (150313) CKT 3 | L_888860RUBICONALPHA_POI-060791PERIGEE7AC1 | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 100.1675 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G871 (150311) -> LNCRK2_1_8 (150313) CKT 3 | LCRA TSC_T21457 | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 100.1565 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G871 (150311) -> LNCRK2_1_8 (150313) CKT 3 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 103.9695 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G871 (150311) -> LNCRK2_1_8 (150313) CKT 3 | RUBICONALPHA_CON | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 105.5949 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G871 (150311) -> LNCRK2_1_8 (150313) CKT 3 | SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 1 & SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 100.6855 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G871 (150311) -> LNCRK2_1_8 (150313) CKT 3 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 108.1057 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G872 (150312) -> LNCRK2_1_8 (150313) CKT 2 | BAS_RANCH_CON | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 104.1737 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G872 (150312) -> LNCRK2_1_8 (150313) CKT 2 | G_888839BAS_RANCH_POIUC1 | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 104.1866 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G872 (150312) -> LNCRK2_1_8 (150313) CKT 2 | HOLLY_CON | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 100.6683 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G872 (150312) -> LNCRK2_1_8 (150313) CKT 2 | L_001435LONGCREK_5-001442COKFIELD_5C1 | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 100.608 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G872 (150312) -> LNCRK2_1_8 (150313) CKT 2 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 100.8038 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G872 (150312) -> LNCRK2_1_8 (150313) CKT 2 | L_006235ABMULCW7A-060040BLF_CRK7AC1 | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 102.9349 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G872 (150312) -> LNCRK2_1_8 (150313) CKT 2 | L_006235ABMULCW7A-888860RUBICONALPHA_POIC1 | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 105.6079 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G872 (150312) -> LNCRK2_1_8 (150313) CKT 2 | L_888856HOLLY_POI-059900LONG_DRAWC1 | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 100.7359 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G872 (150312) -> LNCRK2_1_8 (150313) CKT 2 | L_888860RUBICONALPHA_POI-060791PERIGEE7AC1 | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 100.0281 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G872 (150312) -> LNCRK2_1_8 (150313) CKT 2 | LCRA TSC_T21457 | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 100.0169 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G872 (150312) -> LNCRK2_1_8 (150313) CKT 2 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 103.8891 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G872 (150312) -> LNCRK2_1_8 (150313) CKT 2 | RUBICONALPHA_CON | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 105.5398 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G872 (150312) -> LNCRK2_1_8 (150313) CKT 2 | SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 1 & SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 100.5541 | - | -
RPSTOK | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LNCRK2_G872 (150312) -> LNCRK2_1_8 (150313) CKT 2 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 34.5 | Branch MVA | 151.3 | - | - | - | - | 108.0898 | - | -
TRAYBN | NORTH_CE | EAST | NORTH_CE, EAST | LNOK_RC ( 6871) -> KIOWA_RC ( 6823) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 978.9851 | - | - | - | - | 101.4419 | - | -
TRAYBN | NORTH_CE | EAST | NORTH_CE, EAST | LNOK_RC ( 6871) -> KIOWA_RC ( 6823) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 978.9851 | - | - | - | - | 102.6674 | - | -
TRAYBN | NORTH_CE | EAST | NORTH_CE, EAST | LNOK_RC ( 6871) -> KIOWA_RC ( 6823) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 978.9851 | - | - | - | - | 103.1981 | - | -
TRAYBN | NORTH_CE | EAST | NORTH_CE, EAST | LNOK_RC ( 6871) -> KIOWA_RC ( 6823) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 978.9851 | - | - | - | - | 104.393 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A ( 8125) -> VICTORIA4A ( 8172) CKT 1 | E5DVA1C1_1_B | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 112.8241 | - | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A ( 8125) -> VICTORIA4A ( 8172) CKT 1 | E5DVA1C1_1_B_1 | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 104.9026 | - | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A ( 8125) -> VICTORIA4A ( 8172) CKT 1 | E5DVA1C1_1_B_2 | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 100.2173 | - | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A ( 8125) -> VICTORIA4A ( 8172) CKT 1 | L_008126FORMOSA4A-008140JOSLIN4AC1 | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 122.3466 | - | 125.6406 | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A ( 8125) -> VICTORIA4A ( 8172) CKT 1 | L_008140JOSLIN4A-008685COBIA4AC1 | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 113.3966 | - | 112.9159 | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A ( 8125) -> VICTORIA4A ( 8172) CKT 1 | L_008143V_DUPSW4A-080064CHOCBAYU4AC1 | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 100.3866 | - | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A ( 8125) -> VICTORIA4A ( 8172) CKT 1 | L_008155SANDCRAB4A-008685COBIA4AC1 | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 112.0989 | - | 111.6383 | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A ( 8125) -> VICTORIA4A ( 8172) CKT 1 | L_008155SANDCRAB4A-008723CANGREJO4AC1 | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 114.6631 | - | 114.1431 | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A ( 8125) -> VICTORIA4A ( 8172) CKT 1 | L_008715RADIANT7A-008728COBRA7AC1 | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 108.1796 | - | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A ( 8125) -> VICTORIA4A ( 8172) CKT 1 | L_008728COBRA7A-081003HABER7AC1 | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 111.567 | - | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A ( 8125) -> VICTORIA4A ( 8172) CKT 1 | M100101100271-1A | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 102.73 | - | 103.1923 | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A ( 8125) -> VICTORIA4A ( 8172) CKT 1 | M100101100271-1B | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 100.9389 | - | 101.4117 | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A ( 8125) -> VICTORIA4A ( 8172) CKT 1 | M128607128702-1_MODIFIED_BY_MZ | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 115.0056 | - | 114.1872 | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A ( 8125) -> VICTORIA4A ( 8172) CKT 1 | MB1001010027-1 | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 102.1015 | - | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A ( 8125) -> VICTORIA4A ( 8172) CKT 1 | MB1002710010-1 | 138 | 138 | Branch Amp | 719.5959 | - | - | - | - | - | 102.5875 | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A ( 8125) -> VICTORIA4A ( 8172) CKT 1 | MB1287012860-2_MODIFIED_BY_MZ | 138 | 138 | Branch Amp | 719.5959 | - | - | - | 115.9747 | - | 115.0745 | -
TAEPTC , TAEPTN | COAST | COAST | COAST, COAST | LOLITA4A (8125) -> VICTORIA4A (8172) CKT 1 | Pre-contingency | 138 | 138 | Amps | 648.473 | - | - | - | - | 126.0441 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LONGSHRE_8 (10035) -> Other_131 (900100) CKT 1 | L_010080REDBERRY_8-023833BULLDOG_8C1 | 138 | 138 | Branch Amp | 2568.79 | - | - | - | - | 100.6774 | 100.5265 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LONGSHRE_8 (10035) -> Other_131 (900100) CKT 1 | L_010080REDBERRY_8-900043Other_132C1 | 138 | 138 | Branch Amp | 2568.79 | - | - | - | - | 100.8287 | 100.6766 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LONHILL7A ( 8455) -> BLU LACY (84550) CKT 1 | L_008455LONHILL7A-084550BLU LACYC2 | 345 | 345 | Branch Amp | 4024.7166 | - | - | - | - | 122.5535 | 140.0612 | -
TAEPTC,TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LONHILL7A ( 8455) -> BLU LACY (84550) CKT 2 | L_008455LONHILL7A-084550BLU LACYC1 | 345 | 345 | Branch Amp | 4019.6963 | - | - | - | - | 122.147 | 139.4932 | -
TAEPTC,TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LONHILL7A ( 8455) -> BLU LACY (84550) CKT 2 | MBLH-BLnew | 345 | 345 | Branch Amp | 4019.6963 | - | - | - | - | 121.405 | 139.2766 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LONHILL7A (8455) -> BLU LACY (84550) CKT 1 | Pre-contingency | 345 | 345 | Amps | 3343.6107 | - | - | - | - | - | 106.7011 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | LONHILL7A (8455) -> KATOEN7A (8579) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1768.8671 | - | - | - | - | 105.5353 | - | -
TONCOR | WEST | WEST | WEST, WEST | LORAINES_8 (11342) -> RANGER_8 (10050) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 778.1677 | - | 159.1012 | - | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | 3WT_011010WOLFSS_5_001013WOLFSS_8_011007WOLFSS2_3 C 2 | 138 | 20 | Branch MVA | 100 | - | - | 101.0925 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | 3WT_011010WOLFSS_5_001013WOLFSS_8_011008WOLFSS_3 C 1 | 138 | 20 | Branch MVA | 100 | - | - | 101.0949 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | 3WT_038044TNCOWPEN__3_038043TNCOWPEN__1_038042TNCOWPEN2_4 C 2 | 138 | 20 | Branch MVA | 100 | - | - | 101.3915 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | 3WT_038044TNCOWPEN__3_038043TNCOWPEN__1_038048TNCOWPEN1_4 C 1 | 138 | 20 | Branch MVA | 100 | - | - | 101.3915 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | 3WT_076000L_NORTMC5_1Y_076595L_NORTMC8_2Y_076998L_NORTMC2_2Y C 2 | 138 | 20 | Branch MVA | 100 | - | - | 105.4843 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | 3WT_076000L_NORTMC5_1Y_076595L_NORTMC8_2Y_076999L_NORTMC2_1Y C 1 | 138 | 20 | Branch MVA | 100 | - | - | 105.4843 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_038340TNAIRPORT41UB1 | 138 | 20 | Branch MVA | 100 | - | - | 111.4144 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_038465TNSTONERD_1UB1 | 138 | 20 | Branch MVA | 100 | - | - | 111.6009 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_076026L_SODALA8_1YUB1 | 138 | 20 | Branch MVA | 100 | - | - | 100.4982 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_130011PB2SES_CT1UN1 | 138 | 20 | Branch MVA | 100 | - | - | 103.4368 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_130012PB2SES_CT2UN2 | 138 | 20 | Branch MVA | 100 | - | - | 103.4191 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_130013PB2SES_CT3UN3 | 138 | 20 | Branch MVA | 100 | - | - | 103.4211 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_130014PB2SES_CT4UN4 | 138 | 20 | Branch MVA | 100 | - | - | 103.4143 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_130015PB2SES_CT5UN5 | 138 | 20 | Branch MVA | 100 | - | - | 103.4076 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_130431WOO_WOODWRD1UW1 | 138 | 20 | Branch MVA | 100 | - | - | 103.1041 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_130531WOO_WOODWRD2UW1 | 138 | 20 | Branch MVA | 100 | - | - | 102.7136 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_131455KEO_SHRBINO2UW1 | 138 | 20 | Branch MVA | 100 | - | - | 101.9708 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_132332REROCK_UNIT1US1 | 138 | 20 | Branch MVA | 100 | - | - | 106.363 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_132333REROCK_UNIT2US2 | 138 | 20 | Branch MVA | 100 | - | - | 106.363 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_132431SIRIUS_S1US1 | 138 | 20 | Branch MVA | 100 | - | - | 101.4575 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_132436SIRIUS_S2US2 | 138 | 20 | Branch MVA | 100 | - | - | 100.3769 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_132481RIGGINS_S1US1 | 138 | 20 | Branch MVA | 100 | - | - | 111.2356 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_132781CASLGP_UNIT1US1 | 138 | 20 | Branch MVA | 100 | - | - | 100.9347 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_132941SPTX12B_S1US1 | 138 | 20 | Branch MVA | 100 | - | - | 100.6995 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_134241TAYGETE_S1US1 | 138 | 20 | Branch MVA | 100 | - | - | 111.415 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_134243TAYGETE_S2US2 | 138 | 20 | Branch MVA | 100 | - | - | 111.3983 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_134701TYGTEII_S1US1 | 138 | 20 | Branch MVA | 100 | - | - | 111.6491 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_134702TYGTEII_S2US2 | 138 | 20 | Branch MVA | 100 | - | - | 111.6403 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_134751FOWLR_S1US1 | 138 | 20 | Branch MVA | 100 | - | - | 101.5229 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_135461SWOOSEII_G1UB1 | 138 | 20 | Branch MVA | 100 | - | - | 101.1008 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_135491FLOWERII_G1UB1 | 138 | 20 | Branch MVA | 100 | - | - | 107.924 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_135591BRP_PAVO_BTUBT | 138 | 20 | Branch MVA | 100 | - | - | 111.9614 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_135731APPALOSA_W1UW1 | 138 | 20 | Branch MVA | 100 | - | - | 100.2741 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_136101BLUESKY_S1US1 | 138 | 20 | Branch MVA | 100 | - | - | 100.3138 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_136151RODEORNCH_B1UB1 | 138 | 20 | Branch MVA | 100 | - | - | 100.677 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_136152RODEORNCH_B2UB2 | 138 | 20 | Branch MVA | 100 | - | - | 100.6752 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_136211TBWF_ESS_B1UB1 | 138 | 20 | Branch MVA | 100 | - | - | 100.7221 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_136221GALLSTO1_B1UB1 | 138 | 20 | Branch MVA | 100 | - | - | 111.551 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_136391DOGFISH_B1UB1 | 138 | 20 | Branch MVA | 100 | - | - | 111.939 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_170200ACA_UNIT1US1 | 138 | 20 | Branch MVA | 100 | - | - | 100.0336 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_181651HOVEY_UNIT1US1 | 138 | 20 | Branch MVA | 100 | - | - | 101.3904 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_181651HOVEY_UNIT1US2 | 138 | 20 | Branch MVA | 100 | - | - | 100.0978 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | G_182151EGROVESL_S1US1 | 138 | 20 | Branch MVA | 100 | - | - | 102.2291 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_000842GPL_KINGMTSW-000843GPL_KINGMTTPC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.6349 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_000842GPL_KINGMTSW-076000L_NORTMC5_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 102.4485 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.7519 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_000844GPL_NEVILLSW-076000L_NORTMC5_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 104.8744 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_000844GPL_NEVILLSW-076002L_BAKERS5_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 105.8127 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001001AROYA_8-001009YUCCADR_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 108.8449 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001009YUCCADR_8-011128SHINOAK_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.4126 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001009YUCCADR_8-011204THORNTVLE_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 111.9604 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001009YUCCADR_8-011245RIVERVIEW_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 110.1536 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001013WOLFSS_8-011292PENWELL_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.7619 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001027ODESEHV_8-001052REXALL_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.4792 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001027ODESEHV_8-071230L_PLEAFA8_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 101.4537 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001052REXALL_8-001053GENRUBR_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 104.9437 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001053GENRUBR_8-011281OLEFIN_T8C1 | 138 | 20 | Branch MVA | 100 | - | - | 104.9412 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001074WINKSS_8-001253MIDWAY_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.8103 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001074WINKSS_8-001286ONC900076_TAPC1 | 138 | 20 | Branch MVA | 100 | - | - | 101.3992 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001074WINKSS_8-011135RAILSIDE_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 101.2705 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001074WINKSS_8-900125BLKPEARL_P8C1 | 138 | 20 | Branch MVA | 100 | - | - | 109.8196 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001092LOVING_8-018680BLUEMTN_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.1171 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001147CHEYENTA_8-011147KERMITEAST_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 101.2332 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001149DOLRHIDE_8-001150AMOCO3BA_T8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.1584 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001150AMOCO3BA_T8-001157ANDRCOSO_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.1487 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001202WARDSS_8-001238ROYALTY_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 111.8907 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001202WARDSS_8-011204THORNTVLE_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 111.8895 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001238ROYALTY_8-001239COYANOSA_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 111.8854 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001239COYANOSA_8-011238BLAIRLAKE_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 111.9535 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001250YUKONSS_8-001253MIDWAY_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.6708 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001286ONC900076_TAP-131853NOTSW_1_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 101.2701 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_001299ONC900002_TAP-001092LOVING_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.3973 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006517RUSSEKST4A-006535BIGLAKE4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.0333 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006559JERRY4A-060374PUMPJACK4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.2208 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006562FDRAN4A-060412CARVER4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.0042 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006562FDRAN4A-136103BLUESKY_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.3278 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006564ILLN4A-060389CORRAL4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.1818 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006564ILLN4A-076579L_FORTLA8_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.0063 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006584INDN4A-076019L_FOURMI8_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.4172 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006584INDN4A-076580L_TUNACR8_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.4172 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006601RIOPECOS4A-038445TNGIRVIN__1C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.5191 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006601RIOPECOS4A-038445TNGIRVIN__1C2 | 138 | 20 | Branch MVA | 100 | - | - | 100.4023 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006601RIOPECOS4A-060400LYNX4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 104.7946 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006601RIOPECOS4A-060720SUNV4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 110.8998 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006601RIOPECOS4A-076026L_SODALA8_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 106.223 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006601RIOPECOS4A-076580L_TUNACR8_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 108.3413 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006601RIOPECOS4A-076595L_NORTMC8_2YC1 | 138 | 20 | Branch MVA | 100 | - | - | 108.0934 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006601RIOPECOS4A-076600L_OXTASW8_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 107.9321 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006601RIOPECOS4A-076601L_HORSCR8_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 102.2393 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006601RIOPECOS4A-076615L_LCRANE8_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 101.2686 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006630FTST4A-006671TOMBSTNE4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 111.7454 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006630FTST4A-038355TNLEONCRK_1C1 | 138 | 20 | Branch MVA | 100 | - | - | 110.7204 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006630FTST4A-132482RIGGINS_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 110.8735 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006648HARGROVE4A-060374PUMPJACK4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.428 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006648HARGROVE4A-076011L_TWINBU8_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.5212 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006663COCS2A-038490TNBELDING_0C1 | 138 | 20 | Branch MVA | 100 | - | - | 105.4519 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006665ALPR2A-006666ALPINE2AC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.5778 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006665ALPR2A-909999NSC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.2047 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006666ALPINE2A-006674BRONCO2AC1 | 138 | 20 | Branch MVA | 100 | - | - | 102.8801 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006671TOMBSTNE4A-060400LYNX4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 111.743 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006674BRONCO2A-038490TNBELDING_0C1 | 138 | 20 | Branch MVA | 100 | - | - | 105.4112 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_006675GONZALES2A-060339ACACIA2AC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.0429 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_008255HAMILTON4A-008680ROUGHCAN4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.1973 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_008680ROUGHCAN4A-008683COMSTOCK4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.1685 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_008683COMSTOCK4A-060389CORRAL4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.1737 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011010WOLFSS_5-011188QUARRYFLD_5C1 | 138 | 20 | Branch MVA | 100 | - | - | 102.5641 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011010WOLFSS_5-011188QUARRYFLD_5C2 | 138 | 20 | Branch MVA | 100 | - | - | 102.5641 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011073RUDD_8-011113BOULDER_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 101.6189 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011074ORBISONT_8-011382ASHBY_P8C2 | 138 | 20 | Branch MVA | 100 | - | - | 100.2025 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011084RIVERTON_5-011188QUARRYFLD_5C2 | 138 | 20 | Branch MVA | 100 | - | - | 100.7142 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011084RIVERTON_5-011188QUARRYFLD_5C3 | 138 | 20 | Branch MVA | 100 | - | - | 100.7142 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011097SANDLAKE_8-011104BARKETT_P8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.5145 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011113BOULDER_8-018680BLUEMTN_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 101.5132 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011128SHINOAK_8-018663OXYDAC_P8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.2628 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011135RAILSIDE_8-011147KERMITEAST_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 101.2588 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011157GARDNDALE_5-023873TELPHRD_5C1 | 138 | 20 | Branch MVA | 100 | - | - | 103.9215 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011157GARDNDALE_5-023876CLEARFRK_5C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.3425 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011238BLAIRLAKE_8-011262WOLFCAMP2_T8C1 | 138 | 20 | Branch MVA | 100 | - | - | 111.9697 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011242CRTNYCRK_8-011262WOLFCAMP2_T8C1 | 138 | 20 | Branch MVA | 100 | - | - | 111.3831 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011245RIVERVIEW_8-900064Other_134C1 | 138 | 20 | Branch MVA | 100 | - | - | 110.3856 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011292PENWELL_8-011293REDLAKES_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.7676 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_011382ASHBY_P8-018680BLUEMTN_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.2094 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_037920TNWINK____0-037940TNCALIFRNA0C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.0345 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_037940TNCALIFRNA0-037960TNWNKLRCO60C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.0566 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038001TNPYOTE___1-135464SWOOSEII_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 101.1024 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038010TNREWARDT_1-038021TNWORSHAM_1C1 | 138 | 20 | Branch MVA | 100 | - | - | 101.1905 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038043TNCOWPEN__1-038055TNSALTDRWT1C1 | 138 | 20 | Branch MVA | 100 | - | - | 111.9164 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038055TNSALTDRWT1-038058TNSADDLEBK1C1 | 138 | 20 | Branch MVA | 100 | - | - | 107.9401 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038058TNSADDLEBK1-038065TNBRDRFLD_1C1 | 138 | 20 | Branch MVA | 100 | - | - | 105.3719 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038065TNBRDRFLD_1-038069TNFLATTOP_1C1 | 138 | 20 | Branch MVA | 100 | - | - | 111.271 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038069TNFLATTOP_1-038294TNFOXTAIL_1C1 | 138 | 20 | Branch MVA | 100 | - | - | 111.1751 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038069TNFLATTOP_1-135494FLOWERII_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 111.8781 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038143TNSLVRLEAF1-038165TNBNSPRNGT1C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.5985 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038331TNALAMOST_1-038340TNAIRPORT41C1 | 138 | 20 | Branch MVA | 100 | - | - | 104.6431 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038331TNALAMOST_1-038465TNSTONERD_1C1 | 138 | 20 | Branch MVA | 100 | - | - | 111.734 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038340TNAIRPORT41-038355TNLEONCRK_1C1 | 138 | 20 | Branch MVA | 100 | - | - | 108.5791 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038376TNTRANPECT1-038377TNTRANPEC_1C1 | 138 | 20 | Branch MVA | 100 | - | - | 111.1049 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038376TNTRANPECT1-060377CREOSOTE4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 101.8934 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038380TNCOYANOSA1-060377CREOSOTE4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.3754 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038430TNWHITEBKR1-038445TNGIRVIN__1C1 | 138 | 20 | Branch MVA | 100 | - | - | 110.0349 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038430TNWHITEBKR1-135592BRP_PAVO_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 111.9614 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038445TNGIRVIN__1-038450TNSOAPTREE1C1 | 138 | 20 | Branch MVA | 100 | - | - | 102.7352 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038450TNSOAPTREE1-038455TNHOLIDAY_1C1 | 138 | 20 | Branch MVA | 100 | - | - | 111.5754 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_038450TNSOAPTREE1-038455TNHOLIDAY_1C2 | 138 | 20 | Branch MVA | 100 | - | - | 111.5757 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_059902SAND_BLUFF-059907BERNOULLIC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.235 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_059903BEARKAT-059907BERNOULLIC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.407 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_059903BEARKAT-076000L_NORTMC5_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.1675 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_059903BEARKAT-076000L_NORTMC5_1YC2 | 138 | 20 | Branch MVA | 100 | - | - | 100.1675 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060014SPUD4A-076025L_CASTMO8_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.9896 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060014SPUD4A-076026L_SODALA8_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.9933 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060017HODLRAN27A-060515CLEARCRO7AC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.0117 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060207VERH4A-060808HOEFSROA4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 102.6714 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060383LINTERNA4A-060385SOLSTICE4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 111.9734 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060383LINTERNA4A-132331REROCK_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 111.9208 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060385SOLSTICE4A-060716SGSA4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 106.6723 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060385SOLSTICE4A-060808HOEFSROA4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 111.9705 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060385SOLSTICE4A-181652HOVEY_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 103.1107 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060392LOTEBUSH4A-060415BASIN4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 110.545 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060393PIGCREEK4A-134245TAYGETE_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 110.2516 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060393PIGCREEK4A-134705TYGTEII_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 110.8741 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060397GASPADTA4A-060415BASIN4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 110.4591 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060397GASPADTA4A-900064Other_134C1 | 138 | 20 | Branch MVA | 100 | - | - | 110.5412 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060400LYNX4A-130432WOODWRD1_1_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 103.1871 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060400LYNX4A-130533WOODWRD2_2C1 | 138 | 20 | Branch MVA | 100 | - | - | 102.8568 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060716SGSA4A-060721CRYO4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 102.5901 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060718PECV4A-060720SUNV4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 110.9071 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060718PECV4A-060792ATHEY4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 110.8741 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060728PALOUSE4A-135734APPALOSA_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.4926 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_060792ATHEY4A-060798ELLENBUR4AC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.0567 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_071199L_ARCO__8_1Y-900048Other_56C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.1378 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_071230L_PLEAFA8_1Y-900048Other_56C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.2615 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_076022L_DESEME8_1Y-076582L_MEVISW8_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.4587 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_076026L_SODALA8_1Y-135485CROSBAT_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.3472 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_076040L_CASTIL8_1Y-076615L_LCRANE8_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.3919 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_076040L_CASTIL8_1Y-132783CASL_GAP_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.9564 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_076040L_CASTIL8_1Y-132943SPTX12B_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.745 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_076579L_FORTLA8_1Y-076582L_MEVISW8_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 100.46 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_076595L_NORTMC8_2Y-076600L_OXTASW8_1YC1 | 138 | 20 | Branch MVA | 100 | - | - | 107.9474 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_076601L_HORSCR8_1Y-182154EGROVESL_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 102.2302 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_076635L_KINGMO8_1Y-136213TBWF_ESS_8C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.7223 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L_131453KEO_2_8-131454KEO_3_8CS2 | 138 | 20 | Branch MVA | 100 | - | - | 108.3775 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L10010095 | 138 | 20 | Branch MVA | 100 | - | - | 100.1736 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L2020711-A | 138 | 20 | Branch MVA | 100 | - | - | 111.6984 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L2020925 | 138 | 20 | Branch MVA | 100 | - | - | 100.0339 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L2020971-B2 | 138 | 20 | Branch MVA | 100 | - | - | 110.8735 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | L2920900-B | 138 | 20 | Branch MVA | 100 | - | - | 111.9427 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-1 | 138 | 20 | Branch MVA | 100 | - | - | 102.2732 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-2 | 138 | 20 | Branch MVA | 100 | - | - | 101.9501 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-1 | 138 | 20 | Branch MVA | 100 | - | - | 102.2694 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-2 | 138 | 20 | Branch MVA | 100 | - | - | 101.9469 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | LCRA TSC_NOELK_SNGTR_NOELK_SNGTR2 | 138 | 20 | Branch MVA | 100 | - | - | 101.8298 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | LCRA TSC_SCHNDR_BIGHIL_DC | 138 | 20 | Branch MVA | 100 | - | - | 101.1635 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | LCRA TSC_SNGTR_SCHDR_SNGTR_SCHDR2 | 138 | 20 | Branch MVA | 100 | - | - | 101.4638 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | LCRA TSC_T429_T9426 | 138 | 20 | Branch MVA | 100 | - | - | 100.5273 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | LCRA TSC_T451_T682 | 138 | 20 | Branch MVA | 100 | - | - | 111.8871 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | LCRA TSC_T464_1 | 138 | 20 | Branch MVA | 100 | - | - | 100.0268 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | LCRA TSC_T484 | 138 | 20 | Branch MVA | 100 | - | - | 107.9277 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | LCRA TSC_T620_1 | 138 | 20 | Branch MVA | 100 | - | - | 100.4183 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | LCRA TSC_T633_T664 | 138 | 20 | Branch MVA | 100 | - | - | 100.8946 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | LCRA TSC_T719 | 138 | 20 | Branch MVA | 100 | - | - | 100.9938 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | MB2074220667 | 138 | 20 | Branch MVA | 100 | - | - | 100.4227 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | MB2095020951 | 138 | 20 | Branch MVA | 100 | - | - | 111.3106 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | MB210130210135 | 138 | 20 | Branch MVA | 100 | - | - | 100.2356 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | MB2302023025 | 138 | 20 | Branch MVA | 100 | - | - | 106.7918 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | MB2726627277 | 138 | 20 | Branch MVA | 100 | - | - | 100.2644 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | MIDLAND COUNTY NW - MIDLAND EAST - MCKENZIE DR 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | 20 | Branch MVA | 100 | - | - | 100.089 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | MIDLAND EAST - MIDLAND COUNTY NW/MCKENZIE DR 138 KV 2024 SUM - FUTURE (DOUBLE B TO B) | 138 | 20 | Branch MVA | 100 | - | - | 100.0538 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | MOSS - HOLT 138 KV/MIDLAND COUNTY NW SW 345 KV (DOUBLE B TO B) | 138 | 20 | Branch MVA | 100 | - | - | 100.1773 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | MOSS - HOLT/YUCCA 138 KV/MIDLAND COUNTY NW SW 345 KV (DOUBLE B TO B) SUM 2025- FUTURE | 138 | 20 | Branch MVA | 100 | - | - | 100.5024 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | New Girvin - Whitebk Ckt 2 | 138 | 20 | Branch MVA | 100 | - | - | 110.0349 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | New Shunt 9424 | 138 | 20 | Branch MVA | 100 | - | - | 107.4096 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | ODESSA EHV - NORTH MCCAMEY 345 KV (SINGLE B TO B) | 138 | 20 | Branch MVA | 100 | - | - | 101.6232 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | P1.2_M138I-1_2026-FUTURE | 138 | 20 | Branch MVA | 100 | - | - | 108.1596 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | P7.1_T-SPT-LYNX | 138 | 20 | Branch MVA | 100 | - | - | 103.8666 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | P7-WETT-7 | 138 | 20 | Branch MVA | 100 | - | - | 101.4964 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | PLEASANT FARMS (LCRA) - ARCO (LCRA) 138 KV 2018 SUM - FUTURE (SINGLE B TO B) B | 138 | 20 | Branch MVA | 100 | - | - | 100.1439 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | Pre-contingency | 138 | 20 | MVA | 100 | - | 110.5639 | - | 110.2628 | 109.6107 | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | QUARRY FIELD - BLUE MOUNTAIN CKT 1 138 KV SUM 2025 - FUTURE (SINGLE B TO B) | 138 | 20 | Branch MVA | 100 | - | - | 101.4141 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | QUARRY FIELD - BLUE MOUNTAIN DBL CKT 138 KV SUM 2025 - FUTURE (DOUBLE B TO B)_MODIFIED_BY_MZ | 138 | 20 | Branch MVA | 100 | - | - | 101.8409 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | QUARRY FIELD - RIVERTON 345 KV 2021 SUM - FUTURE (DOUBLE B TO B) | 138 | 20 | Branch MVA | 100 | - | - | 104.1493 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_001009YUCCADR_81 | 138 | 20 | Branch MVA | 100 | - | - | 107.2592 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_038035TNCOLICAP_1C1 | 138 | 20 | Branch MVA | 100 | - | - | 100.1287 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_038035TNCOLICAP_1C2 | 138 | 20 | Branch MVA | 100 | - | - | 100.1287 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_038035TNCOLICAP_1C3 | 138 | 20 | Branch MVA | 100 | - | - | 100.1287 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_038035TNCOLICAP_1C4 | 138 | 20 | Branch MVA | 100 | - | - | 100.1287 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_038035TNCOLICAP_1C5 | 138 | 20 | Branch MVA | 100 | - | - | 100.1287 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_038035TNCOLICAP_1C6 | 138 | 20 | Branch MVA | 100 | - | - | 100.1287 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_038065TNBRDRFLD_11 | 138 | 20 | Branch MVA | 100 | - | - | 104.2229 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_038340TNAIRPORT411 | 138 | 20 | Branch MVA | 100 | - | - | 110.3593 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_038377TNTRANPEC_11 | 138 | 20 | Branch MVA | 100 | - | - | 110.8735 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_038380TNCOYANOSA11 | 138 | 20 | Branch MVA | 100 | - | - | 110.8735 | - | - | 109.065 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_038410TNCAYMUSVQ11 | 138 | 20 | Branch MVA | 100 | - | - | 110.8735 | - | - | 109.7595 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_038430TNWHITEBKR11 | 138 | 20 | Branch MVA | 100 | - | - | 107.1971 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_060385SOLSTICE4A1 | 138 | 20 | Branch MVA | 100 | - | - | 102.0694 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_060392LOTEBUSH4A1 | 138 | 20 | Branch MVA | 100 | - | - | 110.875 | - | - | 103.4568 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_060721CRYO4A1 | 138 | 20 | Branch MVA | 100 | - | - | 104.7382 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | S_076595L_NORTMC8_2Y1 | 138 | 20 | Branch MVA | 100 | - | - | 100.9909 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | SAND LAKE - SOLSTICE 345 KV DCKT LINE (DOUBLE B TO B) WIN 2027 - FUTURE | 138 | 20 | Branch MVA | 100 | - | - | 110.4038 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | SS20041 | 138 | 20 | Branch MVA | 100 | - | - | 103.5542 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | STECL_10592 | 138 | 20 | Branch MVA | 100 | - | - | 103.2029 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | STECL_4720 | 138 | 20 | Branch MVA | 100 | - | - | 101.8444 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | STECL_4721-1 | 138 | 20 | Branch MVA | 100 | - | - | 102.2732 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | STECL_4721-2 | 138 | 20 | Branch MVA | 100 | - | - | 101.9501 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | T_006601RIOPECOS4A-006598RIOP2AC1 | 138 | 20 | Branch MVA | 100 | - | - | 101.1912 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | T_006601RIOPECOS4A-006598RIOP2AC2 | 138 | 20 | Branch MVA | 100 | - | - | 101.3803 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | TESORO - MIDESSA SOUTH/CONSAVVY 345 KV WIN 2024 - FUTURE (DOUBLE B TO B) | 138 | 20 | Branch MVA | 100 | - | - | 100.1405 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | WINK - ANDREWS COUNTY SOUTH 138 KV CKT 1 SUM 2027 - FUTURE (SINGLE B TO B) | 138 | 20 | Branch MVA | 100 | - | - | 101.4349 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | WINK - AROYA 138 KV CKT 1 SUM 2020 - FUTURE (SINGLE B TO B)_MODIFIED_BY_MZ_2 | 138 | 20 | Branch MVA | 100 | - | - | 109.8196 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | WINK - BLUE MOUNTAIN DBL CKT 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 138 | 20 | Branch MVA | 100 | - | - | 101.1143 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | WINK - NOTREES 138 KV 2020 WIN - FUTURE (SINGLE B TO B) | 138 | 20 | Branch MVA | 100 | - | - | 101.4055 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | WINK - YUKON 138 KV 2019 SUM - FUTURE (SINGLE B TO B) CKT 2 | 138 | 20 | Branch MVA | 100 | - | - | 100.8254 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | WOLF - METEOR/REITER 345 KV 2026 SUM - FUTURE (DOUBLE B TO B) | 138 | 20 | Branch MVA | 100 | - | - | 100.7735 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | WOLF - QUARRY FIELD 345 KV LINE 2021 SUM - FUTURE (DOUBLE B TO B) | 138 | 20 | Branch MVA | 100 | - | - | 103.3115 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | WOLF - RED LAKES 138 KV WIN 2020 - FUTURE (SINGLE B TO B) | 138 | 20 | Branch MVA | 100 | - | - | 100.783 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | WOLF - YUCCA/RED LAKES 138 KV DCKT LINE (DOUBLE B TO B) | 138 | 20 | Branch MVA | 100 | - | - | 100.7511 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | XFMR-PBGENBUS_B-1 | 138 | 20 | Branch MVA | 100 | - | - | 103.4191 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | XFMR-PBGENBUS_B-2 | 138 | 20 | Branch MVA | 100 | - | - | 103.4076 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | XFMR-PBGENBUS_B-3 | 138 | 20 | Branch MVA | 100 | - | - | 103.4368 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | XFMR-PBGENBUS_B-4 | 138 | 20 | Branch MVA | 100 | - | - | 103.4211 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | XFMR-PBGENBUS_B-5 | 138 | 20 | Branch MVA | 100 | - | - | 103.4143 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | YUCCA - COURTNEY CREEK SWITCH 138 KV LINE (SINGLE B TO B) SUM 2025 - SUM 2028 | 138 | 20 | Branch MVA | 100 | - | - | 110.8735 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | YUCCA DRIVE - LOTEBUSH (AEP) 138 KV 2021 SUM - FUTURE (SINGLE B TO B) | 138 | 20 | Branch MVA | 100 | - | - | 110.875 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LOTEBUSH4A (60392) -> LOTEBUSH1A (60439) CKT 1 | YUKON - DUNE/WINK 138 KV DCKT 2019 SUM - FUTURE (DOUBLE B TO B) | 138 | 20 | Branch MVA | 100 | - | - | 100.8051 | - | - | - | -
TCLUBB | NORTH | NORTH | NORTH, NORTH | LP_DUNBAR3 (59181) -> LP_HOLLY3 (59168) CKT 1 | L_023928DBLMTN_5-023930FIDLWD_5C1 | 115 | 115 | Branch Amp | 1092.9491 | - | - | 102.3973 | 108.8165 | 130.76 | 120.2502 | -
TCLUBB | NORTH | NORTH | NORTH, NORTH | LP_MACKNZIE3 (59116) -> LP_NORTHEST3 (59120) CKT 1 | L_023920ABERNATH_5-023928DBLMTN_5C1 | 115 | 115 | Branch Amp | 1092.9491 | - | - | 100.8637 | 107.2155 | 129.2623 | 118.8509 | -
TCLUBB | NORTH | NORTH | NORTH, NORTH | LP_NORTHEST3 (59120) -> LP_DUNBAR3 (59181) CKT 1 | L_023920ABERNATH_5-023928DBLMTN_5C1 | 115 | 115 | Branch Amp | 1093.451 | - | - | - | - | 116.5114 | 106.1478 | -
TCLUBB | NORTH | NORTH | NORTH, NORTH | LP_NORTHWST3 (59121) -> LP_MCDONALD3 (59129) CKT 1 | L_023920ABERNATH_5-023928DBLMTN_5C1 | 115 | 115 | Branch Amp | 1092.9491 | - | - | - | - | 106.2387 | 100.2919 | -
TCLUBB | NORTH | NORTH | NORTH, NORTH | LP_YELHOUSE3 (59124) -> LP_NORTHWST3 (59121) CKT 1 | L_023920ABERNATH_5-023928DBLMTN_5C1 | 115 | 115 | Branch Amp | 1199.8844 | - | - | - | - | 103.1641 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LTV1_8 ( 2259) -> GRANDPR1_8 ( 2262) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 863.0967 | - | - | 109.0123 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LTV1_8 ( 2259) -> GRANDPR1_8 ( 2262) CKT 1 | CEDAR HILL SW 345-138 KV AUTO #1 | 138 | 138 | Branch Amp | 863.0967 | - | - | 101.7822 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LTV1_8 ( 2259) -> GRANDPR1_8 ( 2262) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 863.0967 | - | - | 111.9664 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | LTV1_8 (2259) -> GRANDPR1_8 (2262) CKT 1 | Pre-contingency | 138 | 138 | Amps | 863.0967 | - | - | - | 108.4407 | 145.322 | 120.2863 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LUTHER_8 (23831) -> COYOTE_8 (23832) CKT 1 | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 861.8416 | 114.2707 | 101.6819 | 106.6026 | 110.9726 | 115.7559 | 111.281 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LUTHER_8 (23831) -> COYOTE_8 (23832) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.7748 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LUTHER_8 (23831) -> COYOTE_8 (23832) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 104.2109 | 118.0496 | 109.1206 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | LUTHER_8 (23831) -> COYOTE_8 (23832) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 861.8416 | - | 125.4805 | - | - | - | - | -
TCPSE,TAEPTC | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTLE ( 5290) -> LYTLE4A ( 8962) CKT 1 | L_008221BIG_FOOT4A-008732DEVINE4AC1 | 138 | 138 | Branch Amp | 799.0861 | - | 117.5601 | - | - | - | - | -
TCPSE,TAEPTC | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTLE ( 5290) -> LYTLE4A ( 8962) CKT 1 | L_008732DEVINE4A-008962LYTLE4AC1 | 138 | 138 | Branch Amp | 799.0861 | - | 111.5829 | - | - | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | AEN_LP-AU¦DL_2013 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 109.85 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | AEN_LY-BF¦TV_2017 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 100.8849 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | AEN_P7 FPP-LP.DC_1 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 108.6403 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | AEN_P7 FPP-LP.DC_2 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 103.0948 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | DVCPA1C21B_1 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 115.4427 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | DVCPA1C21B_2 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 112.565 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | E_B_DAVIS_CC1_TRAIN | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 103.1146 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | E_BRAUNIG_CC1_TRAIN | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 100.5622 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | E_GUADG_CC1_TRAIN | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 100.2295 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | E_GUADG_CC2_TRAIN | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 100.1274 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | E_INGLCOSW_CC1_TRAIN | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 100.0782 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | E_NEDIN_CC1_TRAIN | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 103.4771 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | E_NUECES_B_CC1_TRAIN | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 103.4816 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | E5DVA1C1_1_B | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | 110.659 | - | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | G_170126CALAVER_JKS2UL2 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 105.2927 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | G_RIO_TRAIN | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 105.6066 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | J5LCA1C1_B | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 105.5499 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 123.9424 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 131.058 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 116.0097 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 119.4724 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 111.3596 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | L_005380SHAULA-005915SO_TEX__345AC1 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 111.4598 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 104.5505 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | L_007040L_AUSTRO5_1Y-007042L_ZORN__5_1YC1 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 113.1983 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | L_080071ZORILLO7A-080076AJO7AC1 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 100.5836 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | LCRA TSC_T182_T185 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 104.0222 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | LCRA TSC_T185_T352 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 105.8284 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | M10000271115801 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 103.2185 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | M115851115803 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 100.5836 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | MB100002711580 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 103.2185 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | MB1158011585 | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 100.5836 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | N5GSU2_B | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 105.2927 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | P7-1_E1>>T1839X1_ERC | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 112.4089 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | P7-1_E1>>T1839X2_ERC | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 115.2733 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | P7-1_E1>>T2764Y_ERCa | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 111.2971 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | P7-1_E1>>T3944Z_ERC | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 106.1889 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | R4U2A5C1_1_B | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 100.4557 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | STP - HOUDINI & STP - SHAULA | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 111.1266 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 100.4495 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> L_ZORN__5_1Y ( 7042) CKT 1 | WAP - HOUDINI & STP - SHAULA | 345 | 345 | Branch Amp | 1404.0488 | - | - | - | - | 111.5774 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> LYTTOSTR (500193) CKT 1 | 3WT_009074LYTTON5_009075LYTTON8_009081LYTTON_T2 C 2 | 345 | 1 | Branch MVA | 530 | - | - | - | - | 100.0689 | - | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON5 ( 9074) -> LYTTOSTR (500193) CKT 1 | 3WT_009074LYTTON5_009075LYTTON8_077075L_LYTTSP2_1Y C 3 | 345 | 1 | Branch MVA | 530 | - | - | - | - | 100.2725 | - | -
TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | LYTTON8 ( 9075) -> L_MENDOZ8_1Y ( 7325) CKT 1 | LCRA TSC_T410_T648 | 138 | 138 | Branch Amp | 1815.7246 | - | - | - | - | 104.5748 | - | -
TAEPTN | WEST | WEST | WEST, WEST | MAIZE2A (60029) -> SANA2A ( 6353) CKT 1 | L_006340BALLINGE4A-006360COLE_IVI4AC1 | 69 | 69 | Branch Amp | 393.2675 | - | - | - | 104.7032 | - | 104.659 | -
TAEPTN | WEST | WEST | WEST, WEST | MAIZE2A (60029) -> SANA2A ( 6353) CKT 1 | L_006347COLETAP4A-006360COLE_IVI4AC1 | 69 | 69 | Branch Amp | 393.2675 | - | - | - | 103.9236 | - | 103.8949 | -
TAEPTN | WEST | WEST | WEST, WEST | MAIZE2A (60029) -> SANA2A ( 6353) CKT 1 | L2020903 | 69 | 69 | Branch Amp | 393.2675 | - | - | - | 100.0593 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4735 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | 3WT_002427WATMLL_W5_002429WATMLL_8_012429WTML2_3 C 2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3488 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | 3WT_002427WATMLL_W5_002429WATMLL_8_012430WATMLL1_3 C 1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5634 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | 3WT_002433SGVLSW1_5_002434SGVLSW1_8_012434SGVLSW1_3 C 2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 109.72 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | 3WT_002437FRNY1_5_002438FRNY1_8_012438FRNY1_3 C 1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1755 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | AEN_LY-FPP:CIS-HO | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | AEN_LY-FPP¦CIS | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1298 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5893 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.7104 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.2625 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.9371 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.4694 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.7415 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.285 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.9686 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.5085 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4928 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.9964 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6213 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.9871 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | B2-COD-1_B | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1332 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | BARRETT_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.9999 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | BAS_RANCH_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.1965 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1050.108 | - | - | - | 104.4183 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1050.108 | - | - | - | 100.5954 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 106.3807 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 105.7594 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | BENBROOK-PARKER*CARMICHAEL BEND 345 KV WITH BENBROOK AUTO (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0939 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.6779 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | BEPC_015_2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.9248 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | BEPC_227-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0553 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | BEPC_227-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0553 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | BEPC_301_2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2787 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | BEPC_304_2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3209 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 108.576 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 114.4233 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | BLUBIRD_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.5529 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.743 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | BROWN SS - RUSSELL GAP / BUCKHORN_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2349 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | CARTWHEEL_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.1114 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | CEDAR HILL - DESOTO/LOOP NINE 345 KV DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.484 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 105.7558 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.5947 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | CLY_PHNT1P7F1-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0622 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.027 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2975 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | COODY CROSSING - TECUMSEH AND CLEAR CROSSING - THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2595 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | CORS-TRINIDAD_9 (SINGLE B TO B ) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3733 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | DERMOTT - KIRCHHOF CKT 1 & DERMOTT - KIRCHHOF CKT 2 345 KV (DOUBLE B TO B) C | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3494 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | DERMOTT - KIRCHHOF CKT 1 345 KV WIN 2023 - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4136 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | DES_WILL_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.5272 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | DRY_CREEK_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 106.1819 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.9499 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | DVCPA1C21B_1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.377 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | DVCPA1C21B_2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2408 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_FREC_CC2_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0622 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_FRNYPP_CC1_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 107.2623 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_FRNYPP_CC2_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 107.3345 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_JACKCNTY_CC1_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.8541 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_JCKCNTY2_CC1_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.2264 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_KMCHI_CC1_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.5398 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_KMCHI_CC2_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.5678 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_LPCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.0496 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_LPCCS_CC2_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.7481 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_OECCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.0097 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_OECCS_CC2_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.0145 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_PANDA_S_CC1_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.4844 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_QALSW_CC1_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0741 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_QALSW_CC2_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.061 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_TEN_CC1_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2908 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_TNSKA_CC1_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.8774 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_WCPP_CC1_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.0345 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_WHCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.3597 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | E_WHCCS2_CC2_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.9939 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | EAGLE MTN-PARKER/HICKS 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1195 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | EAST LEVEE - NORWOOD 138 KV & NORWOOD - WEST LEVEE 345 KV DCKT A LUPO | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3416 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | EDGEWOOD-ROYSE_8 (SINGLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.0309 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 105.2585 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 107.7922 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 115.7668 | 100.6493 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ENNIS - PEBBLE CREEK 138 KV SWITCH (SINGLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 105.7052 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ENNIS WEST - STERRETT 138 KV (SINGLE B TO B) A REAGOR SPRINGS | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.7617 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ERIKA_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.0606 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 105.322 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | FORNEY - ROYSE DCKT 345 KV(DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7612 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | FORNEY-CENTERVILLE SW/LAKE HUBBARD DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1137 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | FORNEY-EAST MESQUITE DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.8651 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_000575JCKCNTY5UN1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.3524 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_000579JCKCNTY8UN1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.1612 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_000971PRUITT_8US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6741 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_001777PARIS_8US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2031 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_001877MITCHBND_5UN1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5418 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_006100OKLA7AUC0 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.0364 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_006111RILEY7BUS1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0464 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_010012METEOR_5US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.8035 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_023908DEAFSMITH_5US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.389 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_023909WALLABY_5US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6797 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_060700GAUSS7AUS1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5263 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_060716SGSA4AUS1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0095 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_079000GRAYUS1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.2563 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_079000GRAYUW1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1379 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_120442BR_ARROW_S2US2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2824 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_120591STAM_SLR_S2US2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.237 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_120821HOPKINS_S1US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2419 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_143961MISAE2_S1US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.801 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_144011BRSFORK_S1US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0943 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_144211HRNTSLR_S1US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.9374 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_144261EIFSLR_S1US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5537 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_144511TROJAN_S1US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.072 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_144561BAKE_SLR_S1US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5029 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_144562BAKE_SLR_S2US2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5029 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150021MCSES_UNIT6UN6 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1804 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150022MCSES_UNIT7UN7 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2086 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150023MCSES_UNIT8UN8 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.3329 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150041GRSES_UNIT1UN1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2414 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150042GRSES_UNIT2UN2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.9362 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150051HLSES_UNIT3UN3 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.2844 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150052HLSES_UNIT4UN4 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.8267 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150053HLSES_UNIT5UN5 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.7438 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150082OLIN_OLING_2UN2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5261 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150083OLIN_OLING_3UN3 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.0171 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150084OLIN_OLING_4UN4 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2269 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150091LHSES_UNIT1UN1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.9031 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150092LH2SES_UNIT2UN2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.4029 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150111CPSES_UNIT1UU1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.3256 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150112CPSES_UNIT2UU2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.7231 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150133MIL_MILLERG3UN3 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.037 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150151MDANP_CT1UN1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2922 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150152MDANP_CT2UN2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3441 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150153MDANP_CT3UN3 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3268 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150154MDANP_CT4UN4 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3232 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150155MDANP_CT5UN5 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3306 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_150156MDANP_CT6UN6 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.337 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_151371LILY_S1US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 112.5405 | 100.0606 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_151373LILY_B1UB1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4033 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_152081NOBLESLR_R1US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0174 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_153141PORT_SLR_S1US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4782 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_153361SWRSTRG_B1UB1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.4549 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_153532ELIZA_S1US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3721 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_153911PNGT1_PV_S1US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.5931 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_154331CMPDREPV_S1US1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3005 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_170126CALAVER_JKS2UL2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1094 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_5920EASTDCTIE | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.4525 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_6103NORTHDCTIE | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1503 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_888839BAS_RANCH_POIUC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.2012 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_888848BARRETT_POIUS1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3061 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_888851TRIFECTA_POIUN1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7803 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_888854PINEFOREST_POIUB1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0292 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_888854PINEFOREST_POIUS1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.007 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_888856HOLLY_POIUS1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3164 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_888866HANSON_POIUS1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1716 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_888874VIKING_POIUS1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2995 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_888879BLUBIRD_POIUS1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.7229 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_888881SOLAC_POIUS1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3783 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_888883QUANT_POIUS1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2483 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_888885GALAC_POIUS1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4061 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | G_RIO_TRAIN | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0157 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | GALAC_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1603 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | GLASGOW_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 108.0437 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | GRAHAM UNIT 2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.9362 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | GreenRD Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.9478 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | HANSON_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4384 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | HICKS - EAGLE MTN*PARKER 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.8074 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | HICKS -ALLIANCE 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4503 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | HIGHNOON_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1292 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | HILLSBORO-ASH CREEK 138 KV (SINGLE B TO B) B | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.5533 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | HOLLY_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6891 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | J5LCA1C1_B | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0171 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | JEWETT-BALE*TWINOAK_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7134 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.512 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | KRUM WEST - RILEY A 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4062 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 115.9582 | 100.5274 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 116.1175 | 100.6672 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000200CHATFIELD-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3923 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000200CHATFIELD-003455CORS1_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5689 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000221TRUMBULL8-002229PEBBLCRK_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.9075 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000221TRUMBULL8-012344GAMMA_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 105.7296 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000234CHATT-003352PECANST_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.5281 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000234CHATT-003522HILLBORO1_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.3102 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000237BLANTON-888875THRESLR_POIC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4561 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000237BLANTON-888889MIDPOINT_POIC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4046 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000436GRANDVIEW-000443SANDFLATSWC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0658 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000443SANDFLATSW-000444COVINGTONC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1008 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000444COVINGTON-888859HIGHNOON_POIC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1423 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000646LEWISVLSW5_1-021851DUNHAM_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3481 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000842GPL_KINGMTSW-000843GPL_KINGMTTPC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2498 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5925 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_000902POES31569-000981SPNCRINT69C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1332 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4257 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001141HOLTSS_8-132313ECEC_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.223 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001421WILLOWCK_5-031875RAMHORNH_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1657 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001421WILLOWCK_5-031875RAMHORNH_5C2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1657 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001436PARKER_5-001859BASECAMP_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2681 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001436PARKER_5-002081HICKS_SW1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4179 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001685FARMVLSW_5-001729VAL_STH_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2265 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001685FARMVLSW_5-002461ROYSE_N5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5915 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001685FARMVLSW_5-002478ROYSE_S5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5667 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001685FARMVLSW_5-011689CYCLONE_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.539 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001685FARMVLSW_5-011700SALTILLO_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.175 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 108.7654 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001695MOSES_5-001697SULSP_SS1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7112 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001697SULSP_SS1_5-888847CARTWHEEL_POIC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.6482 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001730W_KRUM_5-011736BIRDDOG_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.295 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001730W_KRUM_5-152087NOBLESLR_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7806 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001816COMM_SW_8-001818SCTBRCH1_9C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2241 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001818SCTBRCH1_9-001824NEYLNDVL1_9C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1983 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001824NEYLNDVL1_9-001827CADMLX_T8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2006 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001827CADMLX_T8-001831CADMHW66_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2008 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001829BURROW_T8-001837INGLE_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1116 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001831CADMHW66_8-001837INGLE_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1996 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.3744 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001880ROCKYCRK_5-888879BLUBIRD_POIC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3585 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001895MITCHBND2_5-002285CARMICHL_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.029 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.8893 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.1469 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.9168 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.2933 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001906VENUS_S5-015201FORBESR2_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.8468 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001906VENUS_S5-888857OYSTER_POIC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.8251 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001906VENUS_S5-888880DES_WILL_POIC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.1519 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.621 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.1865 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001907VENUS_N5-015200FORBESR1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.1821 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001907VENUS_N5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.715 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001921LIGGETTA1_5-002632MILLERRD_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.1173 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001928LIGGETT_3T5-002406NORWD1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.17 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.2809 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.6072 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002217BATCHLRD_8-002427WATMLL_W5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4257 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002217BATCHLRD_8-002427WATMLL_W5C2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.425 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 108.576 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 107.7922 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.176 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002279CLEBRNSW_8-002290CLEBRN_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.785 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002290CLEBRN_8-002291CLEBRN_W_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.9728 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002291CLEBRN_W_8-037810TNHILL_CO_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.2231 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002315WAX_PMP2_8-002319WAX_PMP1_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.5623 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002315WAX_PMP2_8-002320WAX_N_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.601 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002316MG_IND_T8-002319WAX_PMP1_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.4213 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002320WAX_N_8-002321WAX_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.4622 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.0452 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 114.8185 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 114.4747 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002340MELSSA_P8-002374ANNASW_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2592 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002340MELSSA_P8-002704ANNASE_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0994 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002406NORWD1_5-012398TOPEKA1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2168 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002420CHILSW1_5-015204MRRFLD_RD1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2226 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3966 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3966 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002429WATMLL_8-003083WILMER1_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.1982 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002432TRICRN1_5-002433SGVLSW1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1415 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 108.1283 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | 116.1299 | 140.8408 | 116.9145 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002432TRICRN1_5-888878ERIKA_POIC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.847 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002437FRNY1_5-002453CNVLSW1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2493 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 107.3177 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 107.2758 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002465DUCKCOVE_P8-003163DCVERC_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.8669 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002465DUCKCOVE_P8-012467ABLSPRG2_P8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7753 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 107.8027 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002471ROYSE_S_8-012469ABLSPRG_P8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7057 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002478ROYSE_S5-002485POETRY_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.9859 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002485POETRY_5-003103SHAMBRGR_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.1622 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002753WINDMF_T8-012713BLACKLND_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2116 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002756MSQTE1_8-002771ESIDE2T_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.319 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_002771ESIDE2T_8-002775MSQT1_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2591 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003100MARTINLK_5-003102TYLERGND_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.511 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003100MARTINLK_5-003116MTENTRPR_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6875 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 105.1546 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003109STRYKER_5-003123TRINDAD1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.5075 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.1094 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003127TRINIDAD_8-003276MALAKOFF_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6346 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003127TRINIDAD_8-003723OLYMPUS_SWC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.3837 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003133RICHLND2_5-003199CALFRESTN_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0654 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 107.1577 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003163DCVERC_8-003169IRONBRG_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.8669 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003165TAWAKRC_T8-003167ENTERPRI_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.0062 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003165TAWAKRC_T8-003169IRONBRG_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.9704 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003167ENTERPRI_8-003188WILLSPNT_9C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.3984 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003174CANTNSW_8-003181EDGEWOOD_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.8028 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003176MABANK_8-003179PAULINE_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3254 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003177EUSTACE_8-003179PAULINE_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4694 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003177EUSTACE_8-006951EUST6751C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6279 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003180CANTON_RAY_8-006828CANTAPRC_138C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5901 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003181EDGEWOOD_8-003188WILLSPNT_9C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.7794 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003276MALAKOFF_8-006951EUST6751C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0695 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003352PECANST_8-003473ASHCREEK_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.5667 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.6387 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003374FILESVALY_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.2568 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003377LITTLEPOND_5-003687BELL_E_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6976 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003377LITTLEPOND_5-003704HOGCREEK_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3657 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 112.2689 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003381BIGBRNW_5-003391JEWETT_N5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.1519 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003384STJOHNS_5-003409LAKE_CRK1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.3723 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003384STJOHNS_5-003711BALE_S5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.7572 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003386OUTLAW_5-046020LIMEST_POI_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.9646 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003386OUTLAW_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.036 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003388FOURBTHRS_5-003405THOUSE__5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6316 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003388FOURBTHRS_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.1235 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003390JEWETT_S5-003711BALE_S5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7775 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003409LAKE_CRK1_5-013405THOUSE_A_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2224 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003410LAKE_CRK1_8-003702RIESEL_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1144 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5153 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.8936 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003460CORS_GL_T_8-003461CORSGLAS1_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0349 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003473ASHCREEK_8-003515HUBBARD_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3932 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003477EUREKA_P__8-003478NAVARRO1_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1064 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003477EUREKA_P__8-003483GOODLOE_P_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1791 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003483GOODLOE_P_8-003490LNGPRAIRIE_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4657 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003518BLUMPUMP1_8-037810TNHILL_CO_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.2829 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003597GROESBECP_8-888888FEWELL_S1C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6736 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003687BELL_E_5-003705BRANGUS_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7771 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003704HOGCREEK_5-039950TNTNP_ONE_3C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0324 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003705BRANGUS_5-003706GIBSON_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.521 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003706GIBSON_5-039950TNTNP_ONE_3C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1128 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_003723OLYMPUS_SW-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.0486 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.5011 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5004 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7071 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2112 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_005380SHAULA-005915SO_TEX__345AC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2168 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2575 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.3413 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_006802RY_RYMOND_RC-006829GLNPSSRC_138C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.8807 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_006823KIOWA_RC-006871LNOK_RCC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1551 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_006823KIOWA_RC-006884QUINL_RCC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.082 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_006828CANTAPRC_138-006829GLNPSSRC_138C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5903 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_006860UVSS_RC-006883NQUIN_RCC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7951 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_006860UVSS_RC-006886BLDSW_RCC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5953 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_006896OAKGV_RC-006908SCURY_RCC2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5005 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_006903BOZE-006908SCURY_RCC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.3218 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_006903BOZE-151372LILY_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 113.2658 | 100.8863 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_007077L_AMOSCR5_1Y-183171GALLOWAY_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0378 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.827 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_011270DOGHOUSE_5-023876CLEARFRK_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6628 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_011270DOGHOUSE_5-134805PROSPERO_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0056 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_011684BRIGHTR_5-011689CYCLONE_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2538 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_011688THORNTRE_5-143625SAMSON_1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.0014 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_011688THORNTRE_5-143705DELILA_1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.5432 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_012329SHANKLSW_8-012344GAMMA_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 105.7344 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_013401TIGERCK_5-013405THOUSE_A_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2221 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_013401TIGERCK_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.8614 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.6438 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.3151 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_021851DUNHAM_5-033646LEWISVLSW5_2C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3364 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_023920ABERNATH_5-141607AEEC_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7019 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_046020LIMEST_POI_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.1369 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_059906LONGDRAW_138-134145JUNO_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0289 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_059909NOVA_138-059998NOVA8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.0189 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_059909NOVA_138-143115NOVA1SLR_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5008 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_059911MHOS-183406JADE_HI_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1969 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_060011NEBULA7A-183525ANDMDSLR_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0926 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_068011ASPIRE-068051REATAC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2256 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_081003HABER7A-081005ACME7AC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.667 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_143575SAMSON_3_5-143625SAMSON_1_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5966 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_143705DELILA_1_5-143757DELILA_2_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.9052 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 106.689 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_888847CARTWHEEL_POI-002464CASHSW_T5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.9184 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_888848BARRETT_POI-006871LNOK_RCC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1906 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_888857OYSTER_POI-068091NAVARROC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.1518 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2478 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_888874VIKING_POI-011886TIMBERVW_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1171 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_888876P_BTTLECRK_POI-003515HUBBARD_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6098 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 106.6136 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_888878ERIKA_POI-003105ELKTON_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.7411 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_888880DES_WILL_POI-001916LIGGETTA2_5C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.3737 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L_888889MIDPOINT_POI-003518BLUMPUMP1_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.2993 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L201000169 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7021 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | L20255426 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7021 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LAKE CREEK - LAKE HALL/TRADINGHOUSE_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.1235 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LAKE CREEK-RATTLESNAKE/RIESEL_5_8 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1146 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LAKE CREEK-RATTLESNAKE/ST JOHNS_5 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.3727 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LATIMER_REATA_P7F1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.5735 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LCRA TSC_BAKERS_CEDACA_DC | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4878 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2475 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1658 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2475 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1658 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LCRA TSC_NOELK_SNGTR_NOELK_SNGTR2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1416 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LCRA TSC_SNGTR_SCHDR_SNGTR_SCHDR2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0479 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LCRA TSC_T255_TAE3121_1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2217 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6365 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7113 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.8019 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.8998 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.5306 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.377 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.5349 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LIGGETT-NORWOOD 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4569 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.6715 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.4695 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.5578 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 113.2204 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MB210140210145-AAAAA | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.4297 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MB210140210145-AAAAB | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.6168 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MB210140210145-AAABA | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7881 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MB210140210145-AABA | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.2271 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MB210140210145-AABB | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5895 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MB210140210145-ABAAA | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.1305 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MB210140210145-ABAAB | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.9531 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MB210140210145-ABABB | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.9636 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MB210140210145-ABBA | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7524 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MB2551525514 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.355 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MB255152551420840 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3456 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MB2726627277 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2507 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 105.2995 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5823 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.5532 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNIT 4 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6382 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.4251 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 113.6718 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ML-SK*MNT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.244 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | MOSES-SULPHUR SPRINGS SW 345-138 KV AUTO SULPHUR SPRINGS SW 345-138 KV AUTO #1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.2997 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | N5GSU2_B | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1094 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | NAVARRO - LONG PRAIRIE 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.2156 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 109.3018 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | NAV-CORS_W-MONTFORT_8 (SINGLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.6823 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-1-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7436 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7436 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3067 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | NEW-HILLSBORO-CLEBURNE_SW_8 (SINGLE B TO B )-1-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3067 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 113.7656 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | 103.1765 | 119.6347 | 104.1565 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | NORTHWEST CARROLLTON - LEWISVILLE SW (BEPC) 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.9949 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | NORWOOD - WEST LEVEE 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3636 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | NORWOOD-LIGGETT 345 & MOUNTAIN CREEK - LIGGETT 138 KV DCKT A BLUBONT | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.9273 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ODESSA EHV - NORTH MCCAMEY 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2615 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | OYSTER_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.1471 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | P7-1_E1>>T1839X1_ERC | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2297 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | P7-1_E1>>T1839X2_ERC | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3662 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | P7-1_E1>>T2764Y_ERCa | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.121 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | P7-1_E1>>T3944Z_ERC | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2907 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | P7-1_E1>>T4848K | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2709 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 107.2593 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | PARIS SW-MOSES 345 KV-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2567 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | PARKER-COMANCHE PEAK 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6928 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.1473 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV DCKT & EAGLE MOUNTAIN - WEATHERFORD 138 KV LINE | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.9945 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | PINEFOREST_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.3209 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | QUANT_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.096 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | RAMHORN - DUNHAM DC 345 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3608 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (COMMON TOWER) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.6369 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | RAMHORN - WILLOW CREEK DC 345 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.9405 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | REAT_SKYD_P7F2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2814 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | ROYSE-EDGEWOOD 138 KV (SINGLE B TO B) A | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.0309 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | RYBRN_P1-2_CANTON TAP-CANTON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.6385 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | RYBRN_P1-2_EUSTACE-EUSTACE | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7993 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.1354 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 107.5072 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 106.346 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | SAM_NAV_P7F1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0905 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | SCUR_CLY_P7 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1363 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | SEAGOVILLE SW - FORNEY/TRICORNER DCKT 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 109.2989 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | SHAMBURGER - POETRY_5(SINGLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.1622 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | SHAMBURGER-BLACKFORK/POETRY_8_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.4722 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | SOLACE_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1531 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | STECL_4720 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2804 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | STECL_4721-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2475 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | STECL_4721-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1658 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | STP - HOUDINI & STP - SHAULA | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1108 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | T_000981SPNCRINT69-000982DN_STEAM_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1332 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | T_002437FRNY1_5-002438FRNY1_8C2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0896 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | T_002474ROYSE1_T5-002473ROYSE1_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.6156 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | T_002483ROYSE3_5-002460ROYSE3_8C1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.6127 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | T_059908NOVA_345-059998NOVA8CT1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.0189 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7516 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.0408 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.4941 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | THOUSE-LCRK*PCNCRK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.0005 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | THRESLR_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2278 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6826 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TIMBERVIEW-COMANCHE PEAK*CARMICHAEL BEND 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.5436 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TIMBERVIEW-COMANCHE PEAK*DECORDOVA 345 KV (SINGLE B TO B)-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.8067 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.8688 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TIMBERVIEW-VENUS 345 KV DOUBLE-CIRCUIT LINE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.046 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.8701 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.8717 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TRICORNER - TYLER GRANDE (single B TO B) new_load | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.7057 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 115.8255 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 111.3839 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 109.9197 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TRIFECTA_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7784 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TRIN-EUSTACE SE (SINGLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.7354 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 113.0268 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 116.565 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 138 | 138 | Branch Amp | 1050.108 | - | - | - | 129.1878 | - | 126.8652 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.0053 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.9376 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.0479 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VALLEY S-ANNA SW 345 KV & VALLEY S-FARMERSVILLE 345 KV | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3726 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VALLEY S-VALLEY SW 345 KV & VALLEY S-PARIS SW 345 KV | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3914 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3483 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.811 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 106.4517 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 108.0152 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 107.2729 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 107.0243 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.6323 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.5224 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VENUS-FORT SMITH SW 345 KV (SINGLE B TO B) new load | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.8043 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.8739 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6741 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6741 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.795 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.1159 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.903 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VENUS-SAM SW 345 KV (SINGLE B TO B) new load | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.2238 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | VIKING_CON | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.8763 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | WAP - HOUDINI & STP - SHAULA | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3241 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.3975 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | Watermill Switch-Batchler Rd SW 345 kV Line CKT1(SINGLE B TO B) new load | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.4257 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | WAXAHACHI-WAXAHACHI OFC 69KV/ENNIS-STERRETT 138KV (DOUBLE B TO B) A REAGOR | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.0077 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.5108 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.6603 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.4017 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | WILLOW CREEK - TECUMSEH/THOMAS PRICE 345 KV DCKT WIN 2023 - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2164 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | WILLOW CREEK - THOMAS PRICE\TECUMSEH CREEK 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV WIN 2023 - FUTURE (TRIPLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1318 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.0352 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | WINDMILL - AJSWOPE (SINGLE B TO B) SUM 2028 - FUTURE | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6781 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.385 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C2_345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.199 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | WSHACK_LATIMER_P7 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.004 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-GRHAMSES1_8-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2414 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-HANDLEYC_8-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.2844 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-HANDLEYC_8-3 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.7438 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-HANDLEYD_8-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.8267 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-LKHB_1T8-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.9031 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-LKHB_2T8-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 104.4028 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-MDLTHELP_5-5 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3306 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-MDLTHELP_5-6 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.337 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-MDLTHELP_N5-3 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3267 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-MDLTHELP_N5-4 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3232 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-MDLTHELP_S5-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2922 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-MDLTHELP_S5-2 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.3441 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-MTCK_6T8-6 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1804 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-MTCK_7T8-7 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.2086 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-MTCK_8T8-8 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 103.3329 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-WHCCS2_4-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.6382 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-WHCCS2_5-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 102.5452 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-WLFHMDPT_5-1 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 101.3848 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MANKIN_8 ( 3265) -> CEDRCKPU_8 ( 3263) CKT 1 | XFMR-WLFHOSTR-3 | 138 | 138 | Branch Amp | 1050.108 | - | - | - | - | 100.1987 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MARCONI4A ( 8266) -> P_ISABEL4A ( 8338) CKT 1 | P7/C5-SHRY-1 | 138 | 138 | Branch Amp | 903.6786 | - | - | - | 109.9575 | 110.9959 | 110.2047 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MARTINCAP_9 ( 1231) -> MIDBASIN_9 ( 1228) CKT 1 | T_001330SPRABERY_9-001329SPRABERY_8C1 | 69 | 69 | Branch Amp | 334.6958 | - | - | - | 153.671 | 227.862 | 227.3084 | -
TONCOR | EAST | EAST | EAST, EAST | MARTINLK_5 ( 3100) -> DRY_CREEK_POI (888845) CKT 1 | TRIN-SK*ME (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 111.3173 | 101.6535 | -
TONCOR | EAST | EAST | EAST, EAST | MARTINLK_5 ( 3100) -> TYLERGND_5 ( 3102) CKT 1 | DRY_CREEK_CON | 345 | 345 | Branch Amp | 2399.7688 | - | - | - | - | 102.5895 | - | -
TONCOR | EAST | EAST | EAST, EAST | MARTINLK_5 ( 3100) -> TYLERGND_5 ( 3102) CKT 1 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 345 | 345 | Branch Amp | 2399.7688 | - | - | - | - | 101.8143 | - | -
TONCOR | EAST | EAST | EAST, EAST | MARTINLK_5 ( 3100) -> TYLERGND_5 ( 3102) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | 345 | Branch Amp | 2399.7688 | - | - | - | - | 105.5945 | - | -
TONCOR | EAST | EAST | EAST, EAST | MARTINLK_5 ( 3100) -> TYLERGND_5 ( 3102) CKT 1 | TRIN-SK*ME (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2399.7688 | - | - | - | - | 100.3046 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | 3WT_023875EINSTN_5_023852EINSTN_8_023874EINSTN_3 C 1 | 138 | 138 | Branch Amp | 748.8818 | 141.5265 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | EINSTEIN - CARTERVILLE 138 KV LINE 2025 SUM - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | 144.0007 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | L_001328QUARTZSAND_8-010029LILDEWEY_8C1 | 138 | 138 | Branch Amp | 748.8818 | 147.6323 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | L_010018CARTVLRNCH_8-023851CARTRVL_8C1 | 138 | 138 | Branch Amp | 748.8818 | 144.0008 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | L_010018CARTVLRNCH_8-023852EINSTN_8C1 | 138 | 138 | Branch Amp | 748.8818 | 143.9897 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | L_010029LILDEWEY_8-011350WRGRN_P8C1 | 138 | 138 | Branch Amp | 748.8818 | 147.5505 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | L_010032LILLUTHER_8-023831LUTHER_8C1 | 138 | 138 | Branch Amp | 748.8818 | 101.5426 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | L_010032LILLUTHER_8-023835VLMOOR_8C1 | 138 | 138 | Branch Amp | 748.8818 | 101.5382 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | L_010041SALEM_8-023832COYOTE_8C1 | 138 | 138 | Branch Amp | 748.8818 | 100.1906 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | L_010041SALEM_8-023833BULLDOG_8C1 | 138 | 138 | Branch Amp | 748.8818 | 100.1941 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | L_010080REDBERRY_8-023833BULLDOG_8C1 | 138 | 138 | Branch Amp | 748.8818 | 124.8721 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | L_010080REDBERRY_8-900043Other_132C1 | 138 | 138 | Branch Amp | 748.8818 | 125.2114 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | L_011337POLECAT1_8-011350WRGRN_P8C1 | 138 | 138 | Branch Amp | 748.8818 | 143.7187 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | L_023831LUTHER_8-023832COYOTE_8C1 | 138 | 138 | Branch Amp | 748.8818 | 101.0913 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | L_023834ELBOW_8-900043Other_132C1 | 138 | 138 | Branch Amp | 748.8818 | 122.4894 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | L_023834ELBOW_8-900100Other_131C1 | 138 | 138 | Branch Amp | 748.8818 | 120.0228 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | L_023851CARTRVL_8-023853EILAND_8C1 | 138 | 138 | Branch Amp | 748.8818 | 139.5989 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | L_023875EINSTN_5-059903BEARKATC1 | 138 | 138 | Branch Amp | 748.8818 | 141.5267 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | LUTHER - VEALMOOR 138 KV LINE 2026 SUM - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | 101.5397 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | Prairieland-Quartzsand Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | 114.5938 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | QUARTZ SAND - POLECAT CREEK 138 KV LINE SUM 2024 - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | 143.746 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 ( 1333) -> GLASSCNTYN_8 ( 1334) CKT 1 | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | 104.7469 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MCDONALD_8 (1333) -> GLASSCNTYN_8 (1334) CKT 1 | Pre-contingency | 138 | 138 | Amps | 748.8818 | - | 102.7071 | 109.0489 | 113.7373 | 129.4844 | 119.4681 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | MCNEIL_DB1 ( 9076) -> MCNEIL_MB1 ( 9079) CKT 1 | AEN_MC-DP¦DE | 138 | 138 | Branch Amp | 2008.1747 | - | - | - | - | 102.8468 | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2168 | 100.0209 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | 3WT_002431DESSW1_5_002424DESSW1_8_012431DESSW1_3 C 1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | 3WT_002433SGVLSW1_5_002434SGVLSW1_8_012434SGVLSW1_3 C 2 | 138 | 22 | Branch MVA | 625 | - | - | 100.1011 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | 3WT_013125TDADTMOD_5_003127TRINIDAD_8_120151TRSES_UNIT6 C 1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1075 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | AEN_LP-AU¦DL_2013 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0355 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | AEN_LY-FPP:CIS-HO | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0131 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | AEN_LY-FPP¦CIS | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0238 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | AEN_P2HLJ345_RB_570_610_1(94OF224): | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1766 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0968 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | AEN_P7 FPP-LP.DC_1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0041 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | AEN_P7 FPP-LP.DC_2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0063 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW 345-138 KV AUTO #1 (SINGLE AUTO) | 138 | 22 | Branch MVA | 625 | - | - | 100.0365 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 138 | 22 | Branch MVA | 625 | - | - | 100.2168 | 100.025 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0203 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0518 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0204 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0531 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0272 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.1208 | 100.0608 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0305 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.0952 | 100.0642 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0275 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.1159 | 100.061 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0306 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.089 | 100.0643 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-1 | 138 | 22 | Branch MVA | 625 | - | - | 100.035 | 100.0202 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.0843 | 100.0453 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-1 | 138 | 22 | Branch MVA | 625 | - | - | 100.0267 | 100.0202 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.0727 | 100.0453 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLEN-MOSES 345-138 AUTO-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.2168 | 100.0251 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0316 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.1831 | 100.0654 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0298 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.1526 | 100.0631 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ARGENTA_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1554 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | B2-COD-1_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0506 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BARRETT_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0359 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BAS_RANCH_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | 100.0568 | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.1942 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.1349 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0636 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0454 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BEPC_015_2 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0191 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BEPC_211 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0511 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BEPC_22 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0646 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BEPC_227-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0423 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BEPC_227-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0423 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BEPC_23_2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0099 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BEPC_230_4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0281 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BEPC_304_2 | 138 | 22 | Branch MVA | 625 | - | - | 100.1093 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BEPC_311_2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0117 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BEPC_460 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0106 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 138 | 22 | Branch MVA | 625 | - | - | 100.2168 | 100.0491 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0108 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BIGSAMPSON_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0149 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BITTER CREEK SW (LCRA) - CATTLEMEN SW & BITTER CREEK SW (LCRA) - SWEETWATER EAST 345 KV (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0852 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BLUBIRD_CON | 138 | 22 | Branch MVA | 625 | - | - | 100.1145 | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0275 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BROWN SW - RED CREEK SW (AEP) 345 KV WIN 2020 - FUTURE (SINGLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0233 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BRYN_1035 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0058 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BRYN_1036 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0048 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | BRYN_1037 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0378 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | CACTUS_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0884 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | CARLSON - STEGER (LCRA)_8 (SINGLE B TO B ) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0452 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | CARROLLTON NW-HACKBERRY-NORWOOD 345KV (SINGLE B TO B) HACKBERRY 345/138 TRANSFORMER | 138 | 22 | Branch MVA | 625 | - | - | 100.2067 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | CARTWHEEL_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0204 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | Cattleman-Longshore Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0012 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.027 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | 100.0517 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | CLUTCH_CITY_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0636 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | COMANCHE - BROWNWOOD SW 138 KV (SINGLE B TO B )B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0057 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0052 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | COMANCHE PEAK-JOHNSON*TIMBERVIEW 345 KV (DOUBLE B TO B)-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | COODY CROSSING - TECUMSEH AND CLEAR CROSSING - THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0311 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | CROCKETT-LUFKIN_138(SINGLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0139 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | D5GSU1_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0346 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | D5GSU2_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0346 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | DERMOTT - COTTONWOOD/MHOS (WETT) CKT 1 345 KV (SINGLE B TO B) C | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0023 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | DERMOTT - DERMOTT WIND 345 KV (SINGLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.041 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | DERMOTT - FLAVIANA/GOPHER WIND 138 KV (SINGLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0182 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | DERMOTT - KIRCHHOF CKT 1 & DERMOTT - KIRCHHOF CKT 2 345 KV (DOUBLE B TO B) C | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1642 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | DERMOTT - KIRCHHOF CKT 1 345 KV WIN 2023 - FUTURE (SINGLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1638 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | DES_WILL_CON | 138 | 22 | Branch MVA | 625 | - | - | 100.092 | 100.0179 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | DRY_CREEK_CON | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.1054 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | DUNE - WINK/YUKON 138 KV 2019 SUM - FUTURE (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0807 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | DUNHAM - LEWISVILLE DC 345 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0145 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | DVCPA1C21B_1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0115 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | DVCPA1C21B_2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0059 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_AMOCOOIL_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0447 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_AMOCOOIL_CC2_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_AMOCOOIL_CC2_TRAIN_NSO | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_B_DAVIS_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_BASTEN_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_BOSQUESW_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0997 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_BOSQUESW_CC2_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_BRAUNIG_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_BTE_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_BVE_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_BYU_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1454 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_CBEC_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0753 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_CBEC_CC2_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0872 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_CBECII_CC3_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_CBY4_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_CCEC_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_CHE_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_CVC_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_DDPEC_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_DIB_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1346 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_DUKE_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_ETCCS_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | 100.033 | 100.1725 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_FERGCC_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_FLCNS_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0669 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_FREC_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1283 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_FREC_CC2_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2169 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_FRNYPP_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_FRNYPP_CC2_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_FTR_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_GUADG_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_GUADG_CC2_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_INGLCOSW_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_JACKCNTY_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | 100.054 | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_JCKCNTY2_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | 100.1255 | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_KMCHI_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | 100.06 | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_KMCHI_CC2_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | 100.0633 | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_LGE_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2016 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_LOSTPI_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_LPCCS_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_LPCCS_CC2_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2169 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_NEDIN_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_NUECES_B_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_OECCS_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_OECCS_CC2_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_PANDA_S_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_PANDA_T1_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_PANDA_T2_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_PSA_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_PSG_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_QALSW_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1239 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_QALSW_CC2_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1215 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_RAYBURN_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0831 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_RIONOG_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_SANDHSYD_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.15 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_SILASRAY_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0184 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_TEN_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1322 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_TGCCS_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_THW_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1469 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_THW_CC2_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1469 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_TNSKA_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1015 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_TXCTY_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1632 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_VICTORIA_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1378 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_WCPP_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_WFCOGEN_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0143 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_WHCCS_CC1_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E_WHCCS2_CC2_TRAIN | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E5DVA1C1_1_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E5DVA1C1_1_B_1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1007 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | E5DVA1C1_1_B_2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0644 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ELMAX_POI_Con | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ELPATR_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.049 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0448 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ERIKA_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0886 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.03 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | FORNEY - TRI CORNER/SEAGOVILLE SW DCKT 345 KV (DOUBLE B TO B) A M4227 | 138 | 22 | Branch MVA | 625 | - | - | 100.1844 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_000099BENHURUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0544 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_000575JCKCNTY5UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_000579JCKCNTY8UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1868 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_000971PRUITT_8US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0477 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_001700TOCO_8US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_001729VAL_STH_5UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0166 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_001777PARIS_8US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0494 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_001877MITCHBND_5UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1531 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_003306STEKLY_DAM_5UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0007 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_003306STEKLY_DAM_5US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.092 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_003321REDLAND_5UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_003377LITTLEPOND_5US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.067 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_003420TEMP_PEC__8US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0659 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_003423KILL_SS__8UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0036 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_003478NAVARRO1_8US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0649 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_003705BRANGUS_5US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0218 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_003706GIBSON_5US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0633 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_003707CANNON_8US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0121 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_003717TORTOISE_5US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0671 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_003717TORTOISE_5US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0453 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_005506FURHMANSW8US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.052 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_005555SHROPSHRSUB9US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0202 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_005660ORANGEGRVSW8US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0406 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_005700MIRCLLAKSUB8US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0332 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_005705FOWLERTNSUB8UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0058 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_006100OKLA7AUC0 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_006111RILEY7BUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0869 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_007041L_JOHNDU5_1YUN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0896 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_007044L_MARION5_1YUN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_007048L_GARFIE5_1YUN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_007599L_LEESVI8_1YUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0226 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_007680L_CLEASP8_1YUB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.005 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_008003PRIMAVER4AUB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0138 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_008107TYNAN2AUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0085 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_008249ANGSTRM7AUB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0055 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_008249ANGSTRM7AUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0957 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_008573BONILLA7AUW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.094 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_008573BONILLA7AUW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0327 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_008704GULCH7AUB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0043 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_008707DRYFRIOUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0578 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_008736SNAPDRAG4AUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.034 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_010012METEOR_5US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_011419COODYCROSS_5UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0225 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_023906AJSWOPE_5US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0701 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_023908DEAFSMITH_5US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1445 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_023909WALLABY_5US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1878 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_023913KRESS_5US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0628 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_038340TNAIRPORT41UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0019 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_038465TNSTONERD_1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0002 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_038740TNHEIGHTS_1UB2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0062 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_038900TNHDNLAKES1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0032 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_038900TNHDNLAKES1UB2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0074 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_039030TNALVIN___1UB2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0112 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_039703TNFM524___1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0032 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_040000CEDARP_B345AUC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_040700GRNBYU__B345UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1612 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_040710GRNBYU_POI8AUN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2113 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_040890DANEK__POI_8UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0306 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_042400REFUGE_POI_5UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0532 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_042440HAWKIN_POI_5US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0738 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_042770ASHVIL_POI_8US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0005 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_043060SPEDWY_POI_5US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0656 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_043060SPEDWY_POI_5US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1735 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_043060SPEDWY_POI_5US3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0377 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_043060SPEDWY_POI_5US4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_043180SAVANA_POI_5UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0011 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_043340GLFTIE_POI_8UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1415 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_043990ELMATO_POI_5UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0013 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_043990ELMATO_POI_5US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0573 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_043990ELMATO_POI_5US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1902 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_044040BAILEY_POI_5US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0571 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_044040BAILEY_POI_5UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0032 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_045500T_H_W__POI_5UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2148 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_045515T_H_W__POI_8UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2146 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_046220PETERS__B138UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0018 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_047150H_O_C___B138UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0228 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_048262SOWYCK26TP_8UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.004 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_059904COTTONWOODUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0655 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_060700GAUSS7AUB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0034 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_060700GAUSS7AUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1687 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_060716SGSA4AUB2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0105 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_060716SGSA4AUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1176 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_068004PHNTMHLUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0646 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_068014OPENSKYUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.06 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_068025WRANGLERUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.066 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_068035HELIXUW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0074 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_068051REATAUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1559 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_071213L_BENEDU8_1YUB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0185 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_076026L_SODALA8_1YUB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0059 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_079000GRAYUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_079000GRAYUW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1099 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_079007YELLOWWOLFUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1602 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_080039LUCERO7AUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1204 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_080039LUCERO7AUS2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0964 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_080219LOBO7AUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1135 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_080219LOBO7AUS2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0691 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_080229CAVAZOS4AUB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0139 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_080355DELSOL7AUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0716 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_085000N_SHARPE7AUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0475 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110011WAP_WAP_G1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0076 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110012WAP_WAP_G2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0077 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110013WAP_WAP_G3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.027 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110014WAP_WAP_G4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0689 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110015WAP_WAP_G5UL5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0604 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110016WAP_WAP_G6UL6 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110017WAP_WAP_G7UL7 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110018WAP_WAP_G8UL8 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110020WAP_GT2UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0169 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110052THW_THWGT51UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0093 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110053THW_THWGT52UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0093 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110054THW_THWGT53UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0093 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110055THW_THWGT54UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0093 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110056THW_THWGT55UN5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0093 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110057THW_THWGT56UN6 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0093 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110071CBY_CBY_G1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110072CBY_CBY_G2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110092GBY_GBYGT73UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0096 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110093GBY_GBYGT74UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0076 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110094GBY_GBYGT81UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0076 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110095GBY_GBYGT82UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0046 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110096GBY_GBYGT83UN5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0116 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110097GBY_GBYGT84UN6 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0091 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110114DOWG_DOW_G61UP1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0154 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110116DOWG_DOW_G63UP1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0154 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110123DOWG_DOW_G67UP1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0286 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110124DOWG_DOW_G66UP1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0288 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110125DOW_DOW_ST65UP1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0286 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110135DOWG_DOW_G81UP1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0174 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110137DOWG_DOW_G82UP1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0174 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110139DOWG_DOW_G83UP1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0174 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110141DOW_DOW_ST84UP1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0234 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110146DOW_DOW_GT96UP1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0655 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110147DOW_DOW_ST95UP1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0058 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110171DIB_DIB_G1UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0152 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110172DIB_DIB_G2UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0152 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110173DIB_DIB_G3UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0265 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110174DIB_DIB_G4UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0188 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110201BYU_BYU_G1UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0209 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110202BYU_BYU_G2UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0209 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110203BYU_BYU_G3UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0209 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110204BYU_BYU_G4UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0209 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110271AMOC_AMOCO_1UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0127 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110272AMOC_AMOCO_2UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0127 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110280AMO_AMOCO_G1UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0545 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110281AMO_AMOCO_G2UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0545 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110282AMO_AMOCO_G3UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0545 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110283AMO_AMOCO_S1UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0176 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110284AMO_AMOCO_S2UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0176 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110351STP_STP_G1UU1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110352STP_STP_G2UU2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110374EXN_EXN_G4UP4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0253 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110451FOR_FORMOSG1UP1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0114 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110452FOR_FORMOSG2UP2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0114 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110453FOR_FORMOSG3UP3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0114 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110454FOR_FORMOSG4UP4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0129 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110455FOR_FORMOSG5UP5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0129 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110457FOR_FORMOSG7UP7 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0013 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110460FO_FORMOSG10UPA | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0115 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110467FO_FORMOSG11UPB | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0279 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110469FO_FORMOSG12UPC | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0279 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110481SJS_SJS_G1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0212 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110482SJS_SJS_G2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0212 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110501SCLP_SCLPC_1UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0371 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110502SCLP_SCLPC_2UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0371 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110503SCLP_SCLPC_3UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0372 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110504SCLP_SCLPC_4UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0372 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110521CAL_CALGT1UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0467 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110522CAL_CALSTG1UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0102 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110571PSA_PSA_G1UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0105 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110572PSA_PSA_G2UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.011 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110573PSA_PSA_G3UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0115 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110574PSA_PSA_G4UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0118 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110575PSA_PSA_G5UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0112 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110576PSA_PSA_G6UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0107 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110577PSA_PSA_G7UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0387 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110661CHE_CHEGT1UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0437 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110662CHE_CHEST1UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0665 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110681DUP_DUPV1_G1UP1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0187 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110701LHM_CVC_G4UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0639 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110731BTE_BTE_G1UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.079 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110732BTE_BTE_G2UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0532 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110733BTE_BTE_G3UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0532 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_110734BTE_BTE_G4UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0532 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111132BAC_CTG1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0103 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111133BAC_CTG2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0113 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111134BAC_CTG3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0053 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111135BAC_CTG4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0078 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111136BAC_CTG5UN5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0078 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111137BAC_CTG6UN6 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0068 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111181FEGC_N1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0292 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111221CALHOUN_N1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0032 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111241CALHOUN_N2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0032 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111261CHAMON_N1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0027 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111262CHAMON_N2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0027 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111302LEVEE_N1UP1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0178 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111341VICTPORT_1_8UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0045 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111342VICTPORT_2_8UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0045 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111361CITYVICT_N1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0047 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111362CITYVICT_N2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0047 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111381PEY_CRK_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0259 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111442INC_FORMOS14UPG | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0229 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111443INC_FORMOS1UPF | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0163 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111531MYR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0418 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111532MYR_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0334 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111581MUSTNGCK_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0039 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111582MUSTNGCK_S2US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0156 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111631DANISH_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.095 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111632DANISH_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0011 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111633DANISH_S3US3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0374 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111801PRO_N1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111802PRO_N2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111803PRO_N3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111804PRO_N4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0034 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111805PRO_N5UN5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0034 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111806PRO_N6UN6 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0034 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111807PRO_N7UN7 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0034 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111808PRO_N8UN8 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0034 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111861BCK_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0629 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111862BCK_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0643 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111961TOPAZ_G1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0026 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111962TOPAZ_G2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0026 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111963TOPAZ_G3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0026 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111964TOPAZ_G4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0026 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111965TOPAZ_G5UN5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0026 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111966TOPAZ_G6UN6 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0026 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111967TOPAZ_G7UN7 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0026 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111968TOPAZ_G8UN8 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0026 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111969TOPAZ_G9UN9 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0026 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_111970TOPAZ_G10UN0 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0026 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112041HOL_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0453 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112042HOL_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0479 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112261SPACECI_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0162 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112311VICTPRT2_G1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0045 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112312VICTPRT2_G2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0045 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112331LIG_G1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0014 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112332LIG_G2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0014 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112351OLDHCKRY_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0722 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112411RABBS_N1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0029 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112412RABBS_N2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0029 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112413RABBS_N3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0029 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112414RABBS_N4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0029 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112415RABBS_N5UN5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0029 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112416RABBS_N6UN6 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0029 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112417RABBS_N7UN7 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0029 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112418RABBS_N8UN8 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0029 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112491JAY_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0489 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112492JAY_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.046 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112591BCH_G1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.002 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112592BCH_G2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.002 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112593BCH_G3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.002 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112594BCH_G4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.002 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112595BCH_G5UN5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.002 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112596BCH_G6UN6 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.002 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112611ROW_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0184 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112612ROW_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0559 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112661LON_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0083 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112871GSTAR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0292 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112872GSTAR_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0204 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112873GSTAR_S3US3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0218 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_112875GSTAR_S4US4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0203 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113031BCH_N7UN7 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0022 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113032BCH_N8UN8 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0022 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113051GARCITAS_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0685 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113111LUNIS_CK_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113161TEXANA_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0405 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113211JAD_N1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0061 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113212JAD_N2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.006 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113213JAD_N3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.006 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113214JAD_N4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.006 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113215JAD_N5UN5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.006 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113216JAD_N6UN6 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.006 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113217JAD_N7UN7 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.006 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113218JAD_N8UN8 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.006 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113251MLZSLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0775 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113321SOHOBS_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0017 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113331CTDLBS_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0012 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113341TNGLWDPV_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0785 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113391TECO_N1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0065 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113431COTBAYOU_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0443 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113432COTBAYOU_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0443 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113531REDEGRET_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0117 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113541XE_MURAT_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0035 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113601SOHO_II_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0017 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113611IRONMANB_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.012 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113751CASCADE_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0774 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113801ABYBS_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0019 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_113921PARLIMNT_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1716 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_114051ADO_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0018 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120041MLSES_UNIT1UL1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120042MLSES_UNIT2UL2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120043MLSES_UNIT3UL3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120051DAN_DANSBYG1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0378 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120052DAN_DANSBYG2UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0048 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120053DAN_DANSBYG3UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0058 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120071TNP__TNP_O_1UL1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0624 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120072TNP__TNP_O_2UL2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0624 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120131OGSES_UNIT1AUL1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120132OGSES_UNIT2UL2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120141SCSES_UNIT1AUN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0659 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120142SCSES_UNIT2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120151TRSES_UNIT6UN6 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1076 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120191KELAM_SL_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0052 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120261TREB_SLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0542 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120391STARRSOL_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.041 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120441BR_ARROW_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0332 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120442BR_ARROW_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.053 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120542BOARDCRK_W2UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0046 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120591STAM_SLR_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0536 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120592STAM_SLR_LUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0123 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120691GLENPINE_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0308 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120801TNZNTBES_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0091 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120821HOPKINS_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0526 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120822HOPKINS_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.012 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_120871AZALEA_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0511 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_130011PB2SES_CT1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.018 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_130012PB2SES_CT2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0186 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_130013PB2SES_CT3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0186 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_130014PB2SES_CT4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0186 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_130015PB2SES_CT5UN5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0192 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132111SRWE1_UNIT1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.007 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132161SRWE1_SRWE2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0012 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132311ECEC_G1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0652 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132312ECEC_G2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0652 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132332REROCK_UNIT1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0158 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132333REROCK_UNIT2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0158 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132431SIRIUS_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0311 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132436SIRIUS_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0032 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132481RIGGINS_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0514 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132631SANTRITA_G1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0001 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132731BOOTLE_UNIT1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0341 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132781CASLGP_UNIT1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0609 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132831HOLMAN_UNIT1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0033 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132881LMESASLR_G1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.025 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132882LMESASLR_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0025 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132941SPTX12B_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0508 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_132991BEARKAT_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.006 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_133041BEARKAT_W2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0016 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_133341W_PECOS_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0259 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_133841WAYMARK_W1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0609 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134091OBERON_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0604 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134141JUNO_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0494 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134142JUNO_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0415 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134241TAYGETE_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0385 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134243TAYGETE_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0399 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134341LDRAW_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0228 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134343LGDRAW_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0355 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134441LAPETUS_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0246 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134541SAGEDRAW_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.001 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134542SAGEDRAW_W2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.001 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134591QUEEN_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0261 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134592QUEEN_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0261 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134593QUEEN_S3US3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0238 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134594QUEEN_S4US4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0283 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134652WHMESA_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0001 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134654WHMESA_U2UW3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.004 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134701TYGTEII_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0277 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134702TYGTEII_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0277 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134751FOWLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0488 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134801PROSPERO_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0473 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134802PROSPERO_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0457 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134901GREASEW_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0355 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134902GREASE_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0381 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134951EUNICE_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0634 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_134953EUNICE_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0842 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_135011TI_SOLAR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0425 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_135012TI_SOLAR_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0399 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_135111ARAGORN_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0651 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_135181PRSPERO2_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0355 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_135182PRSPERO2_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0355 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_135321REDBARN_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0785 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_135501RDOSLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0677 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_135591BRP_PAVO_BTUBT | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0044 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_135601HYDRA_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0046 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_135731APPALOSA_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0026 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_136101BLUESKY_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.029 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_136161DRSOLAR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0024 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_136281SHAMROCK_WUW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0066 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_136341TRBNT_PV_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1175 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_136441SWIFTAIR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0468 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_140011DND_DENISOG1UH1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0055 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_140181MWEC_G1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0057 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_140401BCAT_WND1UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0007 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_140441SSPUR2_WINDUW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0053 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_140471MIAMI_G1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_140472MIAMI_G2UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_140902WAKE_UNIT2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0032 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_141001SCLAY_UNIT1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.006 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_141051JRDWIND_1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0031 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_141052JRDWIND_2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0042 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_141151RT66_WIND1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0038 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_141302BRISCOE_G1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0041 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_141401SPLAIN2_WND1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.004 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_141451SPLAIN2_WND2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0045 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_141502COTWIND_W2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0044 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_141607AEEC_5UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0942 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_141609ELK_G3UN6 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0839 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_141662SOLARA_UNIT1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0306 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_141711HWFWF_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0057 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_142561FOARDCITY_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0031 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_142562FOARDCITY_W2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0004 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_142661CBREAKS_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.013 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_142811MISAE_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0316 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_142812MISAE_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0304 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_142912BLSMTIII_W2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0026 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_142961LOCKETT_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0027 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143111NOVA1SLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0328 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143112NOVA1SLR_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0328 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143116SRNOVA2_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0657 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143261CONGLI_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0324 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143311AZURE_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0117 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143312AZURE_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.045 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143321RIPPEY_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0071 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143374TRUSGILL_W4UW4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0056 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143421PHOENIX_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0155 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143521AJAX_UNIT1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0085 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143571SAMSON_3_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0077 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143572SAMSON_3_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0314 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143621SAMSON_1_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0314 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143622SAMSON_1_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0314 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143691BRPDICKE_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0031 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143701DELILA_1_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0415 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143702DELILA_1_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0415 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143751DELILA_2_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0231 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143752DELILA_2_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0211 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143753DELILA_2_S3US3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0231 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143901PALEO_ES_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143911SAMSON_2_S3US3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0211 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143912SAMSON_2_S4US4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0211 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_143961MISAE2_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1993 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_144011BRSFORK_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1085 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_144062INERTIA_W3UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0054 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_144064INERTIA_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0652 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_144161NOVA2SLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0634 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_144211HRNTSLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_144261EIFSLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0766 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_144311FRYE_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0811 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_144312FRYE_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0811 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_144362GOODNITE_W2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0019 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_144411GOODNITE_W3UW3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0004 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_144461MONTW_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0047 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_144511TROJAN_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0473 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_144561BAKE_SLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0759 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_144562BAKE_SLR_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0759 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_144721TWOFORKS_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0182 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150021MCSES_UNIT6UN6 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0544 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150022MCSES_UNIT7UN7 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.053 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150041GRSES_UNIT1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1146 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150042GRSES_UNIT2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2002 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150051HLSES_UNIT3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150052HLSES_UNIT4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150053HLSES_UNIT5UN5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150071SPNC_SPNCE_4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0143 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150072SPNC_SPNCE_5UN5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150082OLIN_OLING_2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0433 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150083OLIN_OLING_3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0662 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150084OLIN_OLING_4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0277 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150091LHSES_UNIT1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2147 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150092LH2SES_UNIT2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150101LEG_LEG_G1UL1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150102LEG_LEG_G2UL2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150111CPSES_UNIT1UU1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1779 | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150112CPSES_UNIT2UU2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150131MIL_MILLERG1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0181 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150132MIL_MILLERG2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0438 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150133MIL_MILLERG3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0929 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150134MIL_MILLERG4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0343 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150135MIL_MILLERG5UN5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0343 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150151MDANP_CT1UN1 | 138 | 22 | Branch MVA | 625 | - | - | 100.0344 | 100.1135 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150152MDANP_CT2UN2 | 138 | 22 | Branch MVA | 625 | - | - | 100.0324 | 100.1226 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150153MDANP_CT3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1232 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150154MDANP_CT4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1232 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150155MDANP_CT5UN5 | 138 | 22 | Branch MVA | 625 | - | - | 100.0318 | 100.1203 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150156MDANP_CT6UN6 | 138 | 22 | Branch MVA | 625 | - | - | 100.0318 | 100.1214 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150211LNCRK_G83UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0052 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150611HWF_HWFG1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0012 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150714STEA_STEAM_3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0035 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150721DCSES_CT10UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0193 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150722DCSES_CT20UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0193 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150723DCSES_CT30UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0188 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150724DCSES_CT40UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0193 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150741SCES_UNIT1UL1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_150962GWEC_G1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_151142FLAT_TOP_5UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0056 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_151191DEC_AGR_AUN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0146 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_151192DEC_AGR_BUN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0146 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_151193DEC_AGR_CUN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0146 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_151194DEC_AGR_DUN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0146 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_151261BAIRDWND_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0041 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_151371LILY_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0449 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_151421STRATEGC_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0402 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_151551VISION_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0351 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_151701CROWN_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0215 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_151751RADN_SLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0487 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_151752RADN_SLR_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0504 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_151851PRIDDY_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.004 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_151971GRIZZLY_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0229 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_152031GOLINDA_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0216 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_152081NOBLESLR_R1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0451 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_152082NOBLESLR_R2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.037 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_152132ROSELAND_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0477 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_152133ROSELAND_S3US3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0151 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_152231MARKUM_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0457 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_152281ELLISSLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0171 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_152331FILESSLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0427 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_152381PISGAH_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0586 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_152382PISGAH_S2US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.007 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_152531YNG_WND_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0051 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_152581ESTONIAN_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.016 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_152582ESTONIAN_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0262 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_152681TURQBESS_G1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0033 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_152731FENCESLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0366 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_152732FENCESLR_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0203 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153031AGUAYO_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0047 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153081DILEOSLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0096 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153141PORT_SLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0886 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153191CORAL_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0194 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153192CORAL_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153241ANGUSSLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0256 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153291BIGELM_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0643 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153361SWRSTRG_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.005 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153381FIVEWLLS_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0603 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153382FIVEWLLS_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0336 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153388FIVEWLLS_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0051 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153532ELIZA_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0476 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153581BTSRANCH_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0034 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153631DORADO_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1482 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153681HALO_SLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0846 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153731TNS_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0281 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153732TNS_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0281 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153911PNGT1_PV_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_153961GAIA_SOL_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0438 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_154011MIDPOINT_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0247 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_154061DIVER_PV_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.072 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_154161LANGER_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0839 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_154221ASHCRKSL_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0081 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_154281CLINGHAM_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1261 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_154331CMPDREPV_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1127 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_154411ANOLEBES_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.012 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_154421DESERTWL_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0001 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160002LARDVFTN_G4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.033 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160003LARDVFTN_G5UN5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0314 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160074PEARSAL_ENG1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0089 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160075PEARSA_ENG10UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0089 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160076PEARSA_ENG13UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0089 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160077PEARSA_ENG19UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0089 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160101B_D_B_DAVIG1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1586 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160131SAN_SANMIGG1UL1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2076 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160151INGLCOS_CTG1UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0741 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160152INGLCOS_CTG2UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0741 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160153INGLCOSW_STGUPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0712 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160161KOC_KOCHUPG1UP1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0042 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160201LGE_LGE_GT1UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0677 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160202LGE_LGE_GT2UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0677 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160203LGE_LGE_STGUPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0256 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160261CCEC_GT1UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0562 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160262CCEC_GT2UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0562 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160263CCEC_ST1UPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0637 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160274SIL_SILAS_10UNA | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0106 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160291PENA_UNIT1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.038 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160292PENA_UNIT2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0312 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160293PENA_UNIT3UW3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160296BAFFIN_UNIT1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0164 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160297BAFFIN_UNIT2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0171 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160391PAP1_PAP1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0453 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160392COTTON_PAP2UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0527 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160491TGW_T1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0312 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160492TGW_T2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0312 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160591CEDROHI_CHW1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0005 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160691REDFISH_G1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0176 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160693REDFISH_G2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0189 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160741LV1_LV1AUW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0547 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160742LV1_LV1BUW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.055 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160881LV3_UNIT1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0071 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_160982CAMWIND_G1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0421 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_161032REDGATE_G1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.013 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_161033REDGATE_G2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.013 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_161034REDGATE_G3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.013 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_161035REDGATE_G4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.013 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_161103BRDS_JAVEL20UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0091 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_161451CHAWND_UNIT1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0352 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_161452CHAWND_UNIT2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0164 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_161501MIDWIND_UNIUW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.039 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_161551LV4_UNIT1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.007 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_161602SANROMAN_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0175 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_161651PATWND_UNIT1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0628 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_161751BBREEZE_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.024 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_161752BBREEZE_W2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0198 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_161951STELLA_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0526 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162001KNKWA1_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0175 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162002KNKWA1_W2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0175 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162051KNKWA2_W3UW3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0165 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162101MESTENO_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0072 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162152ELRAYO_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162153ELRAYO_W2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0159 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162201CRANEL_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0097 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162251CHALUPA_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0449 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162301PALMWIND_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0342 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162541MCLNSLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0671 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162691ELTRUENO_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0233 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162692ELTRUENO_W2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0258 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162741LMJDSW_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0215 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162742LMJDSW_W2UW3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0322 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162791HRZN_SLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0657 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162841ELARA_SL_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0371 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162861MORRLAKE_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.023 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162862MORRLAKE_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0229 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162911BLACKJAK_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0231 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_162912BLACKJAK_W2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0232 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163021NEBULA_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0461 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163071ALGODON_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0422 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163121VANCOURT_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0024 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163171BRIGHTSD_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0035 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163221CORAZON_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0682 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163321SPARTA_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0452 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163322SPARTA_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0267 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163411ELSAUZ_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.036 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163412ELSAUZ_W2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0343 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163521PEREGRN_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1174 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163571JACKALOPE_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0157 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163572JACKALOPE_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0158 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163641CHARGER_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1641 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163691REDONDA_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0916 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163801GUAJILLO_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.004 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163811SIETWIND_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0277 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163861ANEMOI_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0055 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163881TULSITA_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0939 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_163931OUTPOST_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2045 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_164071MONTECR1_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0121 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_164121CAROL_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0061 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_164201GUNNAR_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0052 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170032MAR_MARSFOG2UH2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170063LEON__LCPCT1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0077 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170064LEON__LCPCT2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0077 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170065LEON__LCPCT3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0077 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170066LEON__LCPCT4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0077 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170071GID_GIDEONG1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0547 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170072GID_GIDEONG2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0574 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170073GID_GIDEONG3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1729 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170101FPPYD_FPP_G1UL1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170102FPPYD_FPP_G2UL2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170103FPPYD_FPP_G3UL3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170126CALAVER_JKS2UL2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170137BRAU_VHB6CT5UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.009 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170138BRAU_VHB6CT6UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.009 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170139BRAU_VHB6CT7UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.009 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170140BRAU_VHB6CT8UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0084 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170153DECKE_DPGT_1UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0084 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170154DECKE_DPGT_2UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0084 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170155DECKE_DPGT_3UN5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0084 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170156DECKE_DPGT_4UN6 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0084 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170191HAY_HAYSENG1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1014 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170192HAY_HAYSENG2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1123 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170193HAY_HAYSENG3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1118 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170194HAY_HAYSENG4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1031 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170211SANDHSYD_SH1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0079 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170212SANDHSYD_SH2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0079 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170213SANDHSYD_SH3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0079 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170214SANDHSYD_SH4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0079 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170217SANDHSYD_SH6UN6 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.008 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170218SANDHSYD_SH7UN7 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.008 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170331WIPOP_WPP_G1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0047 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170331WIPOP_WPP_G1UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0047 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170332WIPOP_WPP_G3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0047 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170332WIPOP_WPP_G3UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0047 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170441CFLATS_U1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170521E_BLACK_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0448 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170601BIG_STAR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0355 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170602BIG_STAR_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0103 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170671CACHENA_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170721PADUA_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.005 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_1707717RNCHSLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0382 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_1707727RNCHSLR_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0224 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170821EBELLSLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0774 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170825EASTBELL_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0417 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170881LIBRA_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0048 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170891EBONY_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0048 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170901SHLA_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0646 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_170951SHLA_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0646 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_171021AURE_SLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0632 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_171071FERDINAN_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.005 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_171091MPP_N1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0854 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_171111MANDORLA_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0836 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_171161SYPBRNCH_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0924 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_171221GRANSLR1_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0024 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_180031MGSES_CT1UN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0187 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_180032MGSES_CT2UN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0181 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_180033MGSES_CT3UN3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0181 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_180034MGSES_CT4UN4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0193 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_180035MGSES_CT5UN5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0193 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_180036MGSES_CT6UN6 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0193 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_180441SPPKM_CTAUPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.005 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_180442SPPKM_CTBUPE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0056 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_180453BUFF_G_UNIT3UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0017 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_180456H_HOLLO_WND1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0095 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_180458HHOLLO_WIND1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0034 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_180460HHOLLO_WND_1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0108 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_180751CAPRIDGE_CR1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0097 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_180756CAPRIDGE_CR3UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0054 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_181051TTWEC_G1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0016 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_181251LGD_LANGFORDUW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0005 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_181732HELIOS_G1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0237 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182052RTS_34UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0005 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182151EGROVESL_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0303 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182201WL_RANCH_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.006 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182251HOLSTN_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0247 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182252HOLSTN_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0248 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182303PHOEBE_3US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0364 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182305PHOEBE_5US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0377 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182403WKNAMAD_W3UW3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0023 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182451WHITHRSE_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0064 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182452WHITHRSE_W2UW2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0064 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182501RAMBLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0668 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182601NORTON_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0346 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182721AVIATOR_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0029 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182725AVIATOR_W3UW3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0058 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182771MAVCRK1_W_S1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0055 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182821ANSON1_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0223 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182822ANSON1_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0223 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_182971MARYNEAL_W1UW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0032 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_183071CAPRIDG4_S1US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.024 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_183172GALLOWAY_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0878 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_183221GALLOWAY2_S1US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0278 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_183351RATLIFF_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0496 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_183401JADE_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0467 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_183402JADE_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0483 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_183451CROWDEDS_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0713 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_183521ANDMDSLR_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0466 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_183522ANDMDSLR_S2US2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0483 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_183571SUNRAY_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0678 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_183621ZIER_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0524 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_183681TENNYSON_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0452 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_183781ANG_PV_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0649 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_5920EASTDCTIE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_6103NORTHDCTIE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1028 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888838GRAPHIC_GAS_POIUN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0043 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888839BAS_RANCH_POIUC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | 100.0562 | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888840SKULLCREEK_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0364 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888841ELMAX_POIUN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888842IRON_BELT_POIUB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0272 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888845DRY_CREEK_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0623 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888846TIDWELL_POIUB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0022 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888848BARRETT_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.035 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888849CLUTCH_CITY_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.055 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888851TRIFECTA_POIUN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888853BIGSAMPSON_POIUW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0146 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888854PINEFOREST_POIUB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.03 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888854PINEFOREST_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1116 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888856HOLLY_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1566 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888856HOLLY_POIUS2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0911 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888857OYSTER_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0761 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888858ARGENTA_POIUB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0002 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888858ARGENTA_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.126 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888859HIGHNOON_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.056 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888860RUBICONALPHA_POIUW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0091 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888861LEON_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0633 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888865MALDIVES_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0705 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888866HANSON_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1529 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888867INDIGO_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.033 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888868CACTUS_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0328 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888868CACTUS_POIUS2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0329 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888870BTTM_GRSS_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0602 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888871ELPATR_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0488 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888872SKYSLY_POIUN1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0561 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888872SKYSLY_POIUN2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0565 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888874VIKING_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1064 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888875THRESLR_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0268 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888876P_BTTLECRK_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0148 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888877GLASGOW_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0688 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888878ERIKA_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.069 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888879BLUBIRD_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888881SOLAC_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1407 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888882BUZIOS_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0853 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888883QUANT_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1375 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888884HART_POIUW1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0065 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888885GALAC_POIUS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0689 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888886DESTINY_B1UB1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0012 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | G_888888FEWELL_S1US1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0277 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | GALAC_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0727 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | GLASGOW_CON | 138 | 22 | Branch MVA | 625 | - | - | 100.2168 | 100.1392 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | GRAHAM UNIT 2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2002 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | GRAPHIC_GAS_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0043 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | HANSON_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1652 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | HART_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0084 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | HIGHNOON_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0597 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | HOLLY_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1028 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | INDIGO_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0358 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | IRON_BELT_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0371 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | J5CT1_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0708 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | J5CT2_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0711 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | J5CT3_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0711 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | J5GSU1_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0708 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | J5GSU2_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0711 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | J5GSU3_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0711 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | J5GSU4_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1545 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | J5LCA1C1_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | J5ST1_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1545 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | JACKSBORO SW-BOWMAN SW 345 KV A | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0079 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | JW-CROCKETT (SINGLE B TO B)-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0449 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | JW-CROCKETT (SINGLE B TO B)-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0449 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.034 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0787 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | KRUMW-WEST DENT/DUNHAM 345 KV (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0135 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_000192TELICO-002331ENNS_PMP_T8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1498 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_000221TRUMBULL8-002229PEBBLCRK_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2171 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_000842GPL_KINGMTSW-000843GPL_KINGMTTPC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.163 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_000860GPL_GIRVINSW-136341TRBNT_PV_S1C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1175 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_000902POES31569-000981SPNCRINT69C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0506 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001064SUN_8-180256BRAZ_WND_CB1C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0005 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001067GOLDENSW_8-180653CSEC_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0115 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1855 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001141HOLTSS_8-132313ECEC_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1508 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001163LAMESA_8-132883LMESASLR_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0468 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001301WILLOWVAL_8-131955BULLCRK_3_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0012 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001333MCDONALD_8-131143MCDLD_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0092 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001339ESKOTA_8-180052TRENT_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0007 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001442COKFIELD_5-011400COKFIELD1_5C3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0013 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001444BROWN_5-151756RADN_TLINEC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1185 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001458COBB_T5-141002SCLAY_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.006 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001466BYRDSW_5-143525AJAX_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0257 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001475WINDTHOR_8-140402BCAT_WND_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0007 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001653MERCERSGAP_8-151035LGW_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.007 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001685FARMVLSW_5-011689CYCLONE_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0139 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001690VALLYSES1_5-002373ANNASW_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0024 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2168 | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001695MOSES_5-001697SULSP_SS1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0021 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.2168 | 100.0248 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001697SULSP_SS1_5-888847CARTWHEEL_POIC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0008 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001730W_KRUM_5-152087NOBLESLR_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001739DENISND_T8-006949DENISDMA_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0199 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001839STONCRK_8-140002SHER1_TLC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001880ROCKYCRK_5-888879BLUBIRD_POIC1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0063 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001904WEBB3_5-002420CHILSW1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0023 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0057 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0081 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001906VENUS_S5-015201FORBESR2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0015 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001906VENUS_S5-888857OYSTER_POIC1 | 138 | 22 | Branch MVA | 625 | - | - | 100.074 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001907VENUS_N5-002632MILLERRD_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0041 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001907VENUS_N5-068091NAVARROC1 | 138 | 22 | Branch MVA | 625 | - | - | 100.0087 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001919SHRY_A8-002257PARKROW1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.0181 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001922LIGGETT_N8-002124INT_AIR1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2168 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001928LIGGETT_3T5-002406NORWD1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1576 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2168 | 100.0491 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002217BATCHLRD_8-003159ELROD_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2168 | 100.0448 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1443 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002263GELLER_8-003079SSWWT2T_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1784 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002263GELLER_8-003083WILMER1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1393 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002286PADERA_8-002310MDLTHTXI2_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1443 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002289SOAPCRK_8-002310MDLTHTXI2_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1377 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002315WAX_PMP2_8-002319WAX_PMP1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1084 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002315WAX_PMP2_8-002320WAX_N_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1208 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002316MG_IND_T8-002319WAX_PMP1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.0603 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002320WAX_N_8-002321WAX_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1559 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002321WAX_8-012320TMPLTON_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.0955 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.0277 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002372COLLINSS1_5-002373ANNASW_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0085 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002406NORWD1_5-012398TOPEKA1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2168 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0125 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0125 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002429WATMLL_8-003065REINDEER_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1583 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.0094 | 100.022 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1 | 100.0282 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002432TRICRN1_5-888878ERIKA_POIC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0061 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002434SGVLSW1_8-003076SGVL1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002461ROYSE_N5-002513ALLENSW1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.0557 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2168 | 100.0428 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003076SGVL1_8-003077KLEBRG1T_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003077KLEBRG1T_8-003079SSWWT2T_8C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1893 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003100MARTINLK_5-003102TYLERGND_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0054 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 138 | 22 | Branch MVA | 625 | - | - | 100.0536 | 100.0163 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003133RICHLND2_5-003199CALFRESTN_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2169 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003134RICHLND1_5-003186CALPFREST_5C2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1283 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003159ELROD_5-068091NAVARROC1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2168 | 100.0373 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0055 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003374FILESVALY_5-068090SAMSWC1 | 138 | 22 | Branch MVA | 625 | - | - | 100.006 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003380BIGBRNE_5-068091NAVARROC1 | 138 | 22 | Branch MVA | 625 | - | - | 100.0157 | 100.0005 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003385COWBAYOU_8-151703CROWN_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0215 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003385COWBAYOU_8-152033GOLINDA_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0216 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003386OUTLAW_5-046020LIMEST_POI_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0013 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003386OUTLAW_5-068091NAVARROC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0153 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003386OUTLAW_5-120545BOARDCRK_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0188 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003389FORTSMITH_5-152333FILESSLR_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0431 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003403LAKE_HALL_5-151317PHILLWND_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0164 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0645 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003424BUCK_H_5-151856PRIDDY_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0183 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003490LNGPRAIRIE_8-152736FENCESLR_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0845 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003702RIESEL_8-153195CORAL_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0525 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_003711BALE_S5-153733TNS_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0759 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0673 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0186 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005133ELMCREEK-005380SHAULAC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0314 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005180GREEN_MT-170893EBONY_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0047 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0056 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005380SHAULA-005915SO_TEX__345AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0057 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005502RAYBURN8-005513RAYBURNPLNT8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.083 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005521GALOWSW8-111583MUSTNGCK_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0465 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005760PALMASSW8-005764ERIOHONDOSB8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0343 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005761PAREDESSW8-160981CAMWIND_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0443 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005779REDSWTAP8-005784REDGATESW8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1119 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005779REDSWTAP8-161031REDGATE_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1119 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005798AMISTAD8-008686AMISTD4AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0044 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005866PALODUROSW8-005890ELARA8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0371 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005885DOWNIESW8-181731HELIOS_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0238 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005895PEARSALLSUB8-005896MORROWSW8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0656 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005895PEARSALLSUB8-005897HORIZONSW8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0657 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005895PEARSALLSUB8-058959PEARSALLSCB8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0943 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005897HORIZONSW8-162793HRZN_SLR_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0657 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0021 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006015MADDUX4A-183353RATLIFF_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0496 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006104SMOKYHIL7A-142062SALVTION_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0106 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006111RILEY7B-141351ELECTRA_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0313 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006150SPUR4A-140182MWEC_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0057 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006216BLF_CRK4A-170249PONY_3_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0037 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006216BLF_CRK4A-170250PONY_4_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0107 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006216BLF_CRK4A-180455BUFF_GAP_2_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0455 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006216BLF_CRK4A-180457H_HOLLOW_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0094 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006351NICOLE4A-181052TTWEC_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0017 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006490SANTIAGO4A-181252LGD_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.001 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006562FDRAN4A-136103BLUESKY_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.029 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006601RIOPECOS4A-076601L_HORSCR8_1YC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0302 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006630FTST4A-132482RIGGINS_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0514 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006674BRONCO2A-132832HOLMAN1_9C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0033 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006802RY_RYMOND_RC-120692GLENPINE_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0308 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006843BRTN6843-006852BENWH_RCC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0052 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006852BENWH_RC-120193KELAM_SL_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0052 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006867NATHN6867-006899WALTNSS6899C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0091 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_006903BOZE-151372LILY_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0513 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_007070L_GOLDTH8_1Y-150961GWEC_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_007077L_AMOSCR5_1Y-182777MAVCRK_W_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0417 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_007077L_AMOSCR5_1Y-183171GALLOWAY_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.135 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_007126L_FERGUS8_1Y-180015FERGGT1_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0795 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_007126L_FERGUS8_1Y-180016FERGGT2_2_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0795 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_007126L_FERGUS8_1Y-180017FERGST1_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0872 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_007279L_MULDOO8_1Y-1707737RNCHSLR_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.08 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_007304L_WIPOPA8_2Y-007307L_PINECR8_1YC2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0285 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_007307L_PINECR8_1Y-007309L_WIPOPA8_1YC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0285 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_007337L_KIMBRO8_1Y-170523E_BLACK_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0448 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_007389L_PINNAC8_1Y-135019TI_SOLAR_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1031 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_007389L_PINNAC8_1Y-135113ARAGORN_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0651 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008140JOSLIN4A-120263TREB_SLR_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0542 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008156CHARTER4A-163173BRIGHTSD_9C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0035 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008172VICTORIA4A-008174LPLDPOI4AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0285 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008172VICTORIA4A-110883VIC_SU5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0493 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008172VICTORIA4A-110884VIC_SU6C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0683 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008192PULSAR4A-008675TEXNAPOI4AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0405 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008209SHAKEPOI4A-162543MCLNSLR_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0671 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008266MARCONI4A-161601SANROMAN_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0177 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008318RIOHONDO7A-008573BONILLA7AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0023 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008318RIOHONDO7A-162745LMJDSW_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0824 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008319RIOHONDO4A-160750LV1_AB_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1297 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008380NEDIN4A-160234NEDIN_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1074 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008380NEDIN4A-160235NEDIN_2_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1075 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1751 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.01 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008458B_DAVIS4A-160105B_DAVIS_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1586 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008458B_DAVIS4A-160106B_DAVIS_2_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1753 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008458B_DAVIS4A-160107B_DAVIS_3_9C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0758 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008458B_DAVIS4A-160108B_DAVIS_4_9C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0758 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008574POMELO7A-161705MIRASOLE_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0203 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008579KATOEN7A-008606GODDARD7AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0029 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008601CEBOLLA7A-008902RIOHONDO7CC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008640KELVIN4A-088640CHLPAPOI4AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0543 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008656LUNA4A-088657VANCOPOI4AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0024 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008663ELSUZPOI7A-163415ELSAUZ_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.09 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008715RADIANT7A-008728COBRA7AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0484 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008728COBRA7A-081003HABER7AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0699 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008795ROMA_SW4A-088795STARRPOI4AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.041 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008963HEC4A-008981HECGT14AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0684 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008963HEC4A-008983HECST14AC3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0797 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008980FRONTERA4A-160180FRONT_EC_C1TC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0857 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008980FRONTERA4A-160181FRONT_EC_C2TC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0857 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008980FRONTERA4A-160182FRONT_EC_STTC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0902 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_008998MAXWELL4A-181754FERMI_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0002 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_009043CISTERN-009074LYTTON5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.002 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0193 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_011083RIVERTON_8-133342W_PECOS_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0259 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_011270DOGHOUSE_5-023876CLEARFRK_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_011270DOGHOUSE_5-134805PROSPERO_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1128 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_011270DOGHOUSE_5-135183PRSPERO2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0906 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_011273NELSON_8-134043BARROW3C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.001 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_011273NELSON_8-135503RDOSLR_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0677 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_011306DERMOTT_8-181953FLUVANNA_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0182 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_011319SCURCNTYS_8-183025CANYONWD_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.018 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_011406CENTBLUF_5-182255HOLSTN_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0687 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_011418TECUMSEH_5-151808VORTEX_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.037 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_011688THORNTRE_5-143625SAMSON_1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_011688THORNTRE_5-143705DELILA_1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_011735CEDARELM_5-143168WILDWIND_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0046 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_011809COPPERHD_8-143424PHOENIX_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0155 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_015200FORBESR1_5-068090SAMSWC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0063 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.012 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_017002GARVEYRD_5-150753TRINITY_1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0052 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_023863DRIVER_8-136234HUTT_SWC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0013 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_023900ALIBATES_5-140653GRANDVW1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0439 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_023900ALIBATES_5-141152RT66_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0038 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_023906AJSWOPE_5-140442SSPURTWO_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0348 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_023910WINDMILL_5-140753HRFDWIND_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.057 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_023910WINDMILL_5-141765MARIAH_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.016 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_023914TULECNYN_5-140853LHORN_NC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0118 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_023920ABERNATH_5-141607AEEC_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1982 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_023920ABERNATH_5-143902PALEO_ES_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_023922WHITERVR_5-141402SPLAIN2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0277 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_023922WHITERVR_5-141503COTWIND_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0123 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_023924FARMLAND_5-133641TAHOKAW_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0586 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_037450TNBUCKEYE_0-153082DILEOSLR_9C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0096 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_038021TNWORSHAM_1-136153RODEORNCH_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0159 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_038430TNWHITEBKR1-135592BRP_PAVO_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0044 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_038745TNATTWATER1-111971TOPAZ_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2024 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_040000CEDARP_B345A-110076CBY4_1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_040010CEDARP_B138A-049201GENGBY2_02_8CGL | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_040715GRNBYU_POI8B-049211GENGBY7_08_8CGL | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1477 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_041000LYDELL_POI_8-110664CHE_1_8C01 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0436 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_041000LYDELL_POI_8-110665CHE_2_8C04 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0665 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_042010P_H_R___B138-111131BAC_8C92 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1466 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_042110ANGLTN_POI_8-111535MYR_8C01 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1028 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_042110ANGLTN_POI_8-112597BCH_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1536 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_042400REFUGE_POI_5-111383PEY_CRK_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0258 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_042570ARCHER_POI_8-112969BTM_8C01 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.121 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_042875DANBUR_POI_8-112662LON_8C01 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0109 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_044000W_A_P__POI5A-049205GENWAP6_06_5CGL | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_044000W_A_P__POI5A-049206GENWAP7_07_5CGL | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_044005W_A_P__POI5B-049207GENWAP8_08_5CGL | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_044010W_A_P__POI8A-110021PNPI_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_044015W_A_P__POI8B-049212GENWAP3_03_8CGL | 138 | 22 | Branch MVA | 625 | - | - | - | 100.027 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_044060BLUE___POI_5-112043HOL_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1136 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_044070WHALEY_POI_5-112615ROW_5C01 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0945 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_044200HILLJE__B345-111637DANISH_5C01 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1753 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_044200HILLJE__B345-112147PLN_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0106 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_044650SMTHRS_POI_5-112419RABBS_5C01 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1594 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_044880WATERH_POI_5-112878GSTAR_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1666 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_044890SNUG___POI_8-113435COTBAYOU_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1085 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_045500T_H_W__POI_5-049204GENTHW5X05_5CGL | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1531 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_045515T_H_W__POI_8-049202GENTHW3X03_8CGL | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1469 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_045515T_H_W__POI_8-049203GENTHW4X04_8CGL | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1469 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_046020LIMEST_POI_5-068091NAVARROC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0033 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_047150H_O_C___B138-113105CALLISTO_8C01 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0015 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_047170H_O_C__POI_8-111183FEGC_8AC11 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0292 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_047170H_O_C__POI_8-111800PRO_8C01 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1621 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_059900LONG_DRAW-132114SRWE1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0274 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_059900LONG_DRAW-181553MESQCRK_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0066 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_059903BEARKAT-132993BEARKAT_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0268 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_059904COTTONWOOD-140903WAKE_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0215 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_059904COTTONWOOD-143692BRPDICKE_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0032 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_059906LONGDRAW_138-134145JUNO_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1109 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_059906LONGDRAW_138-134342LGDRAW_S8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0777 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_059907BERNOULLI-133442LACY_CRK_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0202 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_059909NOVA_138-059998NOVA8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.217 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_059909NOVA_138-143115NOVA1SLR_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1705 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_059909NOVA_138-144163NOVA2SLR_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0635 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_059911MHOS-183406JADE_HI_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1332 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_060011NEBULA7A-183525ANDMDSLR_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.115 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_060383LINTERNA4A-060385SOLSTICE4AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0278 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_060383LINTERNA4A-132331REROCK_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.051 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_060387HENDRICK4A-141663SOLARA_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0307 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_060393PIGCREEK4A-134245TAYGETE_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0987 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_060393PIGCREEK4A-134705TYGTEII_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0752 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_060423TREADWEL4A-170444CACTSFLT_T3C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_060451GARNET4A-182603NORTON_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0346 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_060464AZUREPOI7A-060514CLEARCRO7BC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0851 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_060500EDITHCLA7A-142563FOARDCITY_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0233 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_060504TESLA7B-142815MISAE_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0812 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_060506AVOGADRO7A-143473GRIF_TRL_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.008 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_060715FIGARO7A-182404WKNAMAD1C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0111 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_060722COULOMB7A-143015VERA_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0102 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_060728PALOUSE4A-135734APPALOSA_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0046 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_060791PERIGEE7A-143222APOGEE_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0295 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_061001JIMTREEC7A-140383BLSMT1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0375 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_068001CLAYTON_345-182455WHITHRSE_4_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0322 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_068008LATIMER-151265BAIRDWND_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0215 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_068011ASPIRE-151602ANCHOR_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0198 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_068051REATA-153433SHEEPCRK_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0145 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_068051REATA-153482RRWIND_345C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0109 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_068090SAMSW-068092LIBERTYC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0126 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_068092LIBERTY-152433MERCURY_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.007 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_071050L_BITTCR5_1Y-180161SWEETWN4_1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0441 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_076002L_BAKERS5_1Y-132732BOOTLEG_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0341 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_076002L_BAKERS5_1Y-133843WAYMARK_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0609 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_076002L_BAKERS5_1Y-135327REDBARN_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0909 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_076002L_BAKERS5_1Y-135602HYDRA_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0047 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_076003L_BIGHIL5_1Y-182203WL_RANCH5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.006 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_076004L_SINGTR5_1Y-136283SHAMROCK_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0092 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_076005L_SCHNDR5_1Y-132632SANTRITA_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.057 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_076005L_SCHNDR5_1Y-134651WHMESA_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0442 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_076006L_BOWWOO5_1Y-182051RTS_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0228 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_076015L_CEDACA5_1Y-134512HILO_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0572 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_076026L_SODALA8_1Y-135485CROSBAT_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0051 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_076040L_CASTIL8_1Y-132783CASL_GAP_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0621 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_076040L_CASTIL8_1Y-132943SPTX12B_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0539 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_076090L_DIVIDE5_1Y-180759CAPRIDG4_1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0587 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_076090L_DIVIDE5_1Y-182727AVIATOR_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0465 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_076601L_HORSCR8_1Y-182154EGROVESL_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0303 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_078255L_PINTCR8_1Y-183623ZIER_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0573 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_079000GRAY-079006ALN_CRKC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0075 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_079000GRAY-140473MIAMI_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0251 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_079005RAILHEAD-140503PH1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0142 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_079005RAILHEAD-140603PH2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.01 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_079604RAILROAD_DC-162963MADERO_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0051 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080013LARDVNTH4A-160009LARDVFTN_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.033 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080013LARDVNTH4A-160010LARDVFTN_2_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0314 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080071ZORILLO7A-080076AJO7AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080071ZORILLO7A-080171SARITA7AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1976 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080072STELPOI7A-080076AJO7AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0527 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080072STELPOI7A-161953STELLA_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0527 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080084VENDPOI4A-162456VENADO_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0061 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080171SARITA7A-160299BAFFIN_2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1976 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080210TORRPOI7A-161257TORCILAS_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0183 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080219LOBO7A-163223CORAZON_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0916 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080220CENIZO7A-161105BORDAS_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0365 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080224TIEMPO7A-162499RELOJ_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0071 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080227RAPIDO7A-161855CABEZONC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0115 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080231PRONTO7A-160885LV3_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.007 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080259PELICAN4A-160394COTTON_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0527 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080259PELICAN4A-160395PAP1_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0453 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080260GILA4A-160095NUECES_B_2_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0759 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080260GILA4A-160096NUECES_B_3_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0758 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080309LASPULGA4A-160694REDFISH_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0562 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080355DELSOL7A-080368LV4BRDG7AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0334 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080439LAQUINTA4A-160592CEDROHIL_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0095 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080503SANTASW4A-085001N_SHARPE4AC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0712 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080503SANTASW4A-161455CHAWIND_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0712 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_080509LADKPOI7A-161753BBREEZE_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0633 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_085008PATPOI7A-161653PATWIND_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0628 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_088173JCKSLPOI4A-163575JACKALOPE_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0509 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_088573ERAYPOI7A-162151EASTRAY_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0518 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_088574WRAYPOI7A-162695ELTRUENO_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0687 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_088606JRVKPOI7A-162005KNKWA1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0541 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_088607WLDRPOI7A-162053KNKWA2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0164 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_088624CRNLLPOI7A-162204CRANEL_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0097 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_088640CHLPAPOI4A-162253CHALUPA_138C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0544 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_088656ASTRSPOI4A-163023NEBULA_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0461 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_088657VANCOPOI4A-163123VANCOURT_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0024 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_088670BLACKPOI7A-162915BLACKJAK_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0658 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_088689FOXPOI7A-163477FOXTROT_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0151 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_131753PC_SOUTH_1_5-131754PC_SOUTH_2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0359 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_131753PC_SOUTH_1_5-131755PC2_SWYD_1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0508 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_131852NWF_1_8-131853NOTSW_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0041 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_132114SRWE1_5-132163SRWE1_A_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0011 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_132632SANTRITA_5-182355OVEJA_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.019 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_132993BEARKAT_5-133043BEARKAT_HC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0016 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_133641TAHOKAW_5-134543SAGEDRAWC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0218 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_136233PION_DJ_8-136234HUTT_SWC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0013 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_140383BLSMT1_5-142915BLSMTIII_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0046 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_140442SSPURTWO_5-140803SPURTRES_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0103 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_140753HRFDWIND_5-141053JRDWIND_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0264 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_141351ELECTRA_5-142962LOCKETT_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0033 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_143575SAMSON_3_5-143625SAMSON_1_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0584 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_143705DELILA_1_5-143757DELILA_2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1063 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_144365GOODNITE_5-144417GOODNIT2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0206 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_150313LNCRK2_1_8-150314LNCRK2_2_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0038 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_160298BAFFIN_5-160299BAFFIN_2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0526 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_160750LV1_AB_8-160751LV1_A_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0547 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_160750LV1_AB_8-160752LV1_B_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.055 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_161105BORDAS_5-161109BORDAS2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0053 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_162103MESTENO_5-162104CHARLYEG_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0072 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_170250PONY_4_8-180461HHOLLOW3_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0108 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_170262PONY_7_8-180459HHOLLOW2_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0034 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_180161SWEETWN4_1_5-180163SWEETWN5_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0143 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_180255BRAZ_WND_3_8-180256BRAZ_WND_CB1C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0004 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_180454BUFF_GAP_1_8-180455BUFF_GAP_2_8CS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0092 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_180752CAPRIDGE_1_8-180757CAPRIDGE_3_8CS1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0097 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_180754DIVIDE_1_8-180757CAPRIDGE_3_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0534 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_180755CAPRIDGE_2_8-180757CAPRIDGE_3_8CS2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0054 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_180955TKWSW_1_5-180956KIO_SWYD_2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.007 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_180958PYRON_1_5-180959KIO_SWYD_3_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0183 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_180961IND_1_5-180962KIO_SWYD_4_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0066 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_181853DERMOTT_H-182101COYOTE_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0104 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_182051RTS_5-182653RTS2_5_1C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0029 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_182404WKNAMAD1-182405WKNAMAD2C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0024 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_182727AVIATOR_5-182728DEWOLF_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0058 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_182777MAVCRK_W_5-182778E_MAVERICK_5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0081 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.0318 | 100.029 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_888847CARTWHEEL_POI-002464CASHSW_T5C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0035 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2168 | 100.0248 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_888856HOLLY_POI-059900LONG_DRAWC1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0144 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0083 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_888877GLASGOW_POI-068091NAVARROC1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0329 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L_888880DES_WILL_POI-001916LIGGETTA2_5C1 | 138 | 22 | Branch MVA | 625 | - | - | 100.0043 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L1000026 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0097 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L1000032 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0518 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L1000047 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0687 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L1000097 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10005-1B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0353 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10006-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0017 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10010060-1A-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.014 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10010061-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0036 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10010152 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.002 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10010434_MODIFIED_BY_MZ | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0647 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10010717 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0684 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10011200 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0025 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10011226 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.039 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10011585 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1977 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10011690 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0819 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10011910-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0803 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10012085 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0183 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10012087 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0628 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10012089 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0165 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10012091 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0541 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10012100 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0493 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10012105 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0683 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10012915 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0711 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L10012965 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0256 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L11000027 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0526 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L11000087 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0152 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L11000090 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0912 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L11000095 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0633 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L11000105 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0526 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L11000171 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0543 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L201000169 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1921 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L2020933-B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0022 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L2025527 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0082 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | L20255426 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1921 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | LAKE CREEK - RATTLE SNAKE 345 KV WITH SANDY UNIT (SINGLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | LCRA TSC_T21451 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0534 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | LCRA TSC_T21456 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0022 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | LCRA TSC_T21457 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0631 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | LCRA TSC_T255_TAE3121_1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1115 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | LCRA TSC_T451_T682 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0329 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | LCRA TSC_T464_1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0547 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | LCRATSC_6_EUCLID_JOHNDU | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0125 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | LEON_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0633 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 138 | 22 | Branch MVA | 625 | - | - | 100.096 | 100.0179 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.0084 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 138 | 22 | Branch MVA | 625 | - | - | 100.2168 | 100.0382 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1449 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.1262 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | LIMESTONE - OUTLAW / NAVARRO_5 (DOUBLE B TO B ) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0503 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0108 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | M10000271115801 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | M1000031210000064 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0024 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | M10000841000093-1A | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0064 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | M1101412110503-1_MODIFIED_BY_MZ | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0319 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | M115851115803 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | M128152129153 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0799 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MALDIVES_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0707 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2168 | 100.0692 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0834 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB100002711580 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB1000510007-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0397 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB1053110532 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2016 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB1111011014-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1114 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB1158011585 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB1291512815a | 138 | 22 | Branch MVA | 625 | - | - | - | 100.079 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB2084520840 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0306 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB2089320892 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0486 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB210140210145-AAAAA | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB210140210145-AAAAB | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB210140210145-AABA | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB210140210145-AABB | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1924 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB210140210145-ABAAA | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB210140210145-ABAAB | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB210140210145-ABABA | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB210140210145-ABABB | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB210140210145-ABBA | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1922 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB210140210145-BAAA-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0544 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB210140210145-BAAA-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0607 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB210140210145-BABA | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0516 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB2302523020 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0045 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MB2726627277 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1717 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0082 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1184 | 100.2168 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MITCHELL BEND-WOLF HOLLOW II UNIT 4 345 KV (SINGLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.165 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | 100.2154 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MOSES-SULPHUR SPRINGS SW 345-138 KV AUTO SULPHUR SPRINGS SW 345-138 KV AUTO #1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0034 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | MOSS - HOLT/YUCCA 138 KV/MIDLAND COUNTY NW SW 345 KV (DOUBLE B TO B) SUM 2025- FUTURE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0475 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | N5GSU2_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0694 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | NAVARRO-ASH CREEK 138 KV (SINGLE B TO B)-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0097 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | NAVARRO-ASH CREEK 138 KV (SINGLE B TO B)-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0097 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0327 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | NEW-HILLSBORO-CLEBURNE_SW_8 (SINGLE B TO B )-1-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0327 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | NEW-SAM - FOURBROTHERS/TRADINGHOUSE_5 (DOUBLE B TO B)-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.0851 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | NORTHWEST CARROLLTON - LEWISVILLE SW (BEPC) 345 KV (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | NORWOOD - WEST LEVEE 345 KV (SINGLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | ODESSA EHV - NORTH MCCAMEY 345 KV (SINGLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1697 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | OYSTER_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0883 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P_BTTLECRK_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0146 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_BTE_1_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1522 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_BTE_2_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1522 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_BTE_3_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1522 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_BVE_1_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1856 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_BVE_2_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1854 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_CAL_1_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0763 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_CBE_1_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0451 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_CBE_2_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0433 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_CBE_3_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0566 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_CBE_4_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0541 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_CBT_1_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_CBT_2_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_CBY_1_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1516 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_CBY_2_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1516 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_CHE_1_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1306 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_CHE_2_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1537 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_CHE_3_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1589 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_CVC_1_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1393 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_CVC_2_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1371 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_CVC_3_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1371 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_CVC_4_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1375 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_DIB_1_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0609 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_DIB_2_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0609 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_DIB_3_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0646 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_DPEC_1_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2089 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_DPEC_2_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2134 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_DPEC_3_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.209 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_DPEC_4_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2134 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_DPEC_5_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2011 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_FTR_1_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_FTR_2_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_FTR_3_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_BLY-CBT_C0_111143 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_BLY-CBT_C1_111141 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1437 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_BLY-CBT_C2_111142 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1467 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_CBY-CBY_C0_110075 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0698 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_CBY-CBY_C1_110073 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0617 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_CBY-CBY_C2_110074 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0617 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_CTR-DPEC_C0_110755 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.123 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_CTR-DPEC_C1_110751 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.066 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_CTR-DPEC_C2_110752 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.071 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_CTR-DPEC_C3_110753 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.066 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_CTR-DPEC_C4_110754 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.071 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_CTR-DPEC_C6_110761 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0576 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_DPW-CHE_C2_110663 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0666 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_DPW-CHE_C3_110668 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0717 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_DYN-CBE_C0_110793 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0131 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_DYN-CBE_C0_110796 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0231 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_DYN-CBE_C1_110791 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0121 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_DYN-CBE_C2_110792 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0103 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_DYN-CBE_C3_110794 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0132 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_DYN-CBE_C4_110795 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0107 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_JFS-PSG_C0_110623 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0665 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_JFS-PSG_C2_110621 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0635 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_JFS-PSG_C3_110622 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0635 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_RNS-FTR_C0_120094 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1883 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_RNS-FTR_C1_120091 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0633 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_RNS-FTR_C2_120092 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0633 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_RNS-FTR_C3_120093 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0633 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_SDN-CVC_C0_110824 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0531 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_SDN-CVC_C1_110821 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0657 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_SDN-CVC_C2_110822 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0635 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_SDN-CVC_C3_110823 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0635 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_SMR-BVE_C0_110773 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1102 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_SMR-BVE_C1_110771 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0553 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_SMR-BVE_C2_110772 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0551 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_THW_C0_110046 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0364 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_THW_C0_110051 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0364 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_THW_C1_110042 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0081 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_THW_C2_110043 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0081 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_THW_C3_110044 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0081 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_THW_C4_110045 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0081 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_THW_C5_110047 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0081 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_THW_C6_110048 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0081 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_THW_C7_110049 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0081 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_GEN_THW_C8_110050 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0081 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_PSA_1_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0691 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_PSA_2_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0696 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_PSA_3_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0701 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_PSA_4_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0704 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_PSA_5_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0698 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_PSA_6_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0692 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_PSG_1_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1509 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_PSG_2_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1509 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_THW_1_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0637 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_THW_2_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0637 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_THW_3_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0637 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_THW_4_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0637 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_THW_5_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0637 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_THW_6_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0637 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_THW_7_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0637 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-1_THW_8_COMBINED-CYCLE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0637 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(110125-110126-SG) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0022 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(110666-110667-BC) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0717 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(111182-111183-1) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0292 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(112330-112333-1) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.022 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(40015-49200-GL) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(40070-110975-1) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0536 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(40240-110756-01) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.123 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(40240-110757-02) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.066 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(40240-110758-03) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.071 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(40240-110759-04) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.066 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(40240-110760-05) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.071 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(40240-110762-01) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0576 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(40260-111263-NC) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0245 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(40270-112333-01) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.022 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(40390-113331-1) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0012 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(40450-110666-02) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1589 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(40600-120095-1) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(40690-113541-1) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0035 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(40890-113219-01) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1853 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(41100-110483-01) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0212 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(41100-110484-02) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0212 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(41240-110624-02) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0635 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(41240-110625-03) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0635 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(41240-110626-02) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0665 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(41430-110825-03) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1393 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(41430-110826-02) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0635 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(41430-110827-01) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0635 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(42985-110797-60) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(43020-113341-1) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0785 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(43035-113321-1) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0017 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(44010-49213-GL) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0076 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(44010-49214-GL) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0077 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(44015-49215-GL) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0689 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(44090-111865-1) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1467 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(44160-112495-1) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1152 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(44200-112261-1) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0162 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(44220-113251-1) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0775 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(44650-110774-1) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0553 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(44650-110775-2) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0551 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(44650-110776-1) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1102 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(46020-49208-GL) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(46020-49209-GL) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_(47430-113391-1) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0065 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P1-2_11.1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0048 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7/C5-SHRY-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.005 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7/C5-SHRY-3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0027 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1/C5-CTT-14 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0053 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1/C5-CTT-38 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0434 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>>JULIA | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0885 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>>T0202K-1-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>>T0202K-2-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0113 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>>T0404YYY | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1247 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>>T1827GX_ERC | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0465 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>>T1839X1_ERC | 138 | 22 | Branch MVA | 625 | - | - | - | 100.006 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>>T1839X2_ERC | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0116 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>>T2764Y_ERCa | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0121 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>>T3944Z_ERC | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0033 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>>T6060B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1474 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>>T7475B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>>T9797B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>>T9799A | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0011 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>>T9799D | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0117 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>>T9899A | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0007 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>LEG-OUTLAW_ERC | 138 | 22 | Branch MVA | 625 | - | - | 100.1187 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>T0202F-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0024 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | P7-1_E1>T6060F | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | PARIS NW-PARIS-PARIS SW138 KV (SINGLE B TO B) A | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0367 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | PARIS SW-MOSES 345 KV-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0078 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | PARIS SW-PACIFIC SW/VALLEY S SW 345 KV (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0262 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | PARKER-EAGLE MTN*HICKS 345 KV (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0101 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | PARKER-EAGLE MTN*HICKS 345 KV DCKT & EAGLE MOUNTAIN - WEATHERFORD 138 KV LINE | 138 | 22 | Branch MVA | 625 | - | - | 100.1978 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | PIN OAK - LONG LAKE 138 KV (SINGLE B TO B)-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.021 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | PIN OAK - LONG LAKE 138 KV (SINGLE B TO B)-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.021 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | PINEFOREST_CON | 138 | 22 | Branch MVA | 625 | - | - | 100.2059 | 100.1904 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | QUANT_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1419 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | R4U2A5C1_1_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (COMMON TOWER) | 138 | 22 | Branch MVA | 625 | - | - | 100.2111 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | RAMHORN - WILLOW CREEK DC 345 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0154 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0036 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | RAT_SNAKE-SNDY_CREEK_5 (SINGLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | RUBICONALPHA_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0147 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | RYBRN_P1-2_VINSON-LORING_2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0232 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | S_002411MTCK_W81 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | S_002421CHILSW_S81 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | S_002422CHILSW_N81 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | S_002481ELEVEE_W81 | 138 | 22 | Branch MVA | 625 | - | - | 100.1435 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | S_002482ELEVEE_E81 | 138 | 22 | Branch MVA | 625 | - | - | 100.1352 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0409 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0209 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.018 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 138 | 22 | Branch MVA | 625 | - | - | 100.1996 | 100.052 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | SAM_NAV_P7F1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0186 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | SAN_PAT_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | SAND LAKE - SOLSTICE 345 KV DCKT LINE (DOUBLE B TO B) WIN 2027 - FUTURE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0061 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | SCUR_CLY_P7 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0008 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 1 & SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0041 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | SEAGOVILLE SW - FORNEY/TRICORNER DCKT 345 KV (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | SKULLCREEK_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0365 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | SKYSLY_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1386 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | SOLACE_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1411 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10010 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0021 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10011 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0074 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10012 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0074 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10013 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0074 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10128 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0216 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10247 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0456 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10248 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0456 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10250 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0074 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10251 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0074 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10252 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0074 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10253 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0021 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10262 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2076 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10263 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0089 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10264 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0089 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10265 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0089 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10266 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0089 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10288 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0443 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10289 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0238 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10588 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0389 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10609 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.021 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_10614 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0166 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STECL_4720 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0246 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STONE CREEK SW-BONHAM SW 69 KV & VALLEY -COMMERCE 138 KV LINE A | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0162 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | STP - HOUDINI & STP - SHAULA | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0121 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | T_000981SPNCRINT69-000982DN_STEAM_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0506 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | T_059908NOVA_345-059998NOVA8CT1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.217 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | T_120545BOARDCRK_5-120544BOARDCRK_SUBCT3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0187 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | T_150315LNCRK2_1_5-150314LNCRK2_2_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0038 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | T_151856PRIDDY_5-151855PRIDDY_T1CT3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0183 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | T_162456VENADO_8-162455VENADO_MCT3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0061 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | T_180760DIVIDE_SC1-180754DIVIDE_1_8C1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0534 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | T200004 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0091 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0019 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0264 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | THRESLR_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.027 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | 100.1232 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | TIMBERVIEW-COMANCHE PEAK*CARMICHAEL BEND 345 KV (DOUBLE B TO B)-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0087 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | TIMBERVIEW-COMANCHE PEAK*DECORDOVA 345 KV (SINGLE B TO B)-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | 100.0637 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.035 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0153 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | TRI CORNER - SEAGOVILLE/FORNEY 345 KV DCKT (DOUBLE B TO B) A | 138 | 22 | Branch MVA | 625 | - | - | 100.0566 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | TRIFECTA_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | TRIN-RICH (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | 100.0924 | 100.0131 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | TRIN-SK*ME (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0324 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.1519 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | TR-TC1 (DOUBLE B TO B)_B | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0837 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0117 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | TWIN_OAK_BKR_8995_345_OAK_GROVE_SINGLE_B_T0_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | TWIN_OAK_BKR_9000_345_OAK_GROVE_SINGLE_B_T0_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | U2GSU56_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0372 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | U2GSU78_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0366 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | U3CT1_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0758 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | U3GSU1_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1866 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | U3GSU2_B | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0895 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | VALLEY S-ANNA SW 345 KV & VALLEY S-FARMERSVILLE 345 KV | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0114 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | VALLEY S-VALLEY SW 345 KV & VALLEY S-PARIS SW 345 KV | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0133 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | VALLEY SW-COMMERCE SW 138 KV BONHAM SW 138-69KV AUTO #1 A | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0232 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | 100.0427 | 100.0545 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 138 | 22 | Branch MVA | 625 | - | - | 100.2163 | 100.0028 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | 138 | 22 | Branch MVA | 625 | - | - | 100.1257 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0503 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | Venus SW - MillerRoad 345 KV (SINGLE B TO B) New Load | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0041 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 138 | 22 | Branch MVA | 625 | - | - | 100.028 | 100.0161 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.2167 | - | 100.0943 | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | 100.1696 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 138 | 22 | Branch MVA | 625 | - | - | 100.0547 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | VENUS-NAVARRO 345 KV (SINGLE B TO B)-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0084 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | VIKING_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1175 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | WAP - HOUDINI & STP - SHAULA | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0062 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 22 | Branch MVA | 625 | - | - | - | 100.002 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | WATERMILL-LOOP NINE 345 KV DCKT (DOUBLE B TO B) A | 138 | 22 | Branch MVA | 625 | - | - | 100.0178 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.1225 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0042 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 138 | 22 | Branch MVA | 625 | - | - | 100.2152 | 100.0031 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | WFCOGEN-PLEASANT VALLEY 138 KV & WFCOGEN-BOWMAN 138 KV | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0034 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | WHITERIVER-COTTONWOOD (DOUBLE B TO B)-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0058 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | WHITERIVER-COTTONWOOD (DOUBLE B TO B)-3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1059 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | WILLOW CREEK - HENDERSON RANCH 345 KV & WILLOW CREEK - JACKSBORO 345 KV (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0025 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | WINDMILL - AJSWOPE (SINGLE B TO B) SUM 2028 - FUTURE | 138 | 22 | Branch MVA | 625 | - | - | - | 100.188 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | WOLF HOLLOW-WOLF HOLLOW_C2_345 KV (SINGLE B TO B) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.11 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | WSHACK_LATIMER_P7 | 138 | 22 | Branch MVA | 625 | - | - | 100.0692 | - | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-CALFRESTN_5-4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0596 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-CALFRESTN_5-5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0596 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-CALFRESTN_5-6 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0721 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-CALPFREST_5-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0311 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-CALPFREST_5-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0311 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-CALPFREST_5-3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.027 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-COKFIELD1_5-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0013 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-DECORDOVA2_8-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0193 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-DECORDOVA2_8-3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0193 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-DECORDOVA2_8-4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0188 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-DECORDOVA2_8-5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0193 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-ENNSTRAC_8-1 | 138 | 22 | Branch MVA | 625 | - | - | 100.1322 | 100.1015 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-ENNSTRAC_8-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0486 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-FSCOGEN_8-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0237 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-FSCOGEN_8-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0237 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-GRHAMSES1_8-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1146 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-HANDLEYC_8-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2003 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-HANDLEYC_8-3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-HANDLEYD_8-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-LKHB_1T8-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2147 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-LKHB_2T8-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-MARTINLK_5-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-MARTINLK_5-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-MARTINLK_5-3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-MDLTHELP_5-5 | 138 | 22 | Branch MVA | 625 | - | - | 100.0318 | 100.1203 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-MDLTHELP_5-6 | 138 | 22 | Branch MVA | 625 | - | - | 100.0318 | 100.1214 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-MDLTHELP_N5-3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1232 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-MDLTHELP_N5-4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1232 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-MDLTHELP_S5-1 | 138 | 22 | Branch MVA | 625 | - | - | 100.0344 | 100.1135 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-MDLTHELP_S5-2 | 138 | 22 | Branch MVA | 625 | - | - | 100.0324 | 100.1226 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-MTCK_6T8-6 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.0544 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-MTCK_7T8-7 | 138 | 22 | Branch MVA | 625 | - | - | 100.2167 | 100.053 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-MTENTRPR_5G-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0605 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-MTENTRPR_5G-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0498 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-MTENTRPR_5G-3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.059 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-MTENTRPR_5G-4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1883 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-PBGENBUS_B-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0186 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-PBGENBUS_B-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0192 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-PBGENBUS_B-3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.018 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-PBGENBUS_B-4 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0186 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-PBGENBUS_B-5 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0186 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-SANDYCRK_5-01 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-STRYKER_8-2 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-STRYKERND_8-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0659 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-TENASKA_8-1_REVA (UNIT1) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.02 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-TENASKA_8-1_REVA (UNIT2) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.02 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-TENASKA_8-1_REVA (UNIT3) | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0216 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-WFCOG1_8-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.0032 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-WHCCS2_4-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.165 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-WHCCS2_5-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-WLFHMDPT_5-1 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.2167 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | XFMR-WLFHOSTR-3 | 138 | 22 | Branch MVA | 625 | - | - | - | 100.11 | - | - | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MCSES_UNIT8 (150023) -> MTCK_8T8 (12418) CKT 8 | YELLOW_WOLF_CON | 138 | 22 | Branch MVA | 625 | - | - | - | 100.1612 | - | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | MDFLDTP2A ( 8552) -> CLMVLTP2A ( 8556) CKT 1 | L_008102EL_CAMPO4A-008679ARROZ4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 103.3296 | - | -
TAEPTC,TAEPTN | COAST | COAST | COAST, COAST | MDFLDTP2A ( 8552) -> CLMVLTP2A ( 8556) CKT 1 | L10006-1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 102.2879 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTH_S_8 ( 2308) -> WAX_NW_8 ( 2309) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.9589 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTH_S_8 ( 2308) -> WAX_NW_8 ( 2309) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 109.2418 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTH_S_8 ( 2308) -> WAX_NW_8 ( 2309) CKT 1 | E_ETCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.411 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTH_S_8 ( 2308) -> WAX_NW_8 ( 2309) CKT 1 | L_000217GLNHEIGHTS-002424DESSW1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.4349 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTH_S_8 ( 2308) -> WAX_NW_8 ( 2309) CKT 1 | L_000220CEDARHILL-000223SAINTPAULC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3736 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTH_S_8 ( 2308) -> WAX_NW_8 ( 2309) CKT 1 | L_000223SAINTPAUL-000404JESSICAC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 113.3876 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTH_S_8 ( 2308) -> WAX_NW_8 ( 2309) CKT 1 | L_000404JESSICA-000419LILLIAN8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.7266 | 118.501 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTH_S_8 ( 2308) -> WAX_NW_8 ( 2309) CKT 1 | L_000432CONLEY-000436GRANDVIEWC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9804 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTH_S_8 ( 2308) -> WAX_NW_8 ( 2309) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 110.3139 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTH_S_8 ( 2308) -> WAX_NW_8 ( 2309) CKT 1 | L_002315WAX_PMP2_8-002319WAX_PMP1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4848 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTH_S_8 ( 2308) -> WAX_NW_8 ( 2309) CKT 1 | L_002315WAX_PMP2_8-002320WAX_N_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7847 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTH_S_8 ( 2308) -> WAX_NW_8 ( 2309) CKT 1 | L_002316MG_IND_T8-002319WAX_PMP1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5662 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTH_S_8 ( 2308) -> WAX_NW_8 ( 2309) CKT 1 | L_002320WAX_N_8-002321WAX_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.4262 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTH_S_8 ( 2308) -> WAX_NW_8 ( 2309) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 109.36 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTH_S_8 ( 2308) -> WAX_NW_8 ( 2309) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.5735 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTH_S_8 ( 2308) -> WAX_NW_8 ( 2309) CKT 1 | WAXAHACHI-WAXAHACHI OFC 69KV/ENNIS-STERRETT 138KV (DOUBLE B TO B) A REAGOR | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8801 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | 3WT_002431DESSW1_5_002424DESSW1_8_012431DESSW1_3 C 1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 101.218 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 863.0967 | - | - | - | 104.0967 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | BEPC_459 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 103.5165 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | CEDAR HILL - DESOTO/LOOP NINE 345 KV DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 103.1787 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 863.0967 | - | - | - | 100.0452 | 115.7935 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 863.0967 | - | - | - | 101.332 | 117.0022 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | CLEBURNE-KEMP RANCH 138 KV WITH RAILPORT (SINGLE B TO B) A | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 102.4985 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | E_ETCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 110.2313 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 104.3004 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | ENNIS WEST - STERRETT 138 KV (SINGLE B TO B) A REAGOR SPRINGS | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 104.2631 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | KEMP RANCH - CLEBURNE 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 102.4985 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | KEMP RANCH-ALVARADO-CLEBURNE 138 KV (SINGLE B TO B) A ALVARDO 138/69 TRANSFORMER | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 102.4985 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 106.1655 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 106.3727 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_000217GLNHEIGHTS-002237STERTRD_8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 102.2585 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_000217GLNHEIGHTS-002424DESSW1_8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 109.0892 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_000220CEDARHILL-000223SAINTPAULC1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | 102.6003 | 112.6065 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_000220CEDARHILL-000280LONGBRANCHC1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 105.4524 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_000223SAINTPAUL-000404JESSICAC1 | 138 | 138 | Branch Amp | 863.0967 | - | - | 100.6868 | 110.7814 | 123.9843 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_000404JESSICA-000419LILLIAN8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | 105.0906 | 115.4705 | 129.0837 | 102.4923 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_000419LILLIAN8-000439HIGHPOINTC1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 103.5889 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_000432CONLEY-000436GRANDVIEWC1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 109.4828 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_000432CONLEY-000439HIGHPOINTC1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 104.4236 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 101.4286 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 100.987 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | 101.1068 | 117.4972 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_002286PADERA_8-002310MDLTHTXI2_8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 104.7727 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_002286PADERA_8-002311MDLTH_N_T8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 101.7963 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_002289SOAPCRK_8-002303KEMPRNCH_8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 100.5478 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_002289SOAPCRK_8-002310MDLTHTXI2_8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 105.0282 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_002315WAX_PMP2_8-002319WAX_PMP1_8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 106.7024 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_002315WAX_PMP2_8-002320WAX_N_8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 107.0067 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_002316MG_IND_T8-002319WAX_PMP1_8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 105.7338 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_002320WAX_N_8-002321WAX_8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 113.8937 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | 100.1663 | 116.5156 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 104.7348 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 104.3065 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 104.293 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 104.9528 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 104.8526 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 106.199 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | SOAP CREEK - CEDAR HILL 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 102.7447 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | STERRETT 5400 - DESOTO (SINGLE B TO B) | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 102.1224 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 100.2397 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 102.1984 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 111.9285 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | Venus Switch- Cleburne 138 kV Line (SINGLE B TO B) new load | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 102.4985 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 101.9298 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | WAXAHACHI-WAXAHACHI OFC 69KV/ENNIS-STERRETT 138KV (DOUBLE B TO B) A REAGOR | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 106.1771 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 100.6824 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 101.905 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI1_8 ( 2307) -> NEWBRCH_8 (12307) CKT 1 | XFMR-ENNSTRAC_8-1 | 138 | 138 | Branch Amp | 863.0967 | - | - | - | - | 101.4119 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI2_8 ( 2310) -> PADERA_8 ( 2286) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2106 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MDLTHTXI2_8 ( 2310) -> PADERA_8 ( 2286) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7028 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | E_B_DAVIS_CC1_TRAIN | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 101.7887 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | E_INGLCOSW_CC1_TRAIN | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 104.4766 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | E_LGE_CC1_TRAIN | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 101.6101 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | E_NUECES_B_CC1_TRAIN | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 102.373 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | E5DVA1C1_1_B | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 108.0003 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | E5DVA1C1_1_B_1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 102.7732 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | E5DVA1C1_1_B_2 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 100.2817 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | L_008162COLETO4A-008172VICTORIA4AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 100.9534 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | L_008162COLETO4A-008172VICTORIA4AC2 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 101.8488 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | L_008410REFUGIO2A-008802HEARDTAP2AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 102.349 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | L_008412REFUGIO4A-008813QUINTANA4AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 101.2801 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | L_008416RINCON2A-008805BONIVIEW2AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 100.688 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 103.1067 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | L_008579KATOEN7A-008606GODDARD7AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 100.9799 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | L_008659NAISMITH7A-080039LUCERO7AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 106.1483 | - | 102.1555 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | L_008715RADIANT7A-008728COBRA7AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 104.7677 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | L_008728COBRA7A-081003HABER7AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 107.4009 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | L_008802HEARDTAP2A-008804WOODSBOR2AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 102.1495 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | L_008804WOODSBOR2A-008805BONIVIEW2AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 101.7049 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | L_008813QUINTANA4A-080065MELNCRK4AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 102.6484 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | L10010035 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 102.1195 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | L10011206 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 102.584 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | M100101100271-1A | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 105.1346 | - | 101.4514 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | M100101100271-1B | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 103.9267 | - | 100.2548 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | M128103100532 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 104.7078 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | M128104100523 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 103.7515 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | MB1001010027-1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 105.3217 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | MB1002710010-1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | - | 101.6777 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | MB1005212810 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 103.7145 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | MB1005312810 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 104.6705 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | MB1053110532 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 101.6085 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | SAN_PAT_CON | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 112.6736 | - | 105.185 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | MELNCRK4A (80065) -> RINCON4B ( 8437) CKT 1 | T_008410REFUGIO2A-008412REFUGIO4AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | 101.1953 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | MERR2A ( 6526) -> CASSAVA2A (60359) CKT 1 | L_006036YUCCA4A-006525ESMERALD4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 102.8126 | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | MERR2A ( 6526) -> CASSAVA2A (60359) CKT 1 | L_006036YUCCA4A-060360CASSAVA4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 102.8259 | - | -
TAEPTN | WEST | WEST | WEST, WEST | MERR2A ( 6526) -> CASSAVA2A (60359) CKT 1 | L_006648HARGROVE4A-060374PUMPJACK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 100.9251 | - | -
TAEPTN | WEST | WEST | WEST, WEST | MERR2A ( 6526) -> CASSAVA2A (60359) CKT 1 | L_006648HARGROVE4A-076011L_TWINBU8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 103.0049 | - | -
TAEPTN | WEST | WEST | WEST, WEST | MERR2A ( 6526) -> CASSAVA2A (60359) CKT 1 | LCRA TSC_T429_T9426 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 101.6786 | - | -
TAEPTN | WEST | WEST | WEST, WEST | MERR2A (6526) -> MERT2A (6529) CKT 1 | Pre-contingency | 69 | 69 | Amps | 317.961 | - | - | - | - | 107.9578 | - | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | BAS_RANCH_CON | 69 | 69 | Branch Amp | 317.961 | - | - | - | 103.3873 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | Cattleman-Longshore Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.859 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | G_136101BLUESKY_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 104.1354 | - | 104.0064 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | G_888839BAS_RANCH_POIUC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 103.2025 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_000844GPL_NEVILLSW-076000L_NORTMC5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6908 | - | 100.6182 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_006036YUCCA4A-006525ESMERALD4AC1 | 69 | 69 | Branch Amp | 317.961 | 112.247 | - | 141.2542 | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_006036YUCCA4A-060360CASSAVA4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 118.1745 | 135.9418 | - | 145.8182 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_006490SANTIAGO4A-006500LVOK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.1829 | - | 102.0594 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_006500LVOK4A-060412CARVER4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 106 | - | 105.5355 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_006517RUSSEKST4A-006535BIGLAKE4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 111.2987 | - | 109.8674 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_006517RUSSEKST4A-006559JERRY4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 113.4571 | - | 112.1985 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_006525ESMERALD4A-006562FDRAN4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 107.6095 | 123.0808 | - | 126.8449 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_006530BARNHRT2A-006534BIGLAKE2BC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 105.6537 | - | 106.1616 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_006535BIGLAKE4A-060375WOLFBERR2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.3788 | - | 101.7835 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_006536BIGLAKE4B-060414OWLS4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 105.7661 | - | 106.0557 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_006559JERRY4A-060374PUMPJACK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 102.4479 | 118.9456 | - | 117.8606 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_006562FDRAN4A-060412CARVER4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 104.1459 | - | 104.5801 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_006562FDRAN4A-136103BLUESKY_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 104.1948 | - | 104.0672 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_006648HARGROVE4A-060374PUMPJACK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 105.8662 | 123.8161 | - | 122.7509 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_006648HARGROVE4A-076011L_TWINBU8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 107.4721 | 126.0702 | - | 124.9995 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_060361SANTARIT4A-060414OWLS4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 116.2896 | - | 118.2902 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 117.634 | - | 119.7644 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_060723CROSSOVE4A-060728PALOUSE4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 108.9124 | - | 110.7319 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_060723CROSSOVE4A-076032L_NORTMC8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 108.9883 | - | 110.8348 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 119.2247 | - | 121.5271 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_076011L_TWINBU8_1Y-900117Other_90_SOC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 105.0901 | - | 104.972 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_076032L_NORTMC8_1Y-900113Other_81_SOC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.0322 | - | 101.4583 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L_900110Other_86_MO-900117Other_90_SOC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 103.5248 | - | 103.4155 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L2020925 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 111.7061 | - | 110.3311 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L2020933-B | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.9904 | - | 100.8841 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L2020944-A | 69 | 69 | Branch Amp | 317.961 | - | - | - | 117.5646 | - | 119.7034 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | L2020944-B | 69 | 69 | Branch Amp | 317.961 | - | - | - | 108.908 | - | 110.7269 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | LCRA TSC_BAKERS_CEDACA_DC | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.9064 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | LCRA TSC_T423_T551_A | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.504 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | LCRA TSC_T429_T9426 | 69 | 69 | Branch Amp | 317.961 | - | - | 106.6677 | 124.2252 | - | 123.1397 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE (DOUBLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.1938 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | MB2092520930 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 112.1759 | - | 110.9507 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | STECL_10592 | 69 | 69 | Branch Amp | 317.961 | - | - | 100.6916 | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | T_006535BIGLAKE4A-006536BIGLAKE4BC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 104.2904 | - | 104.6502 | -
TAEPTN | WEST | WEST | WEST, WEST | MERT2A ( 6529) -> MERR2A ( 6526) CKT 1 | T_060359CASSAVA2A-060360CASSAVA4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 104.5505 | - | 107.5852 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MEXIA_NO_9 ( 3614) -> MEXIA2_T_9 ( 3606) CKT 1 | L_003410LAKE_CRK1_8-003702RIESEL_8C1 | 69 | 69 | Branch Amp | 284.4914 | - | - | - | - | 113.2702 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MEXIA_NO_9 ( 3614) -> MEXIA2_T_9 ( 3606) CKT 1 | L_003597GROESBECP_8-888888FEWELL_S1C1 | 69 | 69 | Branch Amp | 284.4914 | 132.8013 | - | 137.2178 | 174.4094 | 294.1761 | 258.5959 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MEXIA_NO_9 ( 3614) -> MEXIA2_T_9 ( 3606) CKT 1 | LAKE CREEK-RATTLESNAKE/RIESEL_5_8 | 69 | 69 | Branch Amp | 284.4914 | - | - | - | - | 113.2714 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MEXIA_NO_9 ( 3614) -> MEXIA2_T_9 ( 3606) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 69 | 69 | Branch Amp | 284.4914 | - | - | - | - | 110.1288 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MEXIA2_1_8 ( 3632) -> MEXIA_NO_9 ( 3614) CKT 1 | L_003410LAKE_CRK1_8-003702RIESEL_8C1 | 138 | 69 | Branch MVA | 34 | - | - | - | - | 113.8496 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MEXIA2_1_8 ( 3632) -> MEXIA_NO_9 ( 3614) CKT 1 | L_003597GROESBECP_8-888888FEWELL_S1C1 | 138 | 69 | Branch MVA | 34 | 132.2023 | - | 136.6602 | 176.9144 | 297.0624 | 256.8294 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MEXIA2_1_8 ( 3632) -> MEXIA_NO_9 ( 3614) CKT 1 | LAKE CREEK-RATTLESNAKE/RIESEL_5_8 | 138 | 69 | Branch MVA | 34 | - | - | - | - | 113.8507 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MEXIA2_1_8 ( 3632) -> MEXIA_NO_9 ( 3614) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 138 | 69 | Branch MVA | 34 | - | - | - | - | 110.4082 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | MEXIA2_T_9 ( 3606) -> WORTHAM1_9 ( 3605) CKT 1 | L_003597GROESBECP_8-888888FEWELL_S1C1 | 69 | 69 | Branch Amp | 309.5936 | - | - | - | 132.0987 | 242.613 | 209.6893 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | MIDBASIN_9 ( 1228) -> SPRABERY_9 ( 1330) CKT 1 | T_001330SPRABERY_9-001329SPRABERY_8C1 | 69 | 69 | Branch Amp | 334.6958 | - | - | - | 112.5616 | 187.7691 | 187.2367 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MIDPOINT_POI (888889) -> BLUMPUMP1_8 ( 3518) CKT 1 | L_000442RAILPORT-001303FORBESRD_8C1 | 138 | 138 | Branch Amp | 779.8411 | - | - | 107.2447 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MIDPOINT_POI (888889) -> BLUMPUMP1_8 ( 3518) CKT 1 | L_000442RAILPORT-001908VENUSC1 | 138 | 138 | Branch Amp | 779.8411 | - | - | 107.9053 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MIDPOINT_POI (888889) -> BLUMPUMP1_8 ( 3518) CKT 1 | L_002280CLEBRN_N_8-002283AIRLIQD_P8C1 | 138 | 138 | Branch Amp | 779.8411 | - | - | 102.2274 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MIDPOINT_POI (888889) -> BLUMPUMP1_8 ( 3518) CKT 1 | L_002281GODLEY_8-002283AIRLIQD_P8C1 | 138 | 138 | Branch Amp | 779.8411 | - | - | 103.9075 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MIDPOINT_POI (888889) -> BLUMPUMP1_8 ( 3518) CKT 1 | L_002281GODLEY_8-002888CARMICHL_8C1 | 138 | 138 | Branch Amp | 779.8411 | - | - | 103.9568 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MIDPOINT_POI (888889) -> BLUMPUMP1_8 ( 3518) CKT 1 | NEW-SAM - FOURBROTHERS/TRADINGHOUSE_5 (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 779.8411 | - | - | 100.7692 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MIDPOINT_POI (888889) -> BLUMPUMP1_8 ( 3518) CKT 1 | NEW-SAM - FOURBROTHERS/TRADINGHOUSE_5 (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 779.8411 | - | - | 101.0942 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MIDPOINT_POI (888889) -> BLUMPUMP1_8 ( 3518) CKT 1 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 138 | 138 | Branch Amp | 779.8411 | - | - | 102.3103 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MIDPOINT_POI (888889) -> BLUMPUMP1_8 ( 3518) CKT 1 | TRADINGHOUSE - SAM/FOURBROTHERS SWITCH_5 (DOUBLE B TO B)_MODIFIED_BY_MZ | 138 | 138 | Branch Amp | 779.8411 | - | - | 101.1426 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MIDPOINT_POI (888889) -> BLUMPUMP1_8 ( 3518) CKT 1 | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | 138 | 138 | Branch Amp | 779.8411 | - | - | 101.9347 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MIDPOINT_POI (888889) -> BLUMPUMP1_8 ( 3518) CKT 1 | VENUS-JOHNSON 345KV/DECORDOVA-CLEBURNE 138KV (DOUBLE B TO B) new load | 138 | 138 | Branch Amp | 779.8411 | - | - | 103.2359 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MIDPOINT_POI (888889) -> BLUMPUMP1_8 (3518) CKT 1 | Pre-contingency | 138 | 138 | Amps | 779.8411 | - | - | - | 115.1488 | 128.9922 | 119.0539 | -
TCNPE | COAST | COAST | COAST, COAST | MIDTWN_RCTR1 (47707) -> POLK___B138B (47731) CKT 90 | L_047707MIDTWN_RCTR1-047709MIDTWN90LR8ACR1 | 138 | 138 | Branch Amp | 1476.8451 | 115.9471 | - | - | - | - | - | -
TCNPE | COAST | COAST | COAST, COAST | MIDTWN_RCTR1 (47707) -> POLK___B138B (47731) CKT 90 | L_047709MIDTWN90LR8A-047731POLK___B138BC90 | 138 | 138 | Branch Amp | 1476.8451 | 115.8341 | - | - | - | - | - | -
TCNPE | COAST | COAST | COAST, COAST | MIDTWN90LR8A (47709) -> POLK___B138B (47731) CKT 90 | L_047707MIDTWN_RCTR1-047731POLK___B138BC90 | 138 | 138 | Branch Amp | 1158.8842 | 144.9712 | - | - | - | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | MILANO ( 64) -> MINERVA1_8 ( 3683) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 118.2534 | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | MILANO ( 64) -> MINERVA1_8 ( 3683) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 113.2785 | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | MILANO ( 64) -> MINERVA1_8 ( 3683) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 107.8539 | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | MILANO ( 64) -> MINERVA1_8 ( 3683) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.4988 | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | MILANO (64) -> CANNON_8 (3707) CKT 1 | Pre-contingency | 138 | 138 | Amps | 895.3112 | - | - | - | - | 122.6521 | 122.0472 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | MILANO (64) -> MINERVA1_8 (3683) CKT 1 | Pre-contingency | 138 | 138 | Amps | 861.8416 | - | - | - | - | 126.3179 | 125.6838 | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MILLER ( 824) -> NEWMAN8 ( 849) CKT 1 | L_000827BRAND-000968BENDAVIS_8C1 | 138 | 138 | Branch Amp | 983.1688 | - | - | - | 101.7644 | 102.8036 | 102.7414 | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MILLER ( 824) -> NEWMAN8 ( 849) CKT 1 | L_000830SHILOH-000834MCCREE8C1 | 138 | 138 | Branch Amp | 983.1688 | 100.2873 | - | 115.0944 | 114.2326 | 115.4844 | 118.7066 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MITCHBND2_5 ( 1895) -> CARMICHL_5 ( 2285) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-1 | 345 | 345 | Branch Amp | 3198.0183 | - | - | - | 104.0464 | 101.7332 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MITCHBND2_5 ( 1895) -> CARMICHL_5 ( 2285) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-2 | 345 | 345 | Branch Amp | 3198.0183 | - | - | - | 108.7316 | 106.6442 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MITCHBND2_5 ( 1895) -> CARMICHL_5 ( 2285) CKT 1 | COMANCHE PEAK-JOHNSON*TIMBERVIEW 345 KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 3198.0183 | - | - | 104.5485 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MITCHBND2_5 ( 1895) -> CARMICHL_5 ( 2285) CKT 1 | L_001880ROCKYCRK_5-888879BLUBIRD_POIC1 | 345 | 345 | Branch Amp | 3198.0183 | - | - | - | 103.2912 | 102.3995 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MITCHBND2_5 ( 1895) -> CARMICHL_5 ( 2285) CKT 1 | PARKER-COMANCHE PEAK 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 3198.0183 | - | - | - | - | 100.3249 | - | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | ALLEN SW - MONTICELLO 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 110.4577 | - | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.1272 | 119.4238 | 105.278 | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 111.5865 | - | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.6489 | 121.0493 | 105.9838 | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 108.0183 | - | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 117.005 | 102.6154 | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | ALLEN-MOSES 345-138 AUTO-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 113.9548 | - | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | ALLEN-MOSES 345-138 AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 105.1094 | 123.2371 | 108.5112 | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 114.7163 | 131.0175 | 114.0507 | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | L_001685FARMVLSW_5-011689CYCLONE_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 113.2059 | - | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | L_001685FARMVLSW_5-011700SALTILLO_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.3972 | - | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 110.4577 | - | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.0298 | 119.2823 | 105.2191 | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | L_001696MOSES1_T5-888854PINEFOREST_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 110.4577 | - | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | L_011684BRIGHTR_5-011688THORNTRE_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.7916 | - | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | L_011684BRIGHTR_5-011689CYCLONE_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.4041 | - | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | L_011688THORNTRE_5-011700SALTILLO_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.2462 | - | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.0298 | 119.2823 | 105.2191 | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | PARIS SW-PACIFIC SW/VALLEY S SW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 111.4558 | - | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | PINEFOREST_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 110.83 | - | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 129.0374 | 153.2502 | 130.142 | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 121.5779 | 145.6682 | 123.0496 | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_5 ( 1695) -> SULSP_SS1_5 ( 1697) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.8494 | 118.7098 | 103.3151 | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_T8 ( 1794) -> SULBLF1_8 ( 1796) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 120.1435 | 137.3966 | 120.8112 | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_T8 ( 1794) -> SULBLF1_8 ( 1796) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 138 | 138 | Branch Amp | 748.8818 | - | - | 103.5724 | 129.5689 | 147.36 | 129.2751 | -
TONCOR | EAST | EAST | EAST, EAST | MOSES_T8 ( 1794) -> SULBLF1_8 ( 1796) CKT 1 | L_001695MOSES_5-001697SULSP_SS1_5C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 110.9433 | - | -
TONCOR | EAST | EAST | EAST, EAST | MOSES1_T5 ( 1696) -> PINEFOREST_POI (888854) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.7488 | - | -
TONCOR | EAST | EAST | EAST, EAST | MOSES1_T5 ( 1696) -> PINEFOREST_POI (888854) CKT 1 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.2918 | - | -
TONCOR | EAST | EAST | EAST, EAST | MRTNSPG1_8 ( 1800) -> SULSP_SS1_8 ( 1698) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 106.3035 | - | -
TONCOR | EAST | EAST | EAST, EAST | MRTNSPG1_8 ( 1800) -> SULSP_SS1_8 ( 1698) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 116.3679 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MSQT1_8 ( 2775) -> BCHSPG1T_8 ( 2776) CKT 1 | 3WT_002433SGVLSW1_5_002434SGVLSW1_8_012434SGVLSW1_3 C 2 | 138 | 138 | Branch Amp | 1499.8555 | - | - | - | - | 101.33 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MSQT1_8 ( 2775) -> BCHSPG1T_8 ( 2776) CKT 1 | SEAGOVILLE SW - FORNEY/TRICORNER DCKT 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1499.8555 | - | - | - | - | 102.2463 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MSQTE1_8 ( 2756) -> ESIDE2T_8 ( 2771) CKT 1 | 3WT_002433SGVLSW1_5_002434SGVLSW1_8_012434SGVLSW1_3 C 2 | 138 | 138 | Branch Amp | 1499.8555 | - | - | - | 108.477 | 116.6259 | 103.9268 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MSQTE1_8 ( 2756) -> ESIDE2T_8 ( 2771) CKT 1 | SEAGOVILLE SW - FORNEY/TRICORNER DCKT 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1499.8555 | - | - | - | 109.619 | 117.553 | 103.7931 | -
RMOUNT | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | MTCK_8T8 (12418) -> MCSES_UNIT8 (150023) CKT 8 | Pre-contingency | 138 | 22 | MVA | 625 | - | - | - | - | 100.2167 | - | -
TONCOR | EAST | EAST | EAST, EAST | MTENTRPR_5 ( 3116) -> TRINDAD2_5 ( 3124) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.6828 | 109.4463 | 105.7004 | -
TONCOR | EAST | EAST | EAST, EAST | MTENTRPR_5 ( 3116) -> TRINDAD2_5 ( 3124) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 106.9289 | - | 109.8365 | -
TONCOR | EAST | EAST | EAST, EAST | MTENTRPR_5 ( 3116) -> TRINDAD2_5 ( 3124) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.0015 | - | -
TONCOR | EAST | EAST | EAST, EAST | MTENTRPR_5 ( 3116) -> TRINDAD2_5 ( 3124) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.6225 | - | -
TONCOR | EAST | EAST | EAST, EAST | MTENTRPR_5 ( 3116) -> TRINDAD2_5 ( 3124) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.2563 | 107.2075 | 102.9112 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | N_SHARPE7A (85000) -> N_SHARPE4A (85001) CKT 1 | L_008458B_DAVIS4A-085010CARVL4AC1 | 345 | 138 | Branch MVA | 405 | - | - | - | 147.5969 | 143.2569 | 151.095 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | NATDAM_8 (23836) -> HOWD2599_8 (11325) CKT 1 | BIG SPRING WEST SWITCH - BIG SPRING 138 KV WIN 2025 - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 1648.3767 | 104.4281 | - | - | - | 100.3838 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | NATDAM_8 (23836) -> HOWD2599_8 (11325) CKT 1 | L_001322BIGSPRIG_8-010044STEER_8C1 | 138 | 138 | Branch Amp | 1648.3767 | 115.4146 | 101.9674 | 106.4531 | 107.5507 | 111.1157 | 108.0689 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | NATDAM_8 (23836) -> HOWD2599_8 (11325) CKT 1 | L_010044STEER_8-011316BSPGWSW_8C1 | 138 | 138 | Branch Amp | 1648.3767 | 115.4138 | 101.9676 | 106.4526 | 107.5508 | 111.115 | 108.0688 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 100.0811 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 125.8254 | - | 116.1744 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 107.0826 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.653 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | GLASGOW_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 122.2138 | - | 112.7272 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | L_001906VENUS_S5-888857OYSTER_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.39 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | L_001907VENUS_N5-068091NAVARROC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.566 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 125.8254 | - | 116.1744 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 103.4044 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.2618 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 123.6602 | - | 114.3834 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.2596 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 119.9713 | - | 111.2282 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | OYSTER_CON | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1874 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | RICH-BBROWN (DOUBLE B TO B)A | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.8231 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.3283 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 109.6514 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 111.2635 | - | 103.9031 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 116.8003 | - | 107.2405 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.1749 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.4689 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.3356 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 114.0554 | - | 112.7016 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 110.3831 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | VENUS-NAVARRO 345 KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 111.5544 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 124.3441 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> ELROD_5 ( 3159) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 100.0686 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> GLASGOW_POI (888877) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 102.2876 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> GLASGOW_POI (888877) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 101.8708 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> GLASGOW_POI (888877) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 118.8609 | - | 110.1501 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> GLASGOW_POI (888877) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 118.8609 | - | 110.1501 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> GLASGOW_POI (888877) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 116.6706 | - | 108.4212 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> GLASGOW_POI (888877) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 105.5816 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> GLASGOW_POI (888877) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.6761 | - | 100.0099 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> GLASGOW_POI (888877) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 112.1467 | - | 103.3571 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> GLASGOW_POI (888877) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 109.483 | - | 108.8098 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> GLASGOW_POI (888877) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 106.4782 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> GLASGOW_POI (888877) CKT 1 | VENUS-NAVARRO 345 KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 106.9619 | - | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> GLASGOW_POI (888877) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | 119.4963 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> OYSTER_POI (888857) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 129.1123 | - | 132.2887 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> OYSTER_POI (888857) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 118.1328 | - | 123.2363 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> OYSTER_POI (888857) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 108.1826 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> OYSTER_POI (888857) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.0166 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> OYSTER_POI (888857) CKT 1 | GLASGOW_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.6838 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> OYSTER_POI (888857) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 108.1826 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> OYSTER_POI (888857) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.0166 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> OYSTER_POI (888857) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.3643 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> OYSTER_POI (888857) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.3407 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> OYSTER_POI (888857) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.0953 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> OYSTER_POI (888857) CKT 1 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.085 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> OYSTER_POI (888857) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.3616 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> OYSTER_POI (888857) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1168 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> OYSTER_POI (888857) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.4101 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | BAS_RANCH_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.0491 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 140.1028 | - | 149.8008 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 129.0872 | - | 141.1875 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 115.3417 | 110.2287 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 113.737 | 108.1759 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.7584 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 123.6187 | 112.0014 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | BLUBIRD_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.974 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 111.4231 | 105.9038 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.5377 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.2429 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | E_WCPP_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.3099 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | E_WHCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.5667 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | E_WHCCS2_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.202 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 121.459 | 110.3827 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | G_150111CPSES_UNIT1UU1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.2475 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | G_150112CPSES_UNIT2UU2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.3231 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | G_888839BAS_RANCH_POIUC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.0544 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | G_888879BLUBIRD_POIUS1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.0993 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | GLASGOW_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 119.982 | 108.4036 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.4826 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_001902JHNSONSW_P5-015106LILLIAN1C_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.3149 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.3445 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_001906VENUS_S5-888857OYSTER_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 114.2547 | 107.2403 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.0969 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_001907VENUS_N5-015200FORBESR1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 112.1852 | 102.3833 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 123.6187 | 112.0014 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 121.459 | 110.3827 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.7643 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.8884 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 121.7624 | 110.6498 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.9828 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.8847 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 119.6948 | 108.9115 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_003384STJOHNS_5-003409LAKE_CRK1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.047 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_003384STJOHNS_5-003711BALE_S5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.6179 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.875 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.0591 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 118.042 | 107.0681 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_888857OYSTER_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 110.6762 | 104.0529 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 118.6398 | 108.0428 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | LAKE CREEK - LAKE HALL/TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.196 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | LAKE CREEK-RATTLESNAKE/ST JOHNS_5 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.0481 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | LATIMER_REATA_P7F1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.3099 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 108.2805 | 103.3208 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.8453 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.3364 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.9754 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.8068 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | OYSTER_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 112.6408 | 105.0367 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | RICH-BBROWN (DOUBLE B TO B)A | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.8507 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 114.079 | 101.2593 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 111.9004 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | - | 110.049 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.7031 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.8785 | 101.2171 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 108.5823 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.6891 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 120.5161 | 106.4703 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5162 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.0129 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | - | 108.0477 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.1854 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.0279 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.3631 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | - | 109.6149 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 110.4275 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | VENUS-SAM SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 111.9786 | 102.2799 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.3102 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | WSHACK_LATIMER_P7 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.9506 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO (68091) -> VENUS_N5 ( 1907) CKT 1 | XFMR-WHCCS2_5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.9685 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NAVARRO1_9 ( 3479) -> RICHLAND1_9 ( 3486) CKT 1 | L_003632MEXIA2_1_8-003634GROES_SE1_8C1 | 69 | 69 | Branch Amp | 292.8588 | 153.6877 | - | 153.7105 | 153.5298 | 152.3586 | 153.158 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NEWBRCH_8 (12307) -> MDLTH_S_8 ( 2308) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 106.552 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NEWBRCH_8 (12307) -> MDLTH_S_8 ( 2308) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 107.7385 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NEWBRCH_8 (12307) -> MDLTH_S_8 ( 2308) CKT 1 | E_ETCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 101.2651 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NEWBRCH_8 (12307) -> MDLTH_S_8 ( 2308) CKT 1 | L_000217GLNHEIGHTS-002424DESSW1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.2601 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NEWBRCH_8 (12307) -> MDLTH_S_8 ( 2308) CKT 1 | L_000220CEDARHILL-000223SAINTPAULC1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 103.6085 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NEWBRCH_8 (12307) -> MDLTH_S_8 ( 2308) CKT 1 | L_000223SAINTPAUL-000404JESSICAC1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 101.9404 | 114.6019 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NEWBRCH_8 (12307) -> MDLTH_S_8 ( 2308) CKT 1 | L_000404JESSICA-000419LILLIAN8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 106.4365 | 119.5035 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NEWBRCH_8 (12307) -> MDLTH_S_8 ( 2308) CKT 1 | L_000432CONLEY-000436GRANDVIEWC1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.6003 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NEWBRCH_8 (12307) -> MDLTH_S_8 ( 2308) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 108.2816 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NEWBRCH_8 (12307) -> MDLTH_S_8 ( 2308) CKT 1 | L_002320WAX_N_8-002321WAX_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 104.8123 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NEWBRCH_8 (12307) -> MDLTH_S_8 ( 2308) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 107.3381 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NEWBRCH_8 (12307) -> MDLTH_S_8 ( 2308) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 102.8944 | - | -
TCNPE | COAST | COAST | COAST, COAST | NEWGLF_S60_8 (43010) -> S_LANE__B138 (43190) CKT 60 | L_043090PYTHIA_POI_8-043110SANBER_POI_8C60 | 138 | 138 | Branch Amp | 2196.4409 | - | - | - | - | 104.7251 | - | -
TCNPE | COAST | COAST | COAST, COAST | NEWGLF_S60_8 (43010) -> S_LANE__B138 (43190) CKT 60 | L_043090PYTHIA_POI_8-043380W_COL__POI_8C60 | 138 | 138 | Branch Amp | 2196.4409 | - | - | - | - | 118.5432 | - | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NEWMAN8 ( 849) -> WALNUT ( 823) CKT 1 | L_000830SHILOH-000834MCCREE8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 101.0143 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | 3WT_002433SGVLSW1_5_002434SGVLSW1_8_012434SGVLSW1_3 C 2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 101.6396 | - | 102.9738 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 110.4198 | - | 105.5324 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 106.4323 | - | 103.9703 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 100.6698 | - | 102.8377 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 105.2747 | - | 106.5687 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | G_151371LILY_S1US1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 104.7332 | - | 105.9535 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 105.2749 | - | 106.4413 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 105.4306 | - | 106.5871 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 104.2059 | - | 105.5356 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 103.9106 | - | 105.2605 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 122.6048 | - | 123.5072 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | - | 101.6459 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | L_006903BOZE-151372LILY_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 105.5812 | - | 106.8191 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 100.6504 | - | 100.7415 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 101.59 | - | 101.6015 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 102.3906 | - | 102.79 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 103.3572 | - | 104.8365 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 109.1183 | - | 110.2238 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | SEAGOVILLE SW - FORNEY/TRICORNER DCKT 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 101.3184 | - | 103.0574 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 101.645 | - | 101.8576 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 100.734 | - | 101.6013 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | - | 100.6884 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 102.101 | - | 102.7665 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 103.3298 | - | 103.6982 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 ( 3260) -> MANKIN_8 ( 3265) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 138 | 138 | Branch Amp | 1008.2711 | - | - | 102.2006 | 136.2118 | - | 133.876 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NIPAKTAP_8 (3260) -> MANKIN_8 (3265) CKT 1 | Pre-contingency | 138 | 138 | Amps | 1008.271 | - | - | - | - | 105.0429 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NOLANVIL1_8 ( 3617) -> HARK_HTS1_8 ( 3618) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 117.5313 | - | -
TONCOR | NORTH | NORTH | NORTH, NORTH | NORTHGATE_8 (12679) -> HAGGRTY_8 (12677) CKT 1 | L_001839STONCRK_8-012677HAGGRTY_8C1 | 138 | 138 | Branch Amp | 1363.8853 | - | - | - | 101.4816 | 106.4392 | 103.1437 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | NORWD1_5 ( 2406) -> TOPEKA1_5 (12398) CKT 1 | GreenRD Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 103.3442 | - | -
TWETR | NORTH | NORTH | NORTH, NORTH | NOVA_138 (59909) -> NOVA8 (59998) CKT 1 | E_DDPEC_CC1_TRAIN | 138 | 138 | Branch Amp | 1614.9071 | - | - | 100.0189 | - | - | - | -
TWETR | NORTH | NORTH | NORTH, NORTH | NOVA_138 (59909) -> NOVA8 (59998) CKT 1 | E_WHCCS2_CC2_TRAIN | 138 | 138 | Branch Amp | 1614.9071 | - | - | 100.0535 | - | - | - | -
TWETR | NORTH | NORTH | NORTH, NORTH | NOVA_138 (59909) -> NOVA8 (59998) CKT 1 | G_110351STP_STP_G1UU1 | 138 | 138 | Branch Amp | 1614.9071 | - | - | 100.1248 | - | - | - | -
TWETR | NORTH | NORTH | NORTH, NORTH | NOVA_138 (59909) -> NOVA8 (59998) CKT 1 | G_110352STP_STP_G2UU2 | 138 | 138 | Branch Amp | 1614.9071 | - | - | 100.113 | - | - | - | -
TWETR | NORTH | NORTH | NORTH, NORTH | NOVA_138 (59909) -> NOVA8 (59998) CKT 1 | G_150111CPSES_UNIT1UU1 | 138 | 138 | Branch Amp | 1614.9071 | - | - | 100.1547 | - | - | - | -
TWETR | NORTH | NORTH | NORTH, NORTH | NOVA_138 (59909) -> NOVA8 (59998) CKT 1 | G_150112CPSES_UNIT2UU2 | 138 | 138 | Branch Amp | 1614.9071 | - | - | 100.1433 | - | - | - | -
TWETR | NORTH | NORTH | NORTH, NORTH | NOVA_138 (59909) -> NOVA8 (59998) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 138 | 138 | Branch Amp | 1614.9071 | - | - | 100.1335 | - | - | - | -
TWETR | NORTH | NORTH | NORTH, NORTH | NOVA_138 (59909) -> NOVA8 (59998) CKT 1 | P7-1_E1>>T9797B | 138 | 138 | Branch Amp | 1614.9071 | - | - | 100.0189 | - | - | - | -
TWETR | NORTH | NORTH | NORTH, NORTH | NOVA_138 (59909) -> NOVA8 (59998) CKT 1 | Pre-contingency | 138 | 138 | Amps | 1614.9071 | - | - | - | 124.6295 | 125.1584 | 123.6318 | -
TWETR | NORTH | NORTH | NORTH, NORTH | NOVA_138 (59909) -> NOVA8 (59998) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1614.9071 | - | - | 100.4263 | - | - | - | -
TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | OCONNER2A ( 8591) -> GRETA2A ( 8409) CKT 1 | L_008144SEADRFTC4A-008189TUNGSTEN4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 107.9431 | 150.6901 | - | -
TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | OCONNER2A ( 8591) -> GRETA2A ( 8409) CKT 1 | L_008144SEADRFTC4A-080065MELNCRK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 107.6687 | 150.399 | - | -
TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | OCONNER2A ( 8591) -> GRETA2A ( 8409) CKT 1 | L_008412REFUGIO4A-008813QUINTANA4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 115.4486 | - | -
TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | OCONNER2A ( 8591) -> GRETA2A ( 8409) CKT 1 | L_008813QUINTANA4A-080065MELNCRK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 119.3827 | - | -
TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | OCONNER2A ( 8591) -> GRETA2A ( 8409) CKT 1 | L10011206 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 115.435 | - | -
TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | OCONNER2A ( 8591) -> GRETA2A ( 8409) CKT 1 | MB1291012930 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 143.4966 | - | -
TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | OCONNER2A ( 8591) -> GRETA2A ( 8409) CKT 1 | MB1293012910 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 107.3944 | - | - | -
TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | OCONNER2A ( 8591) -> GRETA2A ( 8409) CKT 1 | T_008410REFUGIO2A-008412REFUGIO4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 115.3062 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | ODESEHV_8 ( 1027) -> REITER_8 (18545) CKT 1 | REITER - ODESSA EHV 345 KV 2026 SUM - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 878.5764 | - | 108.5724 | - | - | - | - | -
RLAFRO | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | OECCS_2_5 (130328) -> OECCS_CT22 (130325) CKT 4 | E_OECCS_CC2_TRAIN | 345 | 18.1 | Branch MVA | 210 | 104.134 | 104.1858 | 104.1542 | 104.1864 | 104.2345 | 104.1116 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 100.5852 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 106.2902 | - | 105.2654 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 103.5105 | - | 104.2373 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 101.049 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 100.3568 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 100.4162 | - | 103.962 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | CORS-NAV_8 (SINGLE B TO B ) | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 102.3613 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | CORS-TRINIDAD_9 (SINGLE B TO B ) | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 100.4392 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | E_ETCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 108.1325 | - | 109.3679 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | G_003478NAVARRO1_8US1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 100.3596 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_000200CHATFIELD-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | 100.9298 | 122.4532 | - | 125.6052 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_000200CHATFIELD-003455CORS1_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | 106.5948 | 127.7903 | - | 130.6951 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 100.2169 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 100.2169 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 114.9679 | - | 117.8293 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_002726KEMP_S_8-002774KNGCRK_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 100.3563 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_002726KEMP_S_8-003264SEVENPTS_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 100.9147 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003127TRINIDAD_8-003260NIPAKTAP_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 101.9609 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003127TRINIDAD_8-003466KERENS_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 103.2093 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003260NIPAKTAP_8-003265MANKIN_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 101.9498 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003262CEDRCREK_8-003263CEDRCKPU_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 101.6972 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003262CEDRCREK_8-003287WILL_WHT_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 101.5731 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003263CEDRCKPU_8-003265MANKIN_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 101.8067 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003264SEVENPTS_8-003287WILL_WHT_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 101.3893 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 102.3485 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003455CORS1_8-003840MILDRED2_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 102.4699 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003460CORS_GL_T_8-003462CORSGUART_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 100.8755 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003462CORSGUART_8-003478NAVARRO1_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 101.7939 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003466KERENS_8-003467POWELL1_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 102.747 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003467POWELL1_8-003472BRIAR_CRK_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 102.5818 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003477EUREKA_P__8-003478NAVARRO1_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 100.1228 | - | 104.0714 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003477EUREKA_P__8-003483GOODLOE_P_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 100.9874 | - | 104.9199 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003478NAVARRO1_8-003840MILDRED2_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 100.3812 | - | 102.8835 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | L_003483GOODLOE_P_8-003490LNGPRAIRIE_8C1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 104.4269 | - | 108.2315 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | MANKIN-KINGSCREEK_8 (SINGLE B TO B) | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 101.7746 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 100.5371 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 101.9218 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | NAVARRO - LONG PRAIRIE 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 101.2661 | - | 105.1781 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | NAV-CORS_W-MONTFORT_8 (SINGLE B TO B) | 138 | 138 | Branch Amp | 1041.7406 | - | - | 104.2896 | 125.7762 | - | 128.9244 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | SEAGOVILLE SW-KAUFMAN-TERRELL SW (SINGLE B TO B) A | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 101.933 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 100.5465 | - | 102.3757 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 101.3823 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 100.9012 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 123.1823 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | TRINIDAD - MANKIN (SINGLE B TO B) | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 101.9607 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | TRIN-MANKIN*EUSTACE SOUTHEAST(DOUBLE B TO B) | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 101.7889 | - | 104.3675 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | TRIN-NIP*MA (DOUBLE B TO B)B | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 101.7289 | - | 104.3383 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 102.0901 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 100.7231 | - | 102.8001 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 122.5716 | - | 123.7458 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 101.1895 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 100.5864 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | WATERMILL-LOOP NINE 345 KV DCKT (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | - | - | 103.9851 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 124.4757 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW ( 3723) -> MONTFTSS__8 ( 3454) CKT 1 | XFMR-ENNSTRAC_8-1 | 138 | 138 | Branch Amp | 1041.7406 | - | - | - | 101.9498 | - | 104.0063 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OLYMPUS_SW (3723) -> MONTFTSS__8 (3454) CKT 1 | Pre-contingency | 138 | 138 | Amps | 1041.7406 | - | - | - | - | 106.672 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | 3WT_001302WILLOWVAL_5_001301WILLOWVAL_8_018537WILLOWVAL_3 C 3 | 138 | 138 | Branch Amp | 778.1677 | - | - | 103.0902 | 105.5954 | 125.2345 | 110.1753 | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | BAS_RANCH_CON | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 107.0304 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | BLUFF CREEK SW - WILLOW VALLEY SW 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | 100.8075 | 103.872 | 120.1804 | 109.6105 | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | C5-WETT-2_A-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 108.4686 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | C5-WETT-2_A-2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 113.8921 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | CATTLEMAN - CHAMPION CREEK & MORGAN CREEK SW - BITTER CREEK SW (LCRA) 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.1469 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | CHINA GROVE SW - AEP PAINT CREEK 138 KV & GRAHAM SES - TONKAWA/COOKFIELD/LONGCREEK 345 KV (DOUBLE B TO B) 2019 SUM - FUTURE-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.9848 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | CHINA GROVE SW - SNYDER 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.0039 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | CLY_PHNT1P7F1-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 103.6423 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | CLY_PHNT1P7F1-2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.9951 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | CLY_PHNT2P7F1-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.6281 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | CLY_PHNT2P7F1-2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.9884 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | E_OECCS_CC1_TRAIN | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.5776 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | E_OECCS_CC2_TRAIN | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.595 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | ENNIS CREEK - GOLDEN SW 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 115.0797 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | G_010012METEOR_5US1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.0089 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | G_888839BAS_RANCH_POIUC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 107.0566 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | HOLLY_CON | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 115.6049 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_001064SUN_8-001067GOLDENSW_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 117.032 | 100.7253 | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_001064SUN_8-001311SACROC_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 101.5003 | 115.66 | 100.0252 | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_001067GOLDENSW_8-001315BRAND_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 114.2268 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_001189BARBER_LK1_8-010050RANGER_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.5616 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_001298ONC900014_TAP-001305SNYDER_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 104.0949 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_001298ONC900014_TAP-001318CHINAGRV_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.354 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_001300EXSHARNR_8-001309BLUFCKTA_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | 100.8519 | 103.9128 | 120.2234 | 109.5491 | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_001300EXSHARNR_8-901303ONC900119_TAPC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | 105.2177 | 107.9616 | 124.2061 | 113.6012 | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_001301WILLOWVAL_8-901303ONC900119_TAPC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | 107.4191 | 110.3666 | 126.6386 | 116.1135 | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_001304DEEPCRK_8-001305SNYDER_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 113.4892 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_001304DEEPCRK_8-001311SACROC_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 113.9728 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_001313ENISCKTA_8-001314ENNISCK_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 115.5778 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_001313ENISCKTA_8-001315BRAND_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 115.1388 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_001314ENNISCK_8-011306DERMOTT_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | 102.0504 | 104.496 | 130.3265 | 113.7256 | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.9936 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_010049RANGER_5-011048TONKAWAW_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.4109 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_010049RANGER_5-011048TONKAWAW_5C2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.4109 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_010050RANGER_8-011393FRONTIER_P8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.833 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_011048TONKAWAW_5-011318SCURCNTYS_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.0723 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_011048TONKAWAW_5-011318SCURCNTYS_5C2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.0723 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_011305DERMOTT_5-011318SCURCNTYS_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 110.6571 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_011305DERMOTT_5-011318SCURCNTYS_5C2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 110.6571 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_011318SCURCNTYS_5-059905FARADAYC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.628 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_023920ABERNATH_5-023928DBLMTN_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 103.2846 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_023924FARMLAND_5-023930FIDLWD_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 105.9078 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_023924FARMLAND_5-888856HOLLY_POIC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 108.6355 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_023928DBLMTN_5-023930FIDLWD_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.6739 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_059904COTTONWOOD-060006HYPERION7AC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.0014 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_060017HODLRAN27A-060515CLEARCRO7AC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.9232 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | L_888856HOLLY_POI-059900LONG_DRAWC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 100.3714 | 119.0099 | 101.67 | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | LCRA TSC_BAKERS_CEDACA_DC | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.8897 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.0854 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.0854 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | LONGCREEK SW - COOK FIELD ROAD SW & LONGCREEK SW - GRAHAM SW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.2442 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.9746 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | MB2552825529 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.9523 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | New Meinan - Sweeteast and BitterCreek 345kV Double | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 103.6455 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | New Sweeteast - Meinan and BitterCreek 345kV Double | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.5141 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 111.4946 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 117.2196 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | SCUR_CLY_P7 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 104.2063 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 1 & SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | 102.3628 | - | 115.354 | 128.2575 | 157.6449 | 137.1401 | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | STECL_4721-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.0854 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 107.9549 | 129.4848 | 111.5287 | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | WILLOW VALLEY TRANSFORMER 1 (SINGLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | 103.0903 | 105.5955 | 125.2346 | 110.1754 | -
TONCOR | WEST | WEST | WEST, WEST | ONC900041_TAP ( 1366) -> KNAPP_8 ( 1310) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 778.1677 | - | 101.6367 | - | - | 100.1801 | - | -
1 | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | ONC900057_TAP (901396) -> BRELYN_8 (11332) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 1200.7211 | - | 105.1069 | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | ONC900057_TAP (901396) -> COSDEN_8 ( 1332) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 109.9312 | - | -
TONCOR | WEST | WEST | WEST, WEST | ONC900084_TAP ( 1289) -> RANGER_8 (10050) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 778.1677 | - | 134.4679 | - | - | - | - | -
TONCOR | WEST | FAR_WEST | WEST, FAR_WEST | ONC900119_TAP (901303) -> EXSHARNR_8 ( 1300) CKT 1 | DERMOTT - BLUFF CREEK SW & DERMOTT - ENNIS CREEK 138 KV (DOUBLE B TO B) 2023 WIN - FUTURE | 138 | 138 | Branch Amp | 748.8818 | 122.816 | 108.8599 | 127.1143 | 128.6661 | 146.8844 | 147.4998 | -
TONCOR | WEST | FAR_WEST | WEST, FAR_WEST | ONC900119_TAP (901303) -> EXSHARNR_8 ( 1300) CKT 1 | DERMOTT - BLUFF CREEK SW & ENNIS CREEK - GOLDEN SW 138 KV (DOUBLE B TO B) 2023 WIN - FUTURE | 138 | 138 | Branch Amp | 748.8818 | 111.7894 | 102.8118 | 115.9883 | 118.2089 | 134.3271 | 135.0922 | -
TONCOR | WEST | FAR_WEST | WEST, FAR_WEST | ONC900119_TAP (901303) -> EXSHARNR_8 ( 1300) CKT 1 | DERMOTT - BLUFF CREEK SW 138 KV (SINGLE B TO B) 2023 SUM - FUTURE | 138 | 138 | Branch Amp | 748.8818 | 102.3266 | - | 105.7214 | 108.3112 | 118.179 | 120.6466 | -
TONCOR | WEST | FAR_WEST | WEST, FAR_WEST | ONC900119_TAP (901303) -> EXSHARNR_8 ( 1300) CKT 1 | L_001309BLUFCKTA_8-001310KNAPP_8C1 | 138 | 138 | Branch Amp | 748.8818 | 102.4515 | - | 105.8312 | 108.4127 | 118.2765 | 120.7347 | -
TONCOR | WEST | FAR_WEST | WEST, FAR_WEST | ONC900119_TAP (901303) -> EXSHARNR_8 ( 1300) CKT 1 | L_001310KNAPP_8-001366ONC900041_TAPC1 | 138 | 138 | Branch Amp | 748.8818 | 105.0248 | - | 108.3988 | 110.8505 | 120.6294 | 122.9391 | -
TONCOR | WEST | FAR_WEST | WEST, FAR_WEST | ONC900119_TAP (901303) -> EXSHARNR_8 ( 1300) CKT 1 | L_001312SCURYCHV_8-011130KNDRSACRC_8C1 | 138 | 138 | Branch Amp | 748.8818 | 109.5714 | - | 112.8548 | 114.9848 | 124.6869 | 127.0149 | -
TONCOR | WEST | FAR_WEST | WEST, FAR_WEST | ONC900119_TAP (901303) -> EXSHARNR_8 ( 1300) CKT 1 | L_001312SCURYCHV_8-011306DERMOTT_8C1 | 138 | 138 | Branch Amp | 748.8818 | 111.4874 | - | 114.7573 | 116.8459 | 126.5897 | 128.9427 | -
TONCOR | WEST | FAR_WEST | WEST, FAR_WEST | ONC900119_TAP (901303) -> EXSHARNR_8 ( 1300) CKT 1 | L_001366ONC900041_TAP-011130KNDRSACRC_8C1 | 138 | 138 | Branch Amp | 748.8818 | 106.0633 | - | 109.4229 | 111.8046 | 121.5676 | 123.8701 | -
TONCOR | WEST | FAR_WEST | WEST, FAR_WEST | ONC900119_TAP (901303) -> EXSHARNR_8 ( 1300) CKT 1 | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | 105.0306 | - | 100.8512 | 101.4274 | 106.9385 | 115.362 | -
TONCOR | WEST | FAR_WEST | WEST, FAR_WEST | ONC900119_TAP (901303) -> EXSHARNR_8 ( 1300) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 105.4176 | 116.5542 | 120.1426 | -
TONCOR | WEST | FAR_WEST | WEST, FAR_WEST | ONC900119_TAP (901303) -> EXSHARNR_8 ( 1300) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 748.8818 | - | 128.1173 | - | - | - | - | -
TSTEC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | ORANGEGRVSW9 ( 5658) -> SANDIEGOSUB9 ( 5654) CKT 1 | L_005660ORANGEGRVSW8-008452LON_HILL4AC1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 107.9867 | - | -
TSTEC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | ORANGEGRVSW9 ( 5658) -> SANDIEGOSUB9 ( 5654) CKT 1 | MBAM-REFORnew | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 111.7607 | - | -
TSTEC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | ORANGEGRVSW9 ( 5658) -> SANDIEGOSUB9 ( 5654) CKT 1 | MBBL-AMnew | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 108.1256 | - | -
TSTEC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | ORANGEGRVSW9 ( 5658) -> SANDIEGOSUB9 ( 5654) CKT 1 | MBLH-BLnew | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 108.1828 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | BAS_RANCH_CON | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 103.0704 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 115.4051 | 103.7921 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 113.7451 | 101.4763 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 101.5406 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | BIGBRN__5-JEWETT_S5 & BIGBRN__5-JEWETT_N5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 116.8358 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 121.6257 | 101.1678 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | BLUBIRD_CON | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 101.172 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 111.3087 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | E_FRNYPP_CC1_TRAIN | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 101.9997 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | E_FRNYPP_CC2_TRAIN | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.0408 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | E_WHCCS2_CC2_TRAIN | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.6844 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | G_150111CPSES_UNIT1UU1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 103.4187 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | G_150112CPSES_UNIT2UU2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 103.6546 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | G_888839BAS_RANCH_POIUC1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 103.0786 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | G_888879BLUBIRD_POIUS1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 100.1654 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 103.8376 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.8369 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 100.6973 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.0288 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.0079 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 100.8974 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 109.4717 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | L_003381BIGBRNW_5-003391JEWETT_N5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 108.369 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | L_003381BIGBRNW_5-068091NAVARROC2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 101.7563 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.0408 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 100.9085 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 100.6624 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 101.7734 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | L_046020LIMEST_POI_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | 100.9602 | 122.0169 | 100.5984 | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | LAKE CREEK - LAKE HALL/TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 100.2089 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 108.0337 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 100.3528 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.9708 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 101.1729 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 110.5273 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 108.5727 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 100.1191 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 105.5787 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 105.7061 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.7438 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.7692 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.6062 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.966 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OUTLAW_5 ( 3386) -> NAVARRO (68091) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 108.0973 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | BAS_RANCH_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.5141 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 146.2023 | - | 148.085 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 134.9702 | - | 139.0898 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 114.7492 | 106.6416 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 113.2374 | 104.6424 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.049 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.5845 | 125.0241 | 109.4964 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | BLUBIRD_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.1243 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 111.0614 | 102.4421 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | E_WCPP_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.186 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | E_WHCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.687 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | E_WHCCS2_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.5805 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.7377 | 122.8026 | 107.7349 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | G_150111CPSES_UNIT1UU1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.1353 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | G_150112CPSES_UNIT2UU2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.2785 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | G_888839BAS_RANCH_POIUC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.519 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | G_888879BLUBIRD_POIUS1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.4349 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | GLASGOW_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 121.4327 | 105.8959 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | GreenRD Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.0692 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.0054 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 112.1972 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_001906VENUS_S5-015201FORBESR2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 115.6916 | 101.1848 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5482 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_001907VENUS_N5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 114.6741 | 104.6862 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.5845 | 125.0241 | 109.4964 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.7377 | 122.8026 | 107.7349 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.7367 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.0499 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.9796 | 123.1358 | 108.0267 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.884 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 108.7096 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 121.0299 | 106.2687 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 119.5447 | 104.3067 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_003374FILESVALY_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 113.7109 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_003384STJOHNS_5-003409LAKE_CRK1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.583 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_003384STJOHNS_5-003711BALE_S5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.1919 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.0239 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.2575 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 121.7877 | 105.9833 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_068011ASPIRE-068051REATAC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1477 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 119.972 | 105.3991 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | LAKE CREEK - LAKE HALL/TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.1074 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | LAKE CREEK-RATTLESNAKE/ST JOHNS_5 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.5841 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | LATIMER_REATA_P7F1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.7588 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 108.0988 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.6382 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.7951 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.1254 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.5951 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | REAT_SKYD_P7F2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.207 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | RICH-BBROWN (DOUBLE B TO B)A | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.8938 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 115.9637 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 113.6805 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 106.8206 | - | 112.1345 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.2305 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.8805 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 110.2594 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.9745 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 121.7182 | 103.8742 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.1909 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.684 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | - | 105.9075 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.3559 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.2131 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.5266 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 105.4771 | - | 109.2731 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 116.4028 | 101.531 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | VENUS-FORT SMITH SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 115.4497 | 101.0315 | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1863 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | WSHACK_LATIMER_P7 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.3069 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | OYSTER_POI (888857) -> VENUS_S5 ( 1906) CKT 1 | XFMR-WHCCS2_5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.0427 | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | OZNC2A ( 6552) -> FDRAN2A ( 6550) CKT 1 | L_006562FDRAN4A-060412CARVER4AC1 | 69 | 69 | Branch Amp | 317.961 | - | 122.8102 | 123.7773 | - | 116.5633 | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | OZNR2A ( 6551) -> OZONA2A ( 6560) CKT 1 | L_006564ILLN4A-076579L_FORTLA8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 109.3712 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | P_BTTLECRK_POI (888876) -> HANEY ( 213) CKT 1 | HILLSBORO-ASH CREEK 138 KV (SINGLE B TO B) B | 138 | 138 | Branch Amp | 338.8795 | 107.1346 | - | 111.2906 | 112.4415 | 123.3393 | 123.8247 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | P_BTTLECRK_POI (888876) -> HANEY ( 213) CKT 1 | L_000234CHATT-003352PECANST_8C1 | 138 | 138 | Branch Amp | 338.8795 | 105.5029 | - | 109.6769 | 110.7995 | 121.6978 | 122.1871 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | P_BTTLECRK_POI (888876) -> HANEY ( 213) CKT 1 | L_000234CHATT-003522HILLBORO1_8C1 | 138 | 138 | Branch Amp | 338.8795 | - | - | 100.7491 | 101.7437 | 112.5868 | 113.0719 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | P_BTTLECRK_POI (888876) -> HANEY ( 213) CKT 1 | L_003352PECANST_8-003473ASHCREEK_8C1 | 138 | 138 | Branch Amp | 338.8795 | 107.1422 | - | 111.3024 | 112.4481 | 123.3399 | 123.83 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | P_BTTLECRK_POI (888876) -> HUBBARD_8 ( 3515) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 338.8795 | - | - | - | - | 100.5379 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | P_BTTLECRK_POI (888876) -> HUBBARD_8 ( 3515) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 338.8795 | - | - | - | - | 100.2613 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | P_BTTLECRK_POI (888876) -> HUBBARD_8 ( 3515) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 338.8795 | - | - | - | - | 100.6658 | 100.0778 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | P_BTTLECRK_POI (888876) -> HUBBARD_8 ( 3515) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 338.8795 | - | - | - | - | 103.4539 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | P_BTTLECRK_POI (888876) -> HUBBARD_8 ( 3515) CKT 1 | L_003522HILLBORO1_8-003546WHITNEY__8C1 | 138 | 138 | Branch Amp | 338.8795 | 106.7621 | - | - | - | 116.3093 | 110.5931 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | P_BTTLECRK_POI (888876) -> HUBBARD_8 ( 3515) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 338.8795 | - | - | - | - | 106.74 | 106.387 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | P_BTTLECRK_POI (888876) -> HUBBARD_8 ( 3515) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 338.8795 | - | - | - | - | 116.1668 | 115.0213 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | P_BTTLECRK_POI (888876) -> HUBBARD_8 ( 3515) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 138 | 138 | Branch Amp | 338.8795 | - | - | - | - | - | 104.4861 | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PANDA_T2_5 (150908) -> PTMPL2_CT1 (150904) CKT 1 | Pre-contingency | 345 | 18 | MVA | 250 | - | - | - | - | 100.4724 | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PANDA_T2_5 (150908) -> PTMPL2_CT2 (150905) CKT 1 | Pre-contingency | 345 | 18 | MVA | 250 | - | - | - | - | 100.5091 | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PANDA_TL (150907) -> PTMPL_CT1 (150901) CKT 1 | Pre-contingency | 345 | 18 | MVA | 250 | - | - | - | - | 100.9388 | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PANDA_TL (150907) -> PTMPL_CT2 (150902) CKT 1 | Pre-contingency | 345 | 18 | MVA | 250 | - | - | - | - | 100.6855 | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | PANDALE2A ( 6567) -> OZNR2A ( 6551) CKT 1 | L_006564ILLN4A-076579L_FORTLA8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 111.8146 | - | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | PANDALE2A ( 6567) -> OZNR2A ( 6551) CKT 1 | MB2074220667 | 69 | 69 | Branch Amp | 317.961 | - | - | 100.1378 | - | - | - | -
TONCOR | NORTH | NORTH | NORTH, NORTH | PARIS_SW1_5 ( 1692) -> VAL_STH_5 ( 1729) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.4359 | - | -
TONCOR | NORTH | NORTH | NORTH, NORTH | PARIS_SW1_5 ( 1692) -> VAL_STH_5 ( 1729) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.0326 | - | -
TONCOR | NORTH | NORTH | NORTH, NORTH | PARIS_SW1_5 ( 1692) -> VAL_STH_5 ( 1729) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.7325 | - | -
TONCOR | NORTH | NORTH | NORTH, NORTH | PARIS_SW1_5 ( 1692) -> VAL_STH_5 ( 1729) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.2929 | - | -
TONCOR | NORTH | NORTH | NORTH, NORTH | PARIS_SW1_5 ( 1692) -> VAL_STH_5 ( 1729) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.2924 | - | -
TONCOR | NORTH | NORTH | NORTH, NORTH | PARIS_SW1_5 ( 1692) -> VAL_STH_5 ( 1729) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.7183 | - | -
TONCOR | NORTH | NORTH | NORTH, NORTH | PARIS_SW1_5 ( 1692) -> VAL_STH_5 ( 1729) CKT 1 | L_001690VALLYSES1_5-011683PACIFICSW_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 109.5033 | 122.0069 | 114.0485 | -
TONCOR | NORTH | NORTH | NORTH, NORTH | PARIS_SW1_5 ( 1692) -> VAL_STH_5 ( 1729) CKT 1 | L_001692PARIS_SW1_5-011683PACIFICSW_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.1818 | - | -
TONCOR | NORTH | NORTH | NORTH, NORTH | PARIS_SW1_5 ( 1692) -> VAL_STH_5 ( 1729) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.6734 | - | -
TONCOR | NORTH | NORTH | NORTH, NORTH | PARIS_SW1_5 ( 1692) -> WOODARD_5 (11699) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.0968 | - | - | -
TONCOR | NORTH | EAST | NORTH, EAST | PARIS_SW1_8 ( 1693) -> ENLOE_T8 (11806) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 106.597 | - | -
TONCOR | NORTH | NORTH | NORTH, NORTH | PARIS_SW1_8 ( 1693) -> PARIS_KC_8 ( 1776) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.4105 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKDB2_8 ( 2445) -> PLGRV1T_8 ( 2960) CKT 1 | L_002263GELLER_8-003079SSWWT2T_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 105.0292 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKDB2_8 ( 2445) -> PLGRV1T_8 ( 2960) CKT 1 | L_002263GELLER_8-003083WILMER1_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 104.491 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKDB2_8 ( 2445) -> PLGRV1T_8 ( 2960) CKT 1 | L_002434SGVLSW1_8-003076SGVL1_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 108.2429 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKDB2_8 ( 2445) -> PLGRV1T_8 ( 2960) CKT 1 | L_003076SGVL1_8-003077KLEBRG1T_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 106.7799 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKDB2_8 ( 2445) -> PLGRV1T_8 ( 2960) CKT 1 | L_003077KLEBRG1T_8-003079SSWWT2T_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 105.1895 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKDB2_8 ( 2445) -> PLGRV1T_8 ( 2960) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | - | 112.6297 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKDB2_8 ( 2445) -> PLGRV1T_8 ( 2960) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 111.2448 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKDB2_8 ( 2445) -> PLGRV1T_8 ( 2960) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 139.415 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.2623 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | 3WT_001918SHRYAUTO1_5_001920SHRY_B8_011920SHRY_B_3 C 1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.8249 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | 3WT_002420CHILSW1_5_016421CHILSW_1T8_012419CHILSW1_3 C 1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.9653 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 113.5054 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 106.9559 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.503 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 132.0482 | 143.3967 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 133.992 | 145.1306 | 101.0056 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.4448 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8684 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | G_150023MCSES_UNIT8UN8 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.9433 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | GLASGOW_CON | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.5887 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.3077 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.4774 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.1027 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.6825 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | L_001920SHRY_B8-002258PARKROW2_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 106.6686 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | L_001921LIGGETTA1_5-002632MILLERRD_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8942 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 104.9234 | 111.8368 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 107.9658 | 115.1752 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.503 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.8684 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | L_002258PARKROW2_8-002259LTV1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 105.5027 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | L_002259LTV1_8-002262GRANDPR1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.5256 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | L_002262GRANDPR1_8-012491FSHCRK2_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9779 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.9461 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.0528 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 102.2766 | 107.6662 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 103.606 | 110.4282 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 103.467 | 110.2245 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 106.1727 | 112.9521 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 101.556 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 106.497 | 114.8749 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.9336 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 104.1497 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW1_8 ( 2257) -> POLY_AM1_8 ( 2260) CKT 1 | XFMR-MTCK_8T8-8 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 103.9433 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW2_8 ( 2258) -> LTV1_8 ( 2259) CKT 1 | 3WT_002420CHILSW1_5_016421CHILSW_1T8_012419CHILSW1_3 C 1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | - | 100.128 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW2_8 ( 2258) -> LTV1_8 ( 2259) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | 112.9377 | - | 106.2805 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW2_8 ( 2258) -> LTV1_8 ( 2259) CKT 1 | CEDAR HILL SW 345-138 KV AUTO #1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | - | 112.1314 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW2_8 ( 2258) -> LTV1_8 ( 2259) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | 114.3545 | - | 107.742 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW2_8 ( 2258) -> LTV1_8 ( 2259) CKT 1 | L_002421CHILSW_S8-012491FSHCRK2_8C1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | - | 114.5921 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PARKROW2_8 (2258) -> LTV1_8 (2259) CKT 1 | Pre-contingency | 138 | 138 | Amps | 1317.8646 | - | - | - | - | 100.8402 | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | PAUL2A (6048) -> LKPAULS4A (6050) CKT 1 | Pre-contingency | 69 | 138 | MVA | 63 | - | - | - | - | 103.9212 | 100.5217 | -
TAEPTC | COAST | COAST | COAST, COAST | PAVLOV4B ( 8614) -> BLESSING4A ( 8121) CKT 1 | L_005915SO_TEX__345A-008123BLESSING7AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 100.7128 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PAVLOV4B ( 8614) -> BLESSING4A ( 8121) CKT 1 | L_008102EL_CAMPO4A-008679ARROZ4AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 131.4579 | 128.7422 | -
TAEPTC | COAST | COAST | COAST, COAST | PAVLOV4B ( 8614) -> BLESSING4A ( 8121) CKT 1 | L_008104LANCTYPM4A-008127LAN_CTY4AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 122.671 | 120.1231 | -
TAEPTC | COAST | COAST | COAST, COAST | PAVLOV4B ( 8614) -> BLESSING4A ( 8121) CKT 1 | L_008104LANCTYPM4A-008679ARROZ4AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 122.3532 | 119.8101 | -
TAEPTC | COAST | COAST | COAST, COAST | PAVLOV4B ( 8614) -> BLESSING4A ( 8121) CKT 1 | L_042985DYANN__POI_8-043570WHARTN__60B8C&1-MS | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 101.3855 | 114.0754 | -
TAEPTC | COAST | COAST | COAST, COAST | PAVLOV4B ( 8614) -> BLESSING4A ( 8121) CKT 1 | L_043570WHARTN__60B8-044150HNGFRD_POI_8C&1-MS | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | - | 109.874 | -
TAEPTC | COAST | COAST | COAST, COAST | PAVLOV4B ( 8614) -> BLESSING4A ( 8121) CKT 1 | L_044150HNGFRD_POI_8-044190E_BERN__B138C60 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 110.119 | 127.6656 | -
TAEPTC | COAST | COAST | COAST, COAST | PAVLOV4B ( 8614) -> BLESSING4A ( 8121) CKT 1 | L10006-1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 123.5688 | 120.6883 | -
TAEPTC | COAST | COAST | COAST, COAST | PAVLOV4B ( 8614) -> BLESSING4A ( 8121) CKT 1 | L10010006-1B | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 122.6375 | 120.1014 | -
TAEPTC | COAST | COAST | COAST, COAST | PAVLOV4B ( 8614) -> BLESSING4A ( 8121) CKT 1 | P7-1_E1>>T6060D | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 101.2904 | 114.1931 | -
TAEPTC | COAST | COAST | COAST, COAST | PAVLOV4B ( 8614) -> BLESSING4A ( 8121) CKT 1 | T_008121BLESSING4A-008123BLESSING7AC1 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 100.7016 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PAVLOV4B ( 8614) -> BLESSING4A ( 8121) CKT 1 | T100002 | 138 | 138 | Branch Amp | 656.8405 | - | - | - | - | 130.9316 | 128.7127 | -
TCPSE,TSTEC | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | PAWNEESW5 ( 5725) -> SPRUCE ( 5400) CKT 1 | E5SCA1C1_B | 345 | 345 | Branch Amp | 1698.5809 | 110.5118 | - | - | - | - | - | -
TCPSE,TSTEC | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | PAWNEESW5 ( 5725) -> SPRUCE ( 5400) CKT 1 | S2SANMGD1 | 345 | 345 | Branch Amp | 1698.5809 | - | - | 103.5403 | - | - | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | AEN_LY-FPP:CIS-HO | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 102.46 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | AEN_LY-FPP¦CIS | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 104.0594 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 114.0046 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | ARGENTA_CON | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 106.3358 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | BAS_RANCH_CON | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 102.7435 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 109.8453 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 108.3201 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 106.3038 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | DVCPA1C21B_1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 110.0774 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | DVCPA1C21B_2 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 110.7879 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | E_B_DAVIS_CC1_TRAIN | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 110.4057 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | E_BRAUNIG_CC1_TRAIN | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.4898 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | E_CCEC_CC1_TRAIN | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 103.5813 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | E_DUKE_CC1_TRAIN | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 103.1608 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | E_INGLCOSW_CC1_TRAIN | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 106.1855 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | E_LGE_CC1_TRAIN | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 103.8721 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | E_NEDIN_CC1_TRAIN | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 107.527 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | E_NUECES_B_CC1_TRAIN | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 110.3576 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | E_RAYBURN_CC1_TRAIN | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.2445 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | E_VICTORIA_CC1_TRAIN | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 107.0893 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | G_110467FO_FORMOSG11UPB | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 100.4697 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | G_110469FO_FORMOSG12UPC | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 100.4697 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | G_120261TREB_SLR_S1US1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 105.6814 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | G_160101B_D_B_DAVIG1UN1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.1008 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | G_163641CHARGER_S1US1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.6489 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | G_163931OUTPOST_S1US1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 100.3924 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | G_170126CALAVER_JKS2UL2 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 106.2868 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | G_888839BAS_RANCH_POIUC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 102.7279 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | G_RIO_TRAIN | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 102.6486 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | J5LCA1C1_B | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 102.6605 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 116.8786 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 132.6107 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 115.9266 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 119.5552 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 111.5625 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_005380SHAULA-005915SO_TEX__345AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 111.6526 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_005502RAYBURN8-005506FURHMANSW8C1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.4004 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_005502RAYBURN8-005513RAYBURNPLNT8C1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.2445 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_005546DANEVANGSW8-005588REDBLUFSUB8C1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.1394 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_005546DANEVANGSW8-008121BLESSING4AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 102.5171 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_005582VANDERBLTSW9-005586VANDERBLTSB9C1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 100.3796 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_005585VANDRBLTSUB8-005588REDBLUFSUB8C1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 100.1671 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 132.3271 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 120.1081 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008102EL_CAMPO4A-008679ARROZ4AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 108.9266 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008104LANCTYPM4A-008127LAN_CTY4AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 107.0415 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008104LANCTYPM4A-008679ARROZ4AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 106.9752 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008117GANADO4A-008118EDNA4AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 105.0111 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008117GANADO4A-008192PULSAR4AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 105.1977 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008118EDNA4A-008172VICTORIA4AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 104.2853 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008121BLESSING4A-008125LOLITA4AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 128.563 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008126FORMOSA4A-008140JOSLIN4AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 129.4884 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008140JOSLIN4A-008685COBIA4AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 130.4209 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008140JOSLIN4A-120263TREB_SLR_8C1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 105.6806 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008155SANDCRAB4A-008685COBIA4AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 129.3627 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008155SANDCRAB4A-008723CANGREJO4AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 129.0621 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008172VICTORIA4A-110884VIC_SU6C1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.1663 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.9169 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008455LONHILL7A-008579KATOEN7AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 104.6074 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008458B_DAVIS4A-160105B_DAVIS_1_8C1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.1008 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008458B_DAVIS4A-160106B_DAVIS_2_8C1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.829 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008579KATOEN7A-008606GODDARD7AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 103.1889 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_008606GODDARD7A-888858ARGENTA_POIC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.5564 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 117.9826 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_044150HNGFRD_POI_8-044190E_BERN__B138C60 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 100.0151 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_080071ZORILLO7A-080076AJO7AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 105.0851 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_080071ZORILLO7A-080171SARITA7AC1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.2368 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_080171SARITA7A-160299BAFFIN_2_5C1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.2357 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 109.7488 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L10005-2B | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 102.7998 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L10006-1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 107.7126 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L10010006-1B | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 107.0195 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L10011585 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.2367 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L10012105 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.1662 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | L10012965 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 100.8986 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | LCRA TSC_T185_T246 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 100.9306 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | LCRA TSC_T255_TAE3121_1 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 105.1827 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 103.6904 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | M10000271115801 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 107.8683 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | M100052100072 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 109.898 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | M105311105321 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 103.8711 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | M115851115803 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 105.0851 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | MB100002711580 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 107.8683 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | MB1000710005-2 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 108.4284 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | MB1158011585 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 105.0851 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | N5GSU2_B | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 106.2868 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 100.5288 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | P7-1_E1>>T1839X1_ERC | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 110.5948 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | P7-1_E1>>T1839X2_ERC | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 109.8959 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | P7-1_E1>>T2764Y_ERCa | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 113.366 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | P7-1_E1>>T3944Z_ERC | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 131.0658 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | R4U2A5C1_1_B | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.4751 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | SAN_PAT_CON | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 107.6177 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | STECL_10220 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 100.7345 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | STP - HOUDINI & STP - SHAULA | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 113.1794 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | T100002 | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 108.8972 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 101.7451 | - | -
TAEPTC | COAST | COAST | COAST, COAST | PCOMFORT2A ( 8132) -> CANGREJO2A ( 8720) CKT 1 | WAP - HOUDINI & STP - SHAULA | 69 | 69 | Branch Amp | 326.3284 | - | - | - | - | 110.2649 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | PECONE_P8 (11105) -> AQUIFER_8 (11377) CKT 1 | L_011097SANDLAKE_8-011612ONC900009_TAPC1 | 138 | 138 | Branch Amp | 2539.5042 | - | - | - | - | 100.6052 | - | -
TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | PETERS__B138 (46220) -> L_BELLSO8_1Y ( 7270) CKT 1 | E5DVA1C1_1_B | 138 | 138 | Branch Amp | 1627.4583 | - | - | - | 101.5878 | - | - | -
TCNPE | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | PETERS__B138 (46220) -> L_BELLSO8_1Y ( 7270) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | 138 | Branch Amp | 1627.4583 | - | - | - | 100.9963 | - | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | PHBL_TAP2A ( 6546) -> STRS2A ( 6547) CKT 1 | L_060361SANTARIT4A-060414OWLS4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 125.9878 | 122.3456 | 122.4904 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | PHBL_TAP2A ( 6546) -> STRS2A ( 6547) CKT 1 | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 126.032 | 122.2504 | 122.2921 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | PHBL_TAP2A ( 6546) -> STRS2A ( 6547) CKT 1 | L_060723CROSSOVE4A-060728PALOUSE4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 135.8495 | 133.5488 | 136.891 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | PHBL_TAP2A ( 6546) -> STRS2A ( 6547) CKT 1 | L_060723CROSSOVE4A-076032L_NORTMC8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 135.8984 | 133.6042 | 136.9519 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | PHBL_TAP2A ( 6546) -> STRS2A ( 6547) CKT 1 | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 124.3376 | 121.6414 | 121.6071 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | PHBL_TAP2A ( 6546) -> STRS2A ( 6547) CKT 1 | L2020944-A | 69 | 69 | Branch Amp | 317.961 | - | - | - | 126.0346 | 122.2594 | 122.2924 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | PHBL_TAP2A ( 6546) -> STRS2A ( 6547) CKT 1 | L2020944-B | 69 | 69 | Branch Amp | 317.961 | - | - | - | 135.8492 | 133.5485 | 136.8904 | -
TAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | PILOTKNOB ( 9259) -> CARSON ( 9175) CKT 1 | AEN_HC-EP¦PK | 138 | 138 | Branch Amp | 2008.1747 | - | - | - | - | 100.4688 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | ALLEN SW 345-138 KV AUTO #1 (SINGLE AUTO) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.308 | - | 102.7063 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | ANNA SW - VALLEY SOUTH 345 KV & ANNA SW - FARMERSVILLE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0625 | - | 102.0065 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | BEPC_015_2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.6943 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | CARTWHEEL_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 105.2516 | - | 107.7958 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.4582 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 107.4879 | - | 108.9866 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | L_001685FARMVLSW_5-011689CYCLONE_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 105.9844 | - | 108.0005 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | L_001685FARMVLSW_5-011700SALTILLO_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.013 | - | 105.4924 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | L_001690VALLYSES1_5-002373ANNASW_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.568 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | L_001690VALLYSES1_5-011683PACIFICSW_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.3996 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | L_001695MOSES_5-001697SULSP_SS1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 107.6716 | - | 110.1109 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | L_001697SULSP_SS1_5-888847CARTWHEEL_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 105.3861 | - | 107.3149 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | L_002361CRLTN_NW1_5-002522PL_TENNY_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.9146 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | L_002372COLLINSS1_5-002373ANNASW_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.8589 | - | 105.0026 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | L_002461ROYSE_N5-002464CASHSW_T5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.0931 | - | 104.042 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | L_002461ROYSE_N5-002513ALLENSW1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0934 | - | 102.6523 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | L_011684BRIGHTR_5-011688THORNTRE_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 101.8925 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | L_011684BRIGHTR_5-011689CYCLONE_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.6031 | - | 104.3284 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | L_011688THORNTRE_5-011700SALTILLO_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.6785 | - | 102.728 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | L_888847CARTWHEEL_POI-002464CASHSW_T5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 105.7547 | - | 108.3198 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | MOSES-SULPHUR SPRINGS SW 345-138 KV AUTO SULPHUR SPRINGS SW 345-138 KV AUTO #1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 108.1359 | - | 110.7541 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | MOSES-THORNTREE SW 345 KV | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 106.0312 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | PARIS SW-PACIFIC SW/VALLEY S SW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 108.5996 | - | 111.0586 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 124.2425 | - | 125.944 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 119.9056 | - | 121.8643 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 106.1306 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | VALLEY S-VALLEY SW 345 KV & VALLEY S-PARIS SW 345 KV | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.1745 | - | 102.2291 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 112.9222 | - | 115.6709 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 ( 2514) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.1294 | - | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | PINEFOREST_POI (888854) -> ALLENSW2_5 (2514) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1725.3568 | - | - | - | - | 105.8975 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PLGRV1T_8 ( 2960) -> MURDCK2T_8 ( 2962) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 116.1193 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PLRD2_8 ( 2922) -> LKHLS2T_8 ( 2924) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1986.0011 | - | - | - | - | - | 101.8111 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PLRD2_8 ( 2922) -> LKHLS2T_8 ( 2924) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1986.0011 | - | - | - | 101.0792 | - | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | POAGE ( 126) -> TEMPTAYV1_9 ( 3636) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 69 | 69 | Branch Amp | 861.8416 | 103.2632 | - | - | 134.8436 | - | 129.5252 | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | POAGE ( 126) -> TEMPTAYV1_9 ( 3636) CKT 1 | L_000132BELLCNTY8-003415TEMP_SS__8C1 | 69 | 69 | Branch Amp | 861.8416 | - | - | - | 107.6918 | 119.6801 | 111.2604 | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | POAGE ( 126) -> TEMPTAYV1_9 ( 3636) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 69 | 69 | Branch Amp | 861.8416 | - | - | - | 115.2967 | 132.8304 | 116.5863 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | POLY_AM1_8 ( 2260) -> LAKECRST_8 (12492) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 101.1012 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | POLY_AM1_8 ( 2260) -> LAKECRST_8 (12492) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 120.2165 | 130.9114 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | POLY_AM1_8 ( 2260) -> LAKECRST_8 (12492) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | 122.162 | 132.6899 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | POLY_AM1_8 ( 2260) -> LAKECRST_8 (12492) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.9514 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | POLY_AM1_8 ( 2260) -> LAKECRST_8 (12492) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.7844 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | POLY_AM1_8 ( 2260) -> LAKECRST_8 (12492) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 102.5971 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | POMPANO4A (8535) -> CHALYBE4A (8735) CKT 1 | Pre-contingency | 138 | 138 | Amps | 903.6786 | - | - | - | 130.6434 | 131.1127 | 131.5588 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | PORTILLA4A ( 8924) -> CLLCOTTE4A ( 8027) CKT 1 | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | 138 | Branch Amp | 510.4111 | - | - | - | - | 103.6886 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCK1_8 ( 2763) -> PARKDB1_8 ( 2442) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1230.007 | - | - | - | - | - | 109.5743 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCK1_8 ( 2763) -> PARKDB1_8 ( 2442) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1230.007 | - | - | - | 115.4271 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCK2_8 ( 2762) -> SCYENE1T_8 ( 2743) CKT 1 | L_002441PRCKSW1_8-002763PRCK1_8C1 | 138 | 138 | Branch Amp | 1230.007 | - | - | - | - | 101.374 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCK2_8 ( 2762) -> SCYENE1T_8 ( 2743) CKT 1 | PARKDALE 260-PRAIRIE CREEK SW (SINGLE B TO B) | 138 | 138 | Branch Amp | 1230.007 | - | - | - | - | 100.745 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCK2_8 ( 2762) -> SCYENE1T_8 ( 2743) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1230.007 | - | - | - | - | - | 114.5554 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCK2_8 ( 2762) -> SCYENE1T_8 ( 2743) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1230.007 | - | - | - | 120.5734 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCKSW1_8 ( 2441) -> PRCK1_8 ( 2763) CKT 1 | L_002441PRCKSW1_8-002762PRCK2_8C1 | 138 | 138 | Branch Amp | 1230.007 | - | - | - | - | 102.6937 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCKSW1_8 ( 2441) -> PRCK1_8 ( 2763) CKT 1 | L_002743SCYENE1T_8-002762PRCK2_8C1 | 138 | 138 | Branch Amp | 1230.007 | - | - | - | - | 101.1578 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCKSW1_8 ( 2441) -> PRCK1_8 ( 2763) CKT 1 | PARKDALE 550-PRAIRIE CREEK SW (SINGLE B TO B) | 138 | 138 | Branch Amp | 1230.007 | - | - | - | - | 100.9685 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCKSW1_8 ( 2441) -> PRCK1_8 ( 2763) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1230.007 | - | - | - | - | - | 114.0968 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCKSW1_8 ( 2441) -> PRCK1_8 ( 2763) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1230.007 | - | - | - | 120.0209 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCKSW1_8 ( 2441) -> PRCK2_8 ( 2762) CKT 1 | CENTERVILLE SW - PARKDALE DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1230.007 | - | - | - | - | 101.7718 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCKSW1_8 ( 2441) -> PRCK2_8 ( 2762) CKT 1 | L_002441PRCKSW1_8-002763PRCK1_8C1 | 138 | 138 | Branch Amp | 1230.007 | - | - | - | - | 104.8484 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCKSW1_8 ( 2441) -> PRCK2_8 ( 2762) CKT 1 | L_002442PARKDB1_8-002763PRCK1_8C1 | 138 | 138 | Branch Amp | 1230.007 | - | - | - | - | 102.8422 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCKSW1_8 ( 2441) -> PRCK2_8 ( 2762) CKT 1 | PARKDALE 260-PRAIRIE CREEK SW (SINGLE B TO B) | 138 | 138 | Branch Amp | 1230.007 | - | - | - | - | 104.2174 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCKSW1_8 ( 2441) -> PRCK2_8 ( 2762) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1230.007 | - | - | - | - | - | 118.0238 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PRCKSW1_8 ( 2441) -> PRCK2_8 ( 2762) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1230.007 | - | - | - | 124.1394 | - | - | -
TONCOR | EAST | EAST | EAST, EAST | PRKCENTRAL_8 ( 3164) -> TYLERLOP_8 ( 3220) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 2062.5625 | - | - | - | 139.4287 | 156.7071 | 145.9608 | -
TONCOR | EAST | EAST | EAST, EAST | PRKCENTRAL_8 ( 3164) -> TYLERLOP_8 ( 3220) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 2062.5625 | - | - | - | 137.3341 | 154.3996 | 143.2139 | -
TONCOR | EAST | EAST | EAST, EAST | PRKCENTRAL_8 ( 3164) -> TYLERLOP_8 ( 3220) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 2062.5625 | - | - | 104.2218 | 144.5167 | 163.2768 | 151.0406 | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT1 (150901) -> PANDA_TL (150907) CKT 1 | E_PANDA_T2_CC1_TRAIN | 345 | 18 | Branch MVA | 250 | - | - | - | 100.9388 | - | 100.4343 | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT1 (150901) -> PANDA_TL (150907) CKT 1 | E5DVA1C1_1_B | 345 | 18 | Branch MVA | 250 | - | - | - | 100.9388 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT1 (150901) -> PANDA_TL (150907) CKT 1 | E5DVA1C1_1_B_1 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.7955 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT1 (150901) -> PANDA_TL (150907) CKT 1 | E5DVA1C1_1_B_2 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.0607 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT1 (150901) -> PANDA_TL (150907) CKT 1 | KILLEEN SS - RUSSELL GAP / BUCKHORN_5 (DOUBLE B TO B ) | 345 | 18 | Branch MVA | 250 | - | - | - | 100.7146 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT1 (150901) -> PANDA_TL (150907) CKT 1 | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | 18 | Branch MVA | 250 | - | - | - | 100.7175 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT1 (150901) -> PANDA_TL (150907) CKT 1 | L_007041L_JOHNDU5_1Y-007047L_HORNSB5_1YC1 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.7242 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT1 (150901) -> PANDA_TL (150907) CKT 1 | L_007042L_ZORN__5_1Y-007510L_EUCLID5_1YC1 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.7235 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT1 (150901) -> PANDA_TL (150907) CKT 1 | L_007047L_HORNSB5_1Y-007738L_WHISVA5_1YC1 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.0564 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT1 (150901) -> PANDA_TL (150907) CKT 1 | LCRA TSC_T510_T511_3 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.5022 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT1 (150901) -> PANDA_TL (150907) CKT 1 | LCRA TSC_T510_T775 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.5148 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT1 (150901) -> PANDA_TL (150907) CKT 1 | LCRATSC_3_GILLCR_WHISVA | 345 | 18 | Branch MVA | 250 | - | - | - | 100.5723 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT1 (150901) -> PANDA_TL (150907) CKT 1 | LCRATSC_4_WHISVA_HORNSB | 345 | 18 | Branch MVA | 250 | - | - | - | 100.7197 | - | 100.0342 | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT1 (150901) -> PANDA_TL (150907) CKT 1 | LCRATSC_5_HORNSB_EUCLID | 345 | 18 | Branch MVA | 250 | - | - | - | 100.728 | - | 100.0437 | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT1 (150901) -> PANDA_TL (150907) CKT 1 | LCRATSC_6_EUCLID_JOHNDU | 345 | 18 | Branch MVA | 250 | - | - | - | 100.7434 | - | 100.0637 | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT1 (150901) -> PANDA_TL (150907) CKT 1 | LCRATSC_7_JOHNDU_ZORN__ | 345 | 18 | Branch MVA | 250 | - | - | - | 100.7278 | - | 100.0428 | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT2 (150902) -> PANDA_TL (150907) CKT 1 | E_PANDA_T2_CC1_TRAIN | 345 | 18 | Branch MVA | 250 | - | - | - | 100.6854 | - | 100.1932 | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT2 (150902) -> PANDA_TL (150907) CKT 1 | E5DVA1C1_1_B | 345 | 18 | Branch MVA | 250 | - | - | - | 100.6854 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT2 (150902) -> PANDA_TL (150907) CKT 1 | E5DVA1C1_1_B_1 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.5429 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT2 (150902) -> PANDA_TL (150907) CKT 1 | KILLEEN SS - RUSSELL GAP / BUCKHORN_5 (DOUBLE B TO B ) | 345 | 18 | Branch MVA | 250 | - | - | - | 100.4667 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT2 (150902) -> PANDA_TL (150907) CKT 1 | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | 18 | Branch MVA | 250 | - | - | - | 100.4695 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT2 (150902) -> PANDA_TL (150907) CKT 1 | L_007041L_JOHNDU5_1Y-007047L_HORNSB5_1YC1 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.476 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT2 (150902) -> PANDA_TL (150907) CKT 1 | L_007042L_ZORN__5_1Y-007510L_EUCLID5_1YC1 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.4754 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT2 (150902) -> PANDA_TL (150907) CKT 1 | LCRA TSC_T510_T511_3 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.2595 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT2 (150902) -> PANDA_TL (150907) CKT 1 | LCRA TSC_T510_T775 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.2717 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT2 (150902) -> PANDA_TL (150907) CKT 1 | LCRATSC_3_GILLCR_WHISVA | 345 | 18 | Branch MVA | 250 | - | - | - | 100.3155 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT2 (150902) -> PANDA_TL (150907) CKT 1 | LCRATSC_4_WHISVA_HORNSB | 345 | 18 | Branch MVA | 250 | - | - | - | 100.4717 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT2 (150902) -> PANDA_TL (150907) CKT 1 | LCRATSC_5_HORNSB_EUCLID | 345 | 18 | Branch MVA | 250 | - | - | - | 100.4797 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT2 (150902) -> PANDA_TL (150907) CKT 1 | LCRATSC_6_EUCLID_JOHNDU | 345 | 18 | Branch MVA | 250 | - | - | - | 100.4948 | - | - | -
RPANDA | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL_CT2 (150902) -> PANDA_TL (150907) CKT 1 | LCRATSC_7_JOHNDU_ZORN__ | 345 | 18 | Branch MVA | 250 | - | - | - | 100.4796 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT1 (150904) -> PANDA_T2_5 (150908) CKT 1 | E_PANDA_T1_CC1_TRAIN | 345 | 18 | Branch MVA | 250 | - | - | - | 100.4724 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT1 (150904) -> PANDA_T2_5 (150908) CKT 1 | E5DVA1C1_1_B | 345 | 18 | Branch MVA | 250 | - | - | - | 100.4724 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT1 (150904) -> PANDA_T2_5 (150908) CKT 1 | E5DVA1C1_1_B_1 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.3386 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT1 (150904) -> PANDA_T2_5 (150908) CKT 1 | KILLEEN SS - RUSSELL GAP / BUCKHORN_5 (DOUBLE B TO B ) | 345 | 18 | Branch MVA | 250 | - | - | - | 100.2532 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT1 (150904) -> PANDA_T2_5 (150908) CKT 1 | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | 18 | Branch MVA | 250 | - | - | - | 100.256 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT1 (150904) -> PANDA_T2_5 (150908) CKT 1 | L_007041L_JOHNDU5_1Y-007047L_HORNSB5_1YC1 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.2625 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT1 (150904) -> PANDA_T2_5 (150908) CKT 1 | L_007042L_ZORN__5_1Y-007510L_EUCLID5_1YC1 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.2619 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT1 (150904) -> PANDA_T2_5 (150908) CKT 1 | LCRA TSC_T510_T511_3 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.0455 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT1 (150904) -> PANDA_T2_5 (150908) CKT 1 | LCRA TSC_T510_T775 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.0578 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT1 (150904) -> PANDA_T2_5 (150908) CKT 1 | LCRATSC_3_GILLCR_WHISVA | 345 | 18 | Branch MVA | 250 | - | - | - | 100.1416 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT1 (150904) -> PANDA_T2_5 (150908) CKT 1 | LCRATSC_4_WHISVA_HORNSB | 345 | 18 | Branch MVA | 250 | - | - | - | 100.2582 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT1 (150904) -> PANDA_T2_5 (150908) CKT 1 | LCRATSC_5_HORNSB_EUCLID | 345 | 18 | Branch MVA | 250 | - | - | - | 100.2663 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT1 (150904) -> PANDA_T2_5 (150908) CKT 1 | LCRATSC_6_EUCLID_JOHNDU | 345 | 18 | Branch MVA | 250 | - | - | - | 100.2813 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT1 (150904) -> PANDA_T2_5 (150908) CKT 1 | LCRATSC_7_JOHNDU_ZORN__ | 345 | 18 | Branch MVA | 250 | - | - | - | 100.2661 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT2 (150905) -> PANDA_T2_5 (150908) CKT 1 | E_PANDA_T1_CC1_TRAIN | 345 | 18 | Branch MVA | 250 | - | - | - | 100.5091 | - | 100.013 | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT2 (150905) -> PANDA_T2_5 (150908) CKT 1 | E5DVA1C1_1_B | 345 | 18 | Branch MVA | 250 | - | - | - | 100.5091 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT2 (150905) -> PANDA_T2_5 (150908) CKT 1 | E5DVA1C1_1_B_1 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.3753 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT2 (150905) -> PANDA_T2_5 (150908) CKT 1 | KILLEEN SS - RUSSELL GAP / BUCKHORN_5 (DOUBLE B TO B ) | 345 | 18 | Branch MVA | 250 | - | - | - | 100.2899 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT2 (150905) -> PANDA_T2_5 (150908) CKT 1 | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 345 | 18 | Branch MVA | 250 | - | - | - | 100.2928 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT2 (150905) -> PANDA_T2_5 (150908) CKT 1 | L_007041L_JOHNDU5_1Y-007047L_HORNSB5_1YC1 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.2993 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT2 (150905) -> PANDA_T2_5 (150908) CKT 1 | L_007042L_ZORN__5_1Y-007510L_EUCLID5_1YC1 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.2987 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT2 (150905) -> PANDA_T2_5 (150908) CKT 1 | LCRA TSC_T510_T511_3 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.0824 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT2 (150905) -> PANDA_T2_5 (150908) CKT 1 | LCRA TSC_T510_T775 | 345 | 18 | Branch MVA | 250 | - | - | - | 100.0946 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT2 (150905) -> PANDA_T2_5 (150908) CKT 1 | LCRATSC_3_GILLCR_WHISVA | 345 | 18 | Branch MVA | 250 | - | - | - | 100.1783 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT2 (150905) -> PANDA_T2_5 (150908) CKT 1 | LCRATSC_4_WHISVA_HORNSB | 345 | 18 | Branch MVA | 250 | - | - | - | 100.295 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT2 (150905) -> PANDA_T2_5 (150908) CKT 1 | LCRATSC_5_HORNSB_EUCLID | 345 | 18 | Branch MVA | 250 | - | - | - | 100.303 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT2 (150905) -> PANDA_T2_5 (150908) CKT 1 | LCRATSC_6_EUCLID_JOHNDU | 345 | 18 | Branch MVA | 250 | - | - | - | 100.3181 | - | - | -
RCXAT2 | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | PTMPL2_CT2 (150905) -> PANDA_T2_5 (150908) CKT 1 | LCRATSC_7_JOHNDU_ZORN__ | 345 | 18 | Branch MVA | 250 | - | - | - | 100.3029 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | PUMPJACK4A (60374) -> JERRY4A ( 6559) CKT 1 | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 138 | 138 | Branch Amp | 631.7383 | - | - | - | - | 101.3821 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | QUARRSTR (500211) -> QUARRYFLD_8 (11189) CKT 1 | 3WT_011188QUARRYFLD_5_011189QUARRYFLD_8_011216QUARRYFLD2_3 C 2 | 138 | 1 | Branch MVA | 750 | - | - | - | - | 107.9367 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | QUARRSTR (500212) -> QUARRYFLD_8 (11189) CKT 2 | 3WT_011188QUARRYFLD_5_011189QUARRYFLD_8_011194QUARRYFLD1_3 C 1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | 107.9635 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | QUARRYFLD_5 (11188) -> QUARRSTR (500211) CKT 1 | 3WT_011188QUARRYFLD_5_011189QUARRYFLD_8_011216QUARRYFLD2_3 C 2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | 114.8785 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | QUARRYFLD_5 (11188) -> QUARRSTR (500212) CKT 2 | 3WT_011188QUARRYFLD_5_011189QUARRYFLD_8_011194QUARRYFLD1_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | 114.906 | - | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 573.1665 | - | - | - | 127.0361 | 144.1954 | 127.4956 | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 573.1665 | - | - | 103.4629 | 134.9396 | 152.3182 | 134.3351 | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 573.1665 | - | - | - | 128.7573 | 146.1899 | 129.0335 | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 573.1665 | - | - | 103.8881 | 136.731 | 154.3412 | 135.7361 | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 573.1665 | - | - | - | 129.108 | 146.9036 | 129.8683 | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 573.1665 | - | - | 105.5319 | 137.3429 | 155.3316 | 137.9118 | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 573.1665 | - | - | - | 130.8018 | 148.86 | 131.2201 | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 573.1665 | - | - | 106.0193 | 139.1132 | 157.2991 | 138.4293 | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | CARTWHEEL_CON | 138 | 138 | Branch Amp | 573.1665 | - | - | - | 112.572 | 126.3114 | 113.0022 | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | COMMERCE-ROYSE SW 138 KV B (SINGLE B TO B) 23 R985 | 138 | 138 | Branch Amp | 573.1665 | - | - | - | - | 103.7171 | - | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 573.1665 | - | - | - | 104.1325 | 113.5495 | 101.5817 | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | L_001697SULSP_SS1_5-888847CARTWHEEL_POIC1 | 138 | 138 | Branch Amp | 573.1665 | - | - | - | 112.2931 | 125.9186 | 112.5737 | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | L_001816COMM_SW_8-001818SCTBRCH1_9C1 | 138 | 138 | Branch Amp | 573.1665 | - | - | - | - | 104.3473 | - | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | L_001818SCTBRCH1_9-001824NEYLNDVL1_9C1 | 138 | 138 | Branch Amp | 573.1665 | - | - | - | - | 103.9595 | - | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | L_001824NEYLNDVL1_9-001827CADMLX_T8C1 | 138 | 138 | Branch Amp | 573.1665 | - | - | - | - | 103.9599 | - | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | L_001827CADMLX_T8-001831CADMHW66_8C1 | 138 | 138 | Branch Amp | 573.1665 | - | - | - | - | 103.9741 | - | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | L_001829BURROW_T8-001837INGLE_8C1 | 138 | 138 | Branch Amp | 573.1665 | - | - | - | - | 102.5957 | - | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | L_001831CADMHW66_8-001837INGLE_8C1 | 138 | 138 | Branch Amp | 573.1665 | - | - | - | - | 103.9576 | - | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | L_888847CARTWHEEL_POI-002464CASHSW_T5C1 | 138 | 138 | Branch Amp | 573.1665 | - | - | - | 113.6422 | 127.4864 | 113.9021 | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | PARIS SW-PACIFIC SW/VALLEY S SW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 573.1665 | - | - | - | 102.2017 | 112.9108 | 103.1171 | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 573.1665 | - | - | - | - | 107.1876 | - | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 573.1665 | - | - | - | - | 104.444 | - | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | VALLEY S-VALLEY SW 345 KV & VALLEY S-PARIS SW 345 KV | 138 | 138 | Branch Amp | 573.1665 | - | - | - | - | 101.2259 | - | -
TRAYBN | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | QUINL_RC ( 6884) -> NQUIN_RC ( 6883) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 573.1665 | - | - | - | 109.8916 | 122.4013 | 110.5912 | -
TAEPTC | COAST | COAST | COAST, COAST | RADIANT7A ( 8715) -> COBRA7A ( 8728) CKT 1 | E5DVA1C1_1_B | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | - | 115.3083 | -
TAEPTC | COAST | COAST | COAST, COAST | RADIANT7A ( 8715) -> COBRA7A ( 8728) CKT 1 | E5DVA1C1_1_B_2 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | - | 105.5744 | -
TAEPTC | COAST | COAST | COAST, COAST | RADIANT7A ( 8715) -> COBRA7A ( 8728) CKT 1 | G8DVA1C1_B | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | - | 109.5212 | -
TAEPTC | COAST | COAST | COAST, COAST | RADIANT7A ( 8715) -> COBRA7A ( 8728) CKT 1 | Haber - Coleto Creek | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | - | 118.2387 | -
TAEPTC | COAST | COAST | COAST, COAST | RADIANT7A ( 8715) -> COBRA7A ( 8728) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | - | 101.8943 | -
TAEPTC | COAST | COAST | COAST, COAST | RADIANT7A ( 8715) -> COBRA7A ( 8728) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | - | 105.2493 | -
TAEPTC | COAST | COAST | COAST, COAST | RADIANT7A ( 8715) -> COBRA7A ( 8728) CKT 1 | P7-1_E1>>T1827GX_ERC | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | - | 103.4055 | -
TAEPTC | COAST | COAST | COAST, COAST | RADIANT7A (8715) -> COBRA7A (8728) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1780.5816 | - | - | - | 107.9277 | 146.9865 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | 3WT_002285CARMICHL_5_002888CARMICHL_8_012288CARMICHL_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | 102.8236 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | CARMICHAEL BEND-TIMBERVIEW 345 KV*DECORDOVA-CLEBURNE 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | 105.939 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | CLEBURNE-DECORDOVA 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | 105.677 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | CLEBURNE-DECORDOVA/BURLESON 138 KV (DOUBLE B TO B) B WILSHIRE | 138 | 138 | Branch Amp | 861.8416 | - | 110.1854 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | KEMP RANCH - SARDIS 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | 100.435 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | KEMP RANCH - SARDIS 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | 100.435 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | KEMP RANCH - SOAP CREEK / SARDIS 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | 102.3604 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_000237BLANTON-888875THRESLR_POIC1 | 138 | 138 | Branch Amp | 861.8416 | - | 103.6469 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_000237BLANTON-888889MIDPOINT_POIC1 | 138 | 138 | Branch Amp | 861.8416 | - | 103.368 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_001303FORBESRD_8-001905GRIFFTH_P8C1 | 138 | 138 | Branch Amp | 861.8416 | 105.7065 | 146.6051 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_001895MITCHBND2_5-002285CARMICHL_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | 102.2019 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_001905GRIFFTH_P8-002297ALVARADO1_8C1 | 138 | 138 | Branch Amp | 861.8416 | 114.0913 | 150.8047 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_002279CLEBRNSW_8-002280CLEBRN_N_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | 105.6864 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_002279CLEBRNSW_8-002290CLEBRN_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | 102.5461 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_002279CLEBRNSW_8-002294KEENE_8C1 | 138 | 138 | Branch Amp | 861.8416 | 122.0584 | 141.5405 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_002280CLEBRN_N_8-002283AIRLIQD_P8C1 | 138 | 138 | Branch Amp | 861.8416 | 104.1448 | 107.5279 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_002281GODLEY_8-002283AIRLIQD_P8C1 | 138 | 138 | Branch Amp | 861.8416 | 107.0885 | 110.6815 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_002281GODLEY_8-002888CARMICHL_8C1 | 138 | 138 | Branch Amp | 861.8416 | 107.1466 | 110.6423 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_002290CLEBRN_8-002291CLEBRN_W_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | 103.6111 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_002291CLEBRN_W_8-037810TNHILL_CO_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | 103.0858 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_002294KEENE_8-002297ALVARADO1_8C1 | 138 | 138 | Branch Amp | 861.8416 | 114.8835 | 140.0703 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | 138 | Branch Amp | 861.8416 | - | 100.5051 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_003518BLUMPUMP1_8-037810TNHILL_CO_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | 103.2079 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_003522HILLBORO1_8-003546WHITNEY__8C1 | 138 | 138 | Branch Amp | 861.8416 | - | 106.9354 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_003533FILE_SIN1_T9-003537GRANDVEW1_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | 100.1709 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_888875THRESLR_POI-003522HILLBORO1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | 103.596 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | L_888889MIDPOINT_POI-003518BLUMPUMP1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | 103.3822 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | 102.597 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 861.8416 | - | 102.5596 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-1-2 | 138 | 138 | Branch Amp | 861.8416 | - | 102.2323 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-1 | 138 | 138 | Branch Amp | 861.8416 | - | 102.2241 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-2 | 138 | 138 | Branch Amp | 861.8416 | - | 102.2323 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | NEW-HILLSBORO-CLEBURNE_SW_8 (SINGLE B TO B )-1-1 | 138 | 138 | Branch Amp | 861.8416 | - | 102.2241 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | SOAP CREEK - CEDAR HILL / SARDIS 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | 104.1234 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | THRESLR_CON | 138 | 138 | Branch Amp | 861.8416 | - | 103.6554 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT ( 442) -> FORBESRD_8 ( 1303) CKT 1 | VENUS-JOHNSON 345KV/DECORDOVA-CLEBURNE 138KV (DOUBLE B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | 101.5743 | 106.3586 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT (442) -> FORBESRD_8 (1303) CKT 1 | Pre-contingency | 138 | 138 | Amps | 861.8416 | - | - | 104.3036 | 118.3875 | 116.2392 | 122.6855 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RAILPORT (442) -> VENUS (1908) CKT 1 | Pre-contingency | 138 | 138 | Amps | 895.3112 | - | - | 101.6627 | 115.1024 | 112.9901 | 119.2064 | -
TONCOR | WEST | WEST | WEST, WEST | RANGER_5 (10049) -> RANGESTR (500199) CKT 1 | 3WT_010049RANGER_5_010050RANGER_8_010052RANGER2_3 C 2 | 345 | 1 | Branch MVA | 750 | - | 130.5929 | - | - | - | - | -
TONCOR | WEST | WEST | WEST, WEST | RANGER_5 (10049) -> RANGESTR (500200) CKT 2 | 3WT_010049RANGER_5_010050RANGER_8_010051RANGER1_3 C 1 | 345 | 1 | Branch MVA | 750 | - | 130.5702 | - | - | - | - | -
TONCOR | WEST | WEST | WEST, WEST | RANGER_8 (10050) -> BARBER_LK1_8 ( 1189) CKT 1 | L_010050RANGER_8-011393FRONTIER_P8C1 | 138 | 138 | Branch Amp | 2568.79 | 106.1576 | 155.904 | 116.7179 | 127.7198 | 127.9908 | 128.3315 | -
TONCOR | WEST | WEST | WEST, WEST | RANGER_8 (10050) -> FRONTIER_P8 (11393) CKT 1 | L_001189BARBER_LK1_8-010050RANGER_8C1 | 138 | 138 | Branch Amp | 2568.79 | 106.4239 | 155.6549 | 117.0375 | 128.0836 | 128.32 | 128.7178 | -
TONCOR | WEST | WEST | WEST, WEST | RANGER_8 (10050) -> FRONTIER_P8 (11393) CKT 1 | L_001190BARBER_LK2_8-011393FRONTIER_P8C1 | 138 | 138 | Branch Amp | 2568.79 | - | 125.668 | - | - | - | - | -
TONCOR | WEST | WEST | WEST, WEST | RANGESTR (500199) -> RANGER_8 (10050) CKT 1 | 3WT_010049RANGER_5_010050RANGER_8_010052RANGER2_3 C 2 | 138 | 1 | Branch MVA | 750 | - | 118.1157 | - | - | - | - | -
TONCOR | WEST | WEST | WEST, WEST | RANGESTR (500200) -> RANGER_8 (10050) CKT 2 | 3WT_010049RANGER_5_010050RANGER_8_010051RANGER1_3 C 1 | 138 | 1 | Branch MVA | 750 | - | 118.0909 | - | - | - | - | -
TSTEC | COAST | COAST | COAST, COAST | RAYBURN8 ( 5502) -> FORCORNERSB8 ( 5730) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 799.0861 | - | - | - | - | 100.4808 | - | -
TSTEC | COAST | COAST | COAST, COAST | RAYBURN8 ( 5502) -> FORCORNERSB8 ( 5730) CKT 1 | L_005502RAYBURN8-005680LOOP463SUB8C1 | 138 | 138 | Branch Amp | 799.0861 | - | - | - | - | 102.3188 | - | -
TSTEC | COAST | COAST | COAST, COAST | RAYBURN8 ( 5502) -> FORCORNERSB8 ( 5730) CKT 1 | L_005680LOOP463SUB8-008172VICTORIA4AC1 | 138 | 138 | Branch Amp | 799.0861 | - | - | - | - | 100.2181 | - | -
TSTEC | COAST | COAST | COAST, COAST | RAYBURN8 (5502) -> FURHMANSW8 (5506) CKT 1 | Pre-contingency | 138 | 138 | Amps | 648.473 | - | - | - | - | 121.8909 | - | -
TSTEC | COAST | COAST | COAST, COAST | RAYBURN9 ( 5500) -> ALOESUB9 ( 5606) CKT 1 | L_005502RAYBURN8-005680LOOP463SUB8C1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 116.5965 | - | -
TSTEC | COAST | COAST | COAST, COAST | RAYBURN9 ( 5500) -> ALOESUB9 ( 5606) CKT 1 | L_005607WRBRTN8-008172VICTORIA4AC1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | 160.1187 | 201.489 | 145.155 | -
TSTEC | COAST | COAST | COAST, COAST | RAYBURN9 ( 5500) -> ALOESUB9 ( 5606) CKT 1 | L_005680LOOP463SUB8-008172VICTORIA4AC1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 112.9799 | - | -
TSTEC,TLCRA | COAST | SOUTHERN | COAST, SOUTHERN | RAYBURN9 ( 5500) -> L_WESER_9_1Y ( 7239) CKT 1 | L_005502RAYBURN8-005730FORCORNERSB8C1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 112.4389 | - | -
TSTEC,TLCRA | COAST | SOUTHERN | COAST, SOUTHERN | RAYBURN9 ( 5500) -> L_WESER_9_1Y ( 7239) CKT 1 | L_005728CHOATESUB8-005730FORCORNERSB8C1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 110.9422 | - | -
TSTEC,TLCRA | COAST | SOUTHERN | COAST, SOUTHERN | RAYBURN9 ( 5500) -> L_WESER_9_1Y ( 7239) CKT 1 | STECL_10131 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 111.3864 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RECCRS2_8 ( 2814) -> RECCRS1_8 ( 2813) CKT 1 | L_002482ELEVEE_E8-002819REAGAN1_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.2654 | 100.3254 | -
TSTEC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | REDGATESW9 (5780) -> MCCOOKNO1SB9 (5783) CKT 1 | Pre-contingency | 69 | 69 | Amps | 326.3284 | 100.6964 | - | - | - | - | - | -
TONCOR | EAST | EAST | EAST, EAST | REDLAND_8 ( 3319) -> HERTYTAP_8 ( 3318) CKT 1 | L_003118LUFKNSS_8-003333LUFTXFTP_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | - | 100.1898 | -
TAEPTC,TAEPTN | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | REFUGIO2A ( 8410) -> HEARDTAP2A ( 8802) CKT 1 | L_008437RINCON4B-080065MELNCRK4AC1 | 69 | 69 | Branch Amp | 744.6981 | - | - | - | - | 114.5365 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | REFUGIO4A ( 8412) -> REFUGIO2A ( 8410) CKT 1 | L_008437RINCON4B-080065MELNCRK4AC1 | 69 | 138 | Branch MVA | 90 | - | - | - | - | 106.2236 | - | -
TCNPE | COAST | COAST | COAST, COAST | RETREV_T02B8 (43172) -> LKJACK_S02_8 (42880) CKT 02 | L_888852LIATRIS_POI-044010W_A_P__POI8AC02 | 138 | 138 | Branch Amp | 2347.0542 | - | - | - | - | - | 102.2606 | -
TCNPE | COAST | COAST | COAST, COAST | RETREV_T02B8 (43172) -> LKJACK_S02_8 (42880) CKT 02 | P1-2_(42980-44010-02)-2 | 138 | 138 | Branch Amp | 2347.0542 | - | - | - | - | - | 102.2606 | -
TCNPE | COAST | COAST | COAST, COAST | RETREV_T02B8 (43172) -> LKJACK_S02_8 (42880) CKT 02 | P7-1_E1>>T2682EX1 | 138 | 138 | Branch Amp | 2347.0542 | - | - | - | - | - | 113.3127 | -
TCNPE | COAST | COAST | COAST, COAST | RETREV_T02B8 (43172) -> LKJACK_S02_8 (42880) CKT 02 | P7-1_E1>>T2682EX2 | 138 | 138 | Branch Amp | 2347.0542 | - | - | - | - | - | 114.2799 | -
TCNPE | COAST | COAST | COAST, COAST | RETREV_T02B8 (43172) -> LKJACK_S02_8 (42880) CKT 02 | P7-1_E1>>T2682GY1 | 138 | 138 | Branch Amp | 2347.0542 | - | - | - | - | - | 114.3784 | -
TCNPE | COAST | COAST | COAST, COAST | RETREV_T02B8 (43172) -> LKJACK_S02_8 (42880) CKT 02 | P7-1_E1>>T2682GY2 | 138 | 138 | Branch Amp | 2347.0542 | - | - | - | - | - | 114.378 | -
TCNPE | COAST | COAST | COAST, COAST | RETREV_T02B8 (43172) -> LKJACK_S02_8 (42880) CKT 02 | P7-1_E1>T2682DX | 138 | 138 | Branch Amp | 2347.0542 | - | - | - | - | - | 106.2735 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RICHLAND1_9 ( 3486) -> NAVARRO1_9 ( 3479) CKT 1 | L_003597GROESBECP_8-888888FEWELL_S1C1 | 69 | 69 | Branch Amp | 292.8588 | - | - | - | 103.7021 | 218.3897 | 184.9404 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | RICHLAND1_9 ( 3486) -> WRTHMPOD_9 ( 3487) CKT 1 | L_003632MEXIA2_1_8-003634GROES_SE1_8C1 | 69 | 69 | Branch Amp | 292.8588 | 133.1584 | - | 133.4049 | 133.7845 | 133.0521 | 133.7843 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | 3WT_013125TDADTMOD_5_003127TRINIDAD_8_120151TRSES_UNIT6 C 1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 103.087 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 147.1515 | - | 142.1292 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 136.356 | - | 135.105 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 114.803 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 112.9852 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 110.4401 | - | 113.5748 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 126.3556 | - | 140.3956 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 111.0338 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 103.0681 | - | 103.8452 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.2 | - | 103.4055 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | E_FRNYPP_CC1_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.8495 | - | 102.9916 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | E_FRNYPP_CC2_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.8553 | - | 102.9898 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | E_PANDA_S_CC1_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.3261 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | E_TGCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 105.458 | - | 109.6187 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 108.9437 | - | 112.3055 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.4965 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | G_003321REDLAND_5UN1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 104.3403 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | G_003478NAVARRO1_8US1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.2714 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | G_120041MLSES_UNIT1UL1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.4083 | - | 106.868 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | G_120042MLSES_UNIT2UL2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.5312 | - | 106.8602 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | G_120043MLSES_UNIT3UL3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.5538 | - | 106.93 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | G_120142SCSES_UNIT2UN2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 102.214 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | G_120151TRSES_UNIT6UN6 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 103.087 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | G_150092LH2SES_UNIT2UN2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.0774 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | G_5920EASTDCTIE | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.1943 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | GLASGOW_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 108.6008 | - | 111.6878 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | JEWETT-BALE*TWINOAK_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.5767 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.0763 | - | 103.1288 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.3261 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.5158 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.8295 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.9889 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_001906VENUS_S5-888857OYSTER_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 104.6881 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_001907VENUS_N5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 104.7436 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 110.4401 | - | 113.5748 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 108.9437 | - | 112.3055 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.9048 | - | 106.8973 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.8495 | - | 102.9916 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.8553 | - | 102.9898 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 109.1572 | - | 112.5273 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_003116MTENTRPR_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 109.0243 | - | 115.6623 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.7587 | - | 106.8342 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 107.5759 | - | 111.3488 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.1886 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_003377LITTLEPOND_5-003687BELL_E_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 101.4242 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_003377LITTLEPOND_5-003704HOGCREEK_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.4046 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 125.8049 | - | 140.3657 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_003381BIGBRNW_5-003391JEWETT_N5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.9417 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_003384STJOHNS_5-003409LAKE_CRK1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 105.6942 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_003384STJOHNS_5-003711BALE_S5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 104.1338 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_003390JEWETT_S5-003711BALE_S5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.714 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_003490LNGPRAIRIE_8-152736FENCESLR_8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 101.5583 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_003687BELL_E_5-003705BRANGUS_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 101.7934 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_003705BRANGUS_5-003706GIBSON_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.8559 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.4811 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.2975 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.6047 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_888857OYSTER_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 103.288 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 106.9878 | - | 110.7581 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | LAKE CREEK - LAKE HALL/TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.3628 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | LAKE CREEK-RATTLESNAKE/ST JOHNS_5 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 105.6943 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | LATIMER_REATA_P7F1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.432 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 102.1718 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 101.5576 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 101.522 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 108.747 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | ML-SK*ME-TR (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 108.1087 | - | 114.648 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.0348 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | OYSTER_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 103.9149 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | P7-1_E1>>T6472CX1A | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 101.9155 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | P7-1_E1>>T6472CX1B | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 101.5524 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | P7-1_E1>>T6472E | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 101.0586 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.0031 | - | 102.185 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 101.2646 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 103.9655 | - | 105.7784 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 107.0225 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | TRIN-SK*ME (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.2485 | - | 110.1799 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 104.893 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 104.8869 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 105.1322 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 101.6596 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.3051 | - | 106.2404 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 103.435 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 107.5594 | - | 116.3659 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 114.6461 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.1715 | - | - | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.414 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.6469 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | VENUS-NAVARRO 345 KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 105.71 | - | - | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 101.1137 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 101.4757 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | WSHACK_LATIMER_P7 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.7986 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | XFMR-LKHB_2T8-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 100.0774 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | XFMR-MARTINLK_5-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.4083 | - | 106.868 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | XFMR-MARTINLK_5-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.5312 | - | 106.8602 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | XFMR-MARTINLK_5-3 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.5538 | - | 106.93 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | XFMR-MTENTRPR_5G-4 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 102.7694 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND1_5 ( 3134) -> TRINDAD2_5 ( 3124) CKT 1 | XFMR-STRYKER_8-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | - | 102.214 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND2_5 ( 3133) -> TRINDAD1_5 ( 3123) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 114.4812 | - | 100.5758 | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND2_5 ( 3133) -> TRINDAD1_5 ( 3123) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 106.0414 | - | - | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND2_5 ( 3133) -> TRINDAD1_5 ( 3123) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.112 | - | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND2_5 ( 3133) -> TRINDAD1_5 ( 3123) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.9555 | - | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND2_5 ( 3133) -> TRINDAD1_5 ( 3123) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.112 | - | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND2_5 ( 3133) -> TRINDAD1_5 ( 3123) CKT 1 | L_003109STRYKER_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.5048 | - | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND2_5 ( 3133) -> TRINDAD1_5 ( 3123) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.7848 | - | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND2_5 ( 3133) -> TRINDAD1_5 ( 3123) CKT 1 | L_003381BIGBRNW_5-068091NAVARROC2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.7681 | - | -
TONCOR | EAST | EAST | EAST, EAST | RICHLND2_5 ( 3133) -> TRINDAD1_5 ( 3123) CKT 1 | TRIN-SK*ME (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 106.441 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | 3WT_003402LAKE_CRK2_5_003410LAKE_CRK1_8_013410LAKE_CRK1_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.366 | 102.8196 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | 3WT_003406ELM_MOTT__5_003407ELM_MOTT__8_013406ELM_MOTT_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.832 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | 3WT_003409LAKE_CRK1_5_003410LAKE_CRK1_8_013402LAKE_CRK2_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7541 | 100.1481 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | 3WT_003412TEMP_PEC__5_003420TEMP_PEC__8_013420TEMP_PEC__3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5431 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | 3WT_003414TEMP_SS__5_013415TEMP_SS_R_8_013414TEMP_SS__3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8952 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | AEN_FPP-HO¦LY | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2748 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | AEN_LP-AU¦DL_2013 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.7039 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | AEN_LY-FPP:CIS-HO | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0047 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | AEN_LY-FPP¦CIS | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.555 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | AEN_P1-1_GEN_SH5A+5C | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.9476 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | AEN_P2HLJ345_RB_570_610_1(94OF224): | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0776 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.6856 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | AEN_P7 FPP-LP.DC_1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3353 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | AEN_P7 FPP-LP.DC_2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3532 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW - PLANO TENNYSON 345 KV & ALLEN SW - RENNER 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1518 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW 345-138 KV AUTO #1 (SINGLE AUTO) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.087 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4199 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3926 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0319 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4033 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0399 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4653 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1493 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5431 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2945 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4777 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1586 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5556 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3043 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1091 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.8999 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1217 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.9035 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLEN-MOSES 345-138 AUTO-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4611 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1069 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8674 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1796 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8925 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ANNA SW - VALLEY SOUTH 345 KV & ANNA SW - FARMERSVILLE 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0383 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ARGENTA_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.1722 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ASP_WRG_L1F1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.408 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ASP_WRG_P7F2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5445 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | BAS_RANCH_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 110.2089 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | - | 105.0753 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | - | 103.9337 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 107.9593 | 136.7126 | 126.2969 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 104.2326 | 133.8927 | 123.4517 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.1125 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | BEPC_205 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.489 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | BEPC_211 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9546 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | BEPC_22 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3426 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | BEPC_23_2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.692 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | BEPC_230_4 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2182 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | BEPC_311_2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0026 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.7594 | 100.2989 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | BIGBRN__5-JEWETT_S5 & BIGBRN__5-JEWETT_N5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.056 | 101.5999 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.0535 | 102.5477 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | BITTER CREEK SW (LCRA) - CATTLEMEN SW & BITTER CREEK SW (LCRA) - SWEETWATER EAST 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6305 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | BLUBIRD_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.155 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 100.1779 | 129.8574 | 120.3459 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | CACTUS_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8082 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | CARLSON - STEGER (LCRA)_8 (SINGLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1963 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | CHINA GROVE SW - AEP PAINT CREEK 138 KV & GRAHAM SES - TONKAWA/COOKFIELD/LONGCREEK 345 KV (DOUBLE B TO B) 2019 SUM - FUTURE-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0476 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | DERMOTT - KIRCHHOF CKT 1 & DERMOTT - KIRCHHOF CKT 2 345 KV (DOUBLE B TO B) C | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.8669 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | DERMOTT - KIRCHHOF CKT 1 345 KV WIN 2023 - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7532 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | DRY_CREEK_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.6573 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | DUNE - WINK/YUKON 138 KV 2019 SUM - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5505 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | DVCPA1C21B_1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.182 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | DVCPA1C21B_2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.7896 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_AMOCOOIL_CC2_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8374 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_AMOCOOIL_CC2_TRAIN_NSO | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1057 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_B_DAVIS_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.7197 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_BASTEN_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.502 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_BOSQUESW_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.093 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_BOSQUESW_CC2_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.3053 | 101.2266 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_BRAUNIG_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.0399 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_BTE_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0788 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_BVE_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0155 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_BYU_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0795 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_CBECII_CC3_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.9307 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_CBY4_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6508 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_CCEC_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.8946 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_CHE_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1094 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_CVC_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0762 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_DDPEC_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.201 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_DUKE_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.4715 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_ETCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0117 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_FERGCC_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.2676 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_FLCNS_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3436 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_FREC_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1515 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_FREC_CC2_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6858 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_FRNYPP_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.9897 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_FRNYPP_CC2_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.0061 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_FTR_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3855 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_GUADG_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.4852 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_GUADG_CC2_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.4484 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_INGLCOSW_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.0318 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_JACKCNTY_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.1128 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_JCKCNTY2_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.6802 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_KMCHI_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.6729 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_KMCHI_CC2_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.6977 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_LGE_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.6561 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_LOSTPI_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.8121 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_LPCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.2068 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_LPCCS_CC2_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.9574 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_NEDIN_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.6742 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_NUECES_B_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.8692 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_OECCS_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.8213 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_OECCS_CC2_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.836 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_PANDA_S_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.6147 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_PANDA_T1_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.4346 | 100.3627 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_PANDA_T2_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.4992 | 100.3943 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_PSA_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5775 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_PSG_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.681 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_QALSW_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2516 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_QALSW_CC2_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2163 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_RAYBURN_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3808 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_TEN_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2174 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_TGCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9271 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_THW_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0384 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_THW_CC2_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0384 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_TNSKA_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3082 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_TXCTY_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2836 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_VICTORIA_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3644 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_WCPP_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.1089 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_WHCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.773 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E_WHCCS2_CC2_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.0052 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E5DVA1C1_1_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | - | 101.7524 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | E5DVA1C1_1_B_2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | - | 100.0189 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7415 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ELM_MOTT_138_69_KV_AUTO (SINGLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7376 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ELMAX_POI_Con | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7009 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ELPATR_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0752 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4827 | 100.0761 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4503 | 100.2154 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ENNIS - PEBBLE CREEK 138 KV SWITCH (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2961 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ERIKA_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5497 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_000099BENHURUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4848 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_000575JCKCNTY5UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.0509 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_000579JCKCNTY8UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.5959 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_001877MITCHBND_5UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3038 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_003306STEKLY_DAM_5US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4943 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_003420TEMP_PEC__8US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1364 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_003706GIBSON_5US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1278 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_003717TORTOISE_5US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5463 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_003717TORTOISE_5US2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1201 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_006100OKLA7AUC0 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.3852 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_006111RILEY7BUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4909 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_007041L_JOHNDU5_1YUN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8933 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_007044L_MARION5_1YUN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.1831 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_007048L_GARFIE5_1YUN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.5648 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_008249ANGSTRM7AUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8966 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_008573BONILLA7AUW1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8838 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_008707DRYFRIOUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2009 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_010012METEOR_5US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.2177 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_023906AJSWOPE_5US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3041 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_023908DEAFSMITH_5US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3078 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_023909WALLABY_5US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.9854 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_023912OGALLALA_5US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3077 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_023913KRESS_5US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2068 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_040000CEDARP_B345AUC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3109 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_040700GRNBYU__B345UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.463 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_040710GRNBYU_POI8AUN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4956 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_043060SPEDWY_POI_5US2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4831 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_043060SPEDWY_POI_5US4 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1868 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_043340GLFTIE_POI_8UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5742 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_043990ELMATO_POI_5US2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9361 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_045500T_H_W__POI_5UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4882 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_045515T_H_W__POI_8UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.514 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_048262SOWYCK26TP_8UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0126 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_059904COTTONWOODUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2502 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_060700GAUSS7AUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7121 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_060716SGSA4AUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1889 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_068004PHNTMHLUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2686 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_068014OPENSKYUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2086 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_068025WRANGLERUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2451 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_068051REATAUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.577 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_079000GRAYUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.1075 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_079000GRAYUW1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.829 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_080039LUCERO7AUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3556 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_080039LUCERO7AUS2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9741 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_080219LOBO7AUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1564 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_080219LOBO7AUS2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3643 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_080355DELSOL7AUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4163 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_085000N_SHARPE7AUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0741 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_110014WAP_WAP_G4UN4 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8273 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_110015WAP_WAP_G5UL5 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3173 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_110016WAP_WAP_G6UL6 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4156 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_110017WAP_WAP_G7UL7 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0907 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_110018WAP_WAP_G8UL8 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2064 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_110071CBY_CBY_G1UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4766 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_110072CBY_CBY_G2UN2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5096 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_110351STP_STP_G1UU1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.5795 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_110352STP_STP_G2UU2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.5043 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_112351OLDHCKRY_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1415 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_113051GARCITAS_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3255 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_113111LUNIS_CK_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.6432 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_113921PARLIMNT_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0423 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_120041MLSES_UNIT1UL1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9612 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_120042MLSES_UNIT2UL2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0105 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_120043MLSES_UNIT3UL3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.055 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_120131OGSES_UNIT1AUL1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0242 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_120132OGSES_UNIT2UL2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0263 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_132311ECEC_G1UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3306 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_132312ECEC_G2UN2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3306 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_132481RIGGINS_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1486 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_132781CASLGP_UNIT1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2795 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_132941SPTX12B_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1322 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_133841WAYMARK_W1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2815 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_134091OBERON_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2638 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_134141JUNO_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0756 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_134751FOWLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1032 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_134801PROSPERO_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0695 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_134951EUNICE_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3009 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_134953EUNICE_S2US2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5999 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_135111ARAGORN_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3499 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_135321REDBARN_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5387 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_135501RDOSLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3646 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_136341TRBNT_PV_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1781 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_136441SWIFTAIR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0669 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_141607AEEC_5UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6445 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_141609ELK_G3UN6 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5024 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_143116SRNOVA2_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2679 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_143961MISAE2_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.1157 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_144011BRSFORK_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8175 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_144064INERTIA_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2435 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_144161NOVA2SLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2359 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_144211HRNTSLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.5471 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_144261EIFSLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0605 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_144311FRYE_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4522 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_144312FRYE_S2US2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4522 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_144561BAKE_SLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0664 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_144562BAKE_SLR_S2US2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0664 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150023MCSES_UNIT8UN8 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.2434 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150041GRSES_UNIT1UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8663 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150042GRSES_UNIT2UN2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.065 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150051HLSES_UNIT3UN3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.8821 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150052HLSES_UNIT4UN4 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.3682 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150053HLSES_UNIT5UN5 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.3706 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150091LHSES_UNIT1UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.6468 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150092LH2SES_UNIT2UN2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.5883 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150101LEG_LEG_G1UL1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8642 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150102LEG_LEG_G2UL2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9088 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150111CPSES_UNIT1UU1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.3305 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150112CPSES_UNIT2UU2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.3095 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150133MIL_MILLERG3UN3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.632 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150151MDANP_CT1UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.748 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150152MDANP_CT2UN2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8601 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150153MDANP_CT3UN3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9119 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150154MDANP_CT4UN4 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9112 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150155MDANP_CT5UN5 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8323 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150156MDANP_CT6UN6 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8458 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_150741SCES_UNIT1UL1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 113.2269 | 105.2575 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_151701CROWN_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9742 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_151751RADN_SLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0837 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_151752RADN_SLR_S2US2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1093 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_152031GOLINDA_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9644 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_152131ROSELAND_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0345 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_152181SUNVASLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3348 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_152231MARKUM_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6659 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_152331FILESSLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0625 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_152431MERCURY_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7647 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_153141PORT_SLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3967 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_153241ANGUSSLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1776 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_153291BIGELM_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1586 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_153381FIVEWLLS_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.455 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_153631DORADO_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4644 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_153731TNS_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0645 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_153732TNS_S2US2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0656 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_153781JAGUARSP_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0854 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_153861TOKIO_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7787 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_153911PNGT1_PV_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.9422 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_154061DIVER_PV_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3945 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_154161LANGER_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5403 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_154221ASHCRKSL_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4622 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_154281CLINGHAM_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.6604 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_154331CMPDREPV_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.888 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_160101B_D_B_DAVIG1UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.8857 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_160131SAN_SANMIGG1UL1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.5708 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_160151INGLCOS_CTG1UPE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.505 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_160152INGLCOS_CTG2UPE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.505 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_160153INGLCOSW_STGUPE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4803 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_160201LGE_LGE_GT1UPE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4029 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_160202LGE_LGE_GT2UPE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3953 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_160261CCEC_GT1UPE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2059 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_160262CCEC_GT2UPE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2059 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_160263CCEC_ST1UPE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3179 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_160391PAP1_PAP1UW1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0294 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_160392COTTON_PAP2UW1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1787 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_160741LV1_LV1AUW1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1654 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_160742LV1_LV1BUW2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.17 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_161651PATWND_UNIT1UW1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.314 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_161951STELLA_W1UW1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.139 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_162251CHALUPA_W1UW1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0178 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_162541MCLNSLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.336 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_162791HRZN_SLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3135 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_163021NEBULA_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0353 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_163221CORAZON_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3514 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_163321SPARTA_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0132 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_163521PEREGRN_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2813 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_163641CHARGER_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.034 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_163691REDONDA_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8268 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_163881TULSITA_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.827 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_163931OUTPOST_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.5222 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_170071GID_GIDEONG1UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2853 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_170072GID_GIDEONG2UN2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.309 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_170073GID_GIDEONG3UN3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.268 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_170101FPPYD_FPP_G1UL1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.9917 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_170102FPPYD_FPP_G2UL2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.9398 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_170103FPPYD_FPP_G3UL3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.5996 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_170126CALAVER_JKS2UL2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.8589 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_170191HAY_HAYSENG1UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0553 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_170192HAY_HAYSENG2UN2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2213 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_170193HAY_HAYSENG3UN3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2124 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_170194HAY_HAYSENG4UN4 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0817 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_170521E_BLACK_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1896 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_170671CACHENA_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.977 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_170821EBELLSLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2102 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_170901SHLA_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.109 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_170951SHLA_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.109 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_171021AURE_SLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2213 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_171091MPP_N1UN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8208 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_171111MANDORLA_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3845 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_171161SYPBRNCH_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0301 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_182501RAMBLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3669 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_183172GALLOWAY_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6979 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_183351RATLIFF_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0598 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_183401JADE_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0177 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_183402JADE_S2US2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0419 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_183451CROWDEDS_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3672 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_183521ANDMDSLR_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0133 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_183522ANDMDSLR_S2US2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0358 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_183571SUNRAY_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3484 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_183621ZIER_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1185 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_183781ANG_PV_S1US1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3392 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_5920EASTDCTIE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4693 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_6103NORTHDCTIE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6978 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888838GRAPHIC_GAS_POIUN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0164 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888839BAS_RANCH_POIUC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 110.2063 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888841ELMAX_POIUN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.695 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888851TRIFECTA_POIUN1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.0643 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888854PINEFOREST_POIUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4847 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888856HOLLY_POIUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.6575 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888856HOLLY_POIUS2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6536 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888857OYSTER_POIUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1103 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888858ARGENTA_POIUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3804 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888859HIGHNOON_POIUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.611 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888865MALDIVES_POIUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3669 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888866HANSON_POIUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7234 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888870BTTM_GRSS_POIUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3581 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888871ELPATR_POIUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0718 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888874VIKING_POIUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6885 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888879BLUBIRD_POIUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.0422 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888881SOLAC_POIUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3481 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888882BUZIOS_POIUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5148 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888883QUANT_POIUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2187 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_888885GALAC_POIUS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0718 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G_RIO_TRAIN | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.6252 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | G8DVA1C1_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | - | 100.7019 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | GALAC_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.24 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | GLASGOW_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.2644 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | GRAHAM UNIT 2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.065 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | GreenRD Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4244 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | HANSON_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7658 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | HILLSBORO-ASH CREEK 138 KV (SINGLE B TO B) B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2397 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | HOLLY_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.0036 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | IRON_BELT_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0533 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | J5CT1_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5119 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | J5CT2_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5065 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | J5CT3_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5083 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | J5GSU1_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5119 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | J5GSU2_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5065 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | J5GSU3_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5083 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | J5GSU4_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.8777 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | J5LCA1C1_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.6296 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | J5ST1_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.8777 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | JEWETT - RANCHLAND (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8809 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | JEWETT-BALE*TWINOAK_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.5571 | 104.5087 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | JEWETT-ROBERTSON (BEC)_8 (SINGLE B TO B) B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.489 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | JEW-LONG_LAKE-PAL_S_8 (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5465 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000032ROBERTSON-000037RIDGEC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.55 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000032ROBERTSON-003707CANNON_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3781 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000033WATSONCHPL-000037RIDGEC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5647 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000033WATSONCHPL-000042TIMBERCSTC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1274 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000041SKIPPER-000042TIMBERCSTC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3363 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000041SKIPPER-003394JEWETTA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4118 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000064MILANO-003683MINERVA1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.266 | 100.2329 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000064MILANO-003707CANNON_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.2944 | 100.2565 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000092PERRY9-000099BENHURC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3886 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000120TALBRTRIDG-003678ROCKDALE1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.828 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000120TALBRTRIDG-003683MINERVA1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.8741 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.6528 | 100.2211 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.6886 | 100.25 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000212WINKLER-003127TRINIDAD_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0404 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000212WINKLER-003510PINOAK_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1573 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000221TRUMBULL8-002229PEBBLCRK_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0475 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000221TRUMBULL8-012344GAMMA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3578 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000234CHATT-003352PECANST_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3035 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000234CHATT-003522HILLBORO1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1849 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000842GPL_KINGMTSW-000843GPL_KINGMTTPC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.8433 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.9149 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_000860GPL_GIRVINSW-136341TRBNT_PV_S1C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1781 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.2253 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_001141HOLTSS_8-132313ECEC_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.6516 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_001163LAMESA_8-132883LMESASLR_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0499 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_001444BROWN_5-151756RADN_TLINEC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1923 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.8222 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4651 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_001730W_KRUM_5-152087NOBLESLR_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7201 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.593 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.9099 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_001906VENUS_S5-888857OYSTER_POIC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.8836 | 100.7703 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.9304 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_001907VENUS_N5-068091NAVARROC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.0141 | 100.9336 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.7594 | 100.2989 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4827 | 100.0761 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1892 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1511 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4099 | 100.0224 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.3269 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7452 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7452 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.9766 | 101.1444 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.593 | 103.2725 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002432TRICRN1_5-888878ERIKA_POIC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0277 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.0121 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.9946 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002461ROYSE_N5-002513ALLENSW1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1024 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4867 | 100.1199 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002478ROYSE_S5-002485POETRY_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3605 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002726KEMP_S_8-002774KNGCRK_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4671 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_002726KEMP_S_8-003264SEVENPTS_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5816 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003100MARTINLK_5-003102TYLERGND_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4749 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7487 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003109STRYKER_5-003123TRINDAD1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9268 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003118LUFKNSS_8-003349TMPLINLA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7312 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4665 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003127TRINIDAD_8-003260NIPAKTAP_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003133RICHLND2_5-003199CALFRESTN_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6872 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003134RICHLND1_5-003186CALPFREST_5C2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1583 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.2374 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003260NIPAKTAP_8-003265MANKIN_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7975 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003262CEDRCREK_8-003263CEDRCKPU_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7445 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003262CEDRCREK_8-003287WILL_WHT_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7185 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003263CEDRCKPU_8-003265MANKIN_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7674 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003264SEVENPTS_8-003287WILL_WHT_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6801 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003278LAKEVIEW_8-003279LONGLKTA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0432 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003283BUTLERMT_P8-003394JEWETTA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1444 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003352PECANST_8-003473ASHCREEK_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3254 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003355GRPLMGTA_8-013354CROCKETT_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0748 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003355GRPLMGTA_8-888861LEON_POIC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1991 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003377LITTLEPOND_5-003687BELL_E_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.6747 | 104.8605 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003377LITTLEPOND_5-003704HOGCREEK_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.9113 | 103.1928 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.8879 | 100.386 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003381BIGBRNW_5-003391JEWETT_N5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.2262 | 100.4413 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003381BIGBRNW_5-068091NAVARROC2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0499 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003384STJOHNS_5-003409LAKE_CRK1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 118.6089 | 115.2193 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003384STJOHNS_5-003711BALE_S5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 115.113 | 112.1236 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003385COWBAYOU_8-151703CROWN_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8888 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003385COWBAYOU_8-152033GOLINDA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8884 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003386OUTLAW_5-046020LIMEST_POI_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.1512 | 100.0994 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003386OUTLAW_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.8495 | 100.9093 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003389FORTSMITH_5-152333FILESSLR_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0524 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003390JEWETT_S5-003711BALE_S5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.7337 | 105.2174 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003394JEWETTA_8-003501SEATEAG_T_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6431 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003400TWIN_OAK_N5-039950TNTNP_ONE_3C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0073 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003400TWIN_OAK_N5-039950TNTNP_ONE_3C2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0073 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003400TWIN_OAK_N5-888846TIDWELL_POIC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0837 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003400TWIN_OAK_N5-888846TIDWELL_POIC2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0837 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003412TEMP_PEC__5-003414TEMP_SS__5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8393 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003414TEMP_SS__5-003687BELL_E_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0495 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003414TEMP_SS__5-003687BELL_E_5C2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0495 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003415TEMP_SS__8-013415TEMP_SS_R_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8952 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003487WRTHMPOD_9-003488WTXGFPOD_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1293 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003487WRTHMPOD_9-003605WORTHAM1_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.6294 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003488WTXGFPOD_9-003604WESTTXGF1_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1254 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003495BLAIN_8-003501SEATEAG_T_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.468 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003495BLAIN_8-003558RANCHLAND_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2395 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003548OILMILL_9-003637OTTO_SE1_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.2036 | 104.2355 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003548OILMILL_9-013639MARLIN_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.7618 | 100.8912 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003588GROESBECP_9-003637OTTO_SE1_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.5376 | 104.6666 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003605WORTHAM1_9-003606MEXIA2_T_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.3932 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003606MEXIA2_T_9-003614MEXIA_NO_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.8347 | 102.0841 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003606MEXIA2_T_9-013613COOLIDGE_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.457 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003613COOLG_SE1_9-013613COOLIDGE_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4535 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003632MEXIA2_1_8-003634GROES_SE1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 109.7003 | 106.9095 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003678ROCKDALE1_8-003740SLRPRTY_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3537 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003687BELL_E_5-003705BRANGUS_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.0667 | 105.4588 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003704HOGCREEK_5-039950TNTNP_ONE_3C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.7899 | 101.6259 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003705BRANGUS_5-003706GIBSON_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.849 | 103.9206 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003706GIBSON_5-039950TNTNP_ONE_3C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.2926 | 101.9685 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003711BALE_S5-153733TNS_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.074 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_003740SLRPRTY_8-003750VOSSLAKE_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5991 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.8 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.7224 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.5665 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.704 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_005380SHAULA-005915SO_TEX__345AC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.7257 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_005502RAYBURN8-005513RAYBURNPLNT8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3808 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_005761PAREDESSW8-160981CAMWIND_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0103 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_005779REDSWTAP8-005784REDGATESW8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1549 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_005779REDSWTAP8-161031REDGATE_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.1549 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_005895PEARSALLSUB8-005896MORROWSW8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.312 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_005895PEARSALLSUB8-005897HORIZONSW8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3138 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_005895PEARSALLSUB8-058959PEARSALLSCB8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8638 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_005897HORIZONSW8-162793HRZN_SLR_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3138 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4223 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7092 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_006015MADDUX4A-183353RATLIFF_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0598 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_006630FTST4A-132482RIGGINS_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1507 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.5022 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_007077L_AMOSCR5_1Y-183171GALLOWAY_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4741 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_007126L_FERGUS8_1Y-180015FERGGT1_1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7503 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_007126L_FERGUS8_1Y-180016FERGGT2_2_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7503 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_007126L_FERGUS8_1Y-180017FERGST1_1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8736 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_007270L_BELLSO8_1Y-046220PETERS__B138C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5537 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_007279L_MULDOO8_1Y-1707737RNCHSLR_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5068 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_007337L_KIMBRO8_1Y-170523E_BLACK_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1896 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_007389L_PINNAC8_1Y-135019TI_SOLAR_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9082 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_007389L_PINNAC8_1Y-135113ARAGORN_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3499 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008127LAN_CTY4A-008130LAN_CTY4BCS1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1034 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008172VICTORIA4A-110883VIC_SU5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0119 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008172VICTORIA4A-110884VIC_SU6C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2359 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008209SHAKEPOI4A-162543MCLNSLR_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3359 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008318RIOHONDO7A-162745LMJDSW_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7103 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008319RIOHONDO4A-160750LV1_AB_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4357 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008380NEDIN4A-160234NEDIN_1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0876 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008380NEDIN4A-160235NEDIN_2_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0876 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.1762 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.548 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008458B_DAVIS4A-160105B_DAVIS_1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.8858 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008458B_DAVIS4A-160106B_DAVIS_2_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.157 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008458B_DAVIS4A-160107B_DAVIS_3_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5017 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008458B_DAVIS4A-160108B_DAVIS_4_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5016 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008640KELVIN4A-088640CHLPAPOI4AC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1592 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008663ELSUZPOI7A-163415ELSAUZ_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8271 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008963HEC4A-008981HECGT14AC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3674 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008963HEC4A-008983HECST14AC3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5904 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008980FRONTERA4A-160180FRONT_EC_C1TC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7528 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008980FRONTERA4A-160181FRONT_EC_C2TC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7528 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_008980FRONTERA4A-160182FRONT_EC_STTC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8206 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_009043CISTERN-009073HOLMANC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.38 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_009043CISTERN-009074LYTTON5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7021 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.2755 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_011270DOGHOUSE_5-023876CLEARFRK_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.7642 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_011270DOGHOUSE_5-134805PROSPERO_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0128 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_011270DOGHOUSE_5-135183PRSPERO2_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6934 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_011273NELSON_8-135503RDOSLR_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3646 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_011406CENTBLUF_5-182255HOLSTN_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.368 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_011688THORNTRE_5-143625SAMSON_1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.072 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_011688THORNTRE_5-143705DELILA_1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.6676 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_012329SHANKLSW_8-012344GAMMA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3587 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_023910WINDMILL_5-140753HRFDWIND_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1291 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_023920ABERNATH_5-141607AEEC_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.1666 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_023924FARMLAND_5-133641TAHOKAW_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1957 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_038745TNATTWATER1-111971TOPAZ_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5508 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_040000CEDARP_B345A-110076CBY4_1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6508 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_040010CEDARP_B138A-049201GENGBY2_02_8CGL | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5096 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_040715GRNBYU_POI8B-049211GENGBY7_08_8CGL | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0565 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_042010P_H_R___B138-111131BAC_8C92 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1062 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_042110ANGLTN_POI_8-112597BCH_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2365 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_042570ARCHER_POI_8-112969BTM_8C01 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2634 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_044000W_A_P__POI5A-049205GENWAP6_06_5CGL | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4156 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_044000W_A_P__POI5A-049206GENWAP7_07_5CGL | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0907 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_044005W_A_P__POI5B-049207GENWAP8_08_5CGL | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2064 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_044040BAILEY_POI_5-044060BLUE___POI_5C72 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1569 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_044060BLUE___POI_5-044220JULIA__POI_5C72 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3547 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_044200HILLJE__B345-044220JULIA__POI_5C72 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4483 | 100.0064 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_044650SMTHRS_POI_5-112419RABBS_5C01 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2964 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_044880WATERH_POI_5-112878GSTAR_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5082 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_045500T_H_W__POI_5-049204GENTHW5X05_5CGL | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0549 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_045515T_H_W__POI_8-049202GENTHW3X03_8CGL | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0383 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_045515T_H_W__POI_8-049203GENTHW4X04_8CGL | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0384 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_046020LIMEST_POI_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.2265 | 100.2011 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_047170H_O_C__POI_8-111800PRO_8C01 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1938 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_059906LONGDRAW_138-134145JUNO_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9391 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_059906LONGDRAW_138-134342LGDRAW_S8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4725 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_059909NOVA_138-059998NOVA8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.9953 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_059909NOVA_138-143115NOVA1SLR_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.7907 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_059909NOVA_138-144163NOVA2SLR_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2358 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_059911MHOS-183406JADE_HI_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2027 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_060011NEBULA7A-183525ANDMDSLR_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9414 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_060383LINTERNA4A-132331REROCK_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1361 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_060393PIGCREEK4A-134245TAYGETE_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8379 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_060393PIGCREEK4A-134705TYGTEII_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4939 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_060464AZUREPOI7A-060514CLEARCRO7BC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5124 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_060504TESLA7B-142815MISAE_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4377 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_068010ROMNEY1_W-068011ASPIREC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4161 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_068011ASPIRE-068051REATAC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9181 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_068020ROMNEY1_E-068025WRANGLERC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4062 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_068090SAMSW-068092LIBERTYC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.1431 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_068092LIBERTY-152433MERCURY_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4949 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_076002L_BAKERS5_1Y-133843WAYMARK_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2815 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_076002L_BAKERS5_1Y-135327REDBARN_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.72 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_076005L_SCHNDR5_1Y-132632SANTRITA_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2298 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_076015L_CEDACA5_1Y-134512HILO_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.229 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_076040L_CASTIL8_1Y-132783CASL_GAP_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2968 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_076040L_CASTIL8_1Y-132943SPTX12B_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1762 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_076090L_DIVIDE5_1Y-180759CAPRIDG4_1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2391 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_076090L_DIVIDE5_1Y-182727AVIATOR_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.009 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_078255L_PINTCR8_1Y-183623ZIER_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1902 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_080071ZORILLO7A-080076AJO7AC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.2419 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_080071ZORILLO7A-080171SARITA7AC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4799 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_080072STELPOI7A-080076AJO7AC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1402 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_080072STELPOI7A-161953STELLA_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1396 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_080171SARITA7A-160299BAFFIN_2_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4794 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_080219LOBO7A-163223CORAZON_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8242 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_080259PELICAN4A-160394COTTON_1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1787 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_080259PELICAN4A-160395PAP1_1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0294 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_080260GILA4A-160095NUECES_B_2_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5086 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_080260GILA4A-160096NUECES_B_3_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5062 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_080309LASPULGA4A-160694REDFISH_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1897 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_080503SANTASW4A-085001N_SHARPE4AC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4361 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_080503SANTASW4A-161455CHAWIND_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4359 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_080509LADKPOI7A-161753BBREEZE_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2975 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_085008PATPOI7A-161653PATWIND_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3217 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_088173JCKSLPOI4A-163575JACKALOPE_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1438 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_088573ERAYPOI7A-162151EASTRAY_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1216 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_088574WRAYPOI7A-162695ELTRUENO_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3746 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_088606JRVKPOI7A-162005KNKWA1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1768 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_088640CHLPAPOI4A-162253CHALUPA_138C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1592 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_088656ASTRSPOI4A-163023NEBULA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0356 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_088670BLACKPOI7A-162915BLACKJAK_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3876 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_131753PC_SOUTH_1_5-131755PC2_SWYD_1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1322 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_143575SAMSON_3_5-143625SAMSON_1_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0997 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_143705DELILA_1_5-143757DELILA_2_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3349 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_160298BAFFIN_5-160299BAFFIN_2_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1356 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_160750LV1_AB_8-160751LV1_A_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1654 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_160750LV1_AB_8-160752LV1_B_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.17 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_180754DIVIDE_1_8-180757CAPRIDGE_3_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1627 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.3766 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_888846TIDWELL_POI-039950TNTNP_ONE_3C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1225 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_888846TIDWELL_POI-039950TNTNP_ONE_3C2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1225 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4651 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_888856HOLLY_POI-059900LONG_DRAWC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0783 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_888857OYSTER_POI-068091NAVARROC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.268 | 100.2339 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.699 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0489 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L_888878ERIKA_POI-003105ELKTON_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5716 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L1000027 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1402 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L1000032 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1216 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L10010116 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1479 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L10010434_MODIFIED_BY_MZ | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3182 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L10010717 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3674 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L10011585 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4799 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L10011690 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7021 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L10011910-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6167 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L10012087 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3217 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L10012091 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1768 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L10012100 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0119 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L10012105 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2358 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L10012900 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1034 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L10012915 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4361 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L11000047 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3746 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L11000090 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8271 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L11000095 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2975 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L11000105 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1652 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L11000171 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1592 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L201000169 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0277 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | L20255426 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0277 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | LAKE CREEK - LAKE HALL_5 (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.7739 | 102.2439 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | LAKE CREEK - RATTLE SNAKE 345 KV WITH SANDY UNIT (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 113.2253 | 105.2553 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | LAKE CREEK-RATTLESNAKE/ST JOHNS_5 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 118.6119 | 115.2245 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | LCRA TSC_T21451 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1627 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | LCRA TSC_T21457 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2758 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | LCRA TSC_T255_TAE3121_1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.8785 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | LCRA TSC_T698_T217_A | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5671 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | LCRATSC_5_HORNSB_EUCLID | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3101 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | LCRATSC_6_EUCLID_JOHNDU | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3921 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | LCRATSC_7_JOHNDU_ZORN__ | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3393 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 124.2435 | 116.7244 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1689 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | M10000271115801 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.5842 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | M105311105321 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.6565 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | M115851115803 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.2419 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | M128152129153 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6908 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MALDIVES_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3884 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MANKIN-KINGSCREEK_8 (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6633 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MARLIN - GROESBECK_9 (SINGLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.1826 | 104.2915 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.2812 | 101.0233 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | - | 101.3732 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB100002711580 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.5842 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB1000710005-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2156 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB1101411110-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0942 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB1158011585 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.2419 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB1291512815a | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6757 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB2089220893 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0447 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB210140210145-AAAAA | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.4051 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB210140210145-AAAAB | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.7634 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB210140210145-AAABA | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.455 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB210140210145-AABA | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.008 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB210140210145-AABB | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0778 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB210140210145-ABAAA | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.7312 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB210140210145-ABAAB | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.3897 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB210140210145-ABABB | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.7949 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB210140210145-ABBA | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0104 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB210140210145-BAAA-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1439 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB210140210145-BAAA-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3044 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB210140210145-BABA | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0953 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MB2726627277 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.9932 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MINERVA - CANNON_8 (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.2721 | 100.2492 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.4836 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.1562 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNIT 4 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5325 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.9364 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.8508 | 102.1309 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | MOSS - HOLT/YUCCA 138 KV/MIDLAND COUNTY NW SW 345 KV (DOUBLE B TO B) SUM 2025- FUTURE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0546 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | N5GSU2_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.8589 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 112.5628 | 106.4353 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | NAV-CORS_W-MONTFORT_8 (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7987 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | NAV-MEXIA_9 (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.8931 | 102.1396 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.442 | 100.2349 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.3985 | 101.1023 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | ODESSA EHV - NORTH MCCAMEY 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.9633 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | OYSTER_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.6745 | 100.5068 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_BTE_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0779 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_BTE_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0779 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_BTE_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0779 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_BVE_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4779 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_BVE_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4766 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_CBT_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.2948 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_CBT_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.3206 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_CBY_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0775 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_CBY_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0775 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_CHE_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0662 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_CHE_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0962 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_DPEC_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5303 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_DPEC_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5629 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_DPEC_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5305 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_DPEC_4_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.5629 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_DPEC_5_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4788 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_FTR_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4423 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_FTR_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4423 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_FTR_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4417 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_GEN_BLY-CBT_C0_111143 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9172 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_GEN_BLY-CBT_C1_111141 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2832 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_GEN_BLY-CBT_C2_111142 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3584 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_PSG_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0864 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-1_PSG_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0865 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-2_(40015-49200-GL) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4766 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-2_(40450-110666-02) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0889 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-2_(40600-120095-1) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3855 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-2_(40890-113219-01) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3309 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-2_(42985-110797-60) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2908 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-2_(44015-49215-GL) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8273 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-2_(44090-111865-1) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2346 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-2_(46020-49208-GL) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8642 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-2_(46020-49209-GL) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9088 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-2_(8130-43190-1) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1034 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P1-2_11.1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0039 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P7-1_E1>>JULIA | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7236 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P7-1_E1>>T1827D | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2479 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P7-1_E1>>T1839X1_ERC | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.7441 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P7-1_E1>>T1839X2_ERC | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.1381 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P7-1_E1>>T2764Y_ERCa | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4698 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P7-1_E1>>T3944Z_ERC | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.5495 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P7-1_E1>>T6060B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7474 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P7-1_E1>>T6472CX1A | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4414 | 102.1574 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P7-1_E1>>T6472CX1B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2421 | 101.8088 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P7-1_E1>>T6472E | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9363 | 101.3354 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P7-1_E1>>T7475B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0755 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P7-1_E1>>T9797B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.2299 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 111.3345 | 105.3518 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | P7-1_E1>T6060F | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.2345 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | PALESTINE - CROCKETT*PALESTINE SOUTH - ELKTON_8_9 (DOUBLE B TO B)_SUM2019 B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3337 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | PALESTINE - TRINIDAD*PALESTINE SOUTH - BLACKBURN_8_9 (DOUBLE B TO B)B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4181 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | PALESTINE S - BLACKBURN_8 (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0885 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | PARIS SW-PACIFIC SW/VALLEY S SW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.176 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | PINEFOREST_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.1766 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | QUANT_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3482 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | R4U2A5C1_1_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.058 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | RANCHLAND - MEXIA_8 (SINGLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.6659 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1544 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | RAT_SNAKE-SNDY_CREEK_5 (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 113.2269 | 105.2575 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | REAT_SKYD_P7F2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9219 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | RYBRN_P1-2_CANTON TAP-CANTON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1511 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2215 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | SAM_NAV_P7F1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.6296 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | SAN_PAT_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.7458 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | SEAGOVILLE SW-KAUFMAN-TERRELL SW (SINGLE B TO B) A | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7049 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | SKYSLY_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4958 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | SOLACE_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.4793 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | STECL_10247 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0267 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | STECL_10248 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0267 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | STECL_10262 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.5708 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | STECL_10288 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0103 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | STP - HOUDINI & STP - SHAULA | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4259 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | T_003588GROESBECP_9-003597GROESBECP_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.5401 | 104.5671 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | T_003632MEXIA2_1_8-003614MEXIA_NO_9C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.8347 | 102.0842 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | T_059908NOVA_345-059998NOVA8CT1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.9953 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | T_180760DIVIDE_SC1-180754DIVIDE_1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1627 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 112.9182 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 119.8952 | 113.7781 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8299 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TRICORNER - TYLER GRANDE (single B TO B) new_load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.8574 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.1487 | 102.0953 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.2284 | 101.6127 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.7419 | 101.274 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | - | 107.0723 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TRIFECTA_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.0661 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TRINIDAD - MANKIN (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.798 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TRIN-MANKIN*EUSTACE SOUTHEAST(DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0549 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TRIN-NIP*MA (DOUBLE B TO B)B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0269 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7239 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TRIN-SK*ME (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.4064 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.0131 | 102.2902 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.9941 | 102.6608 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TRNDAD-PINOAK_8 (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1962 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | - | 108.3903 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 115.3588 | 110.5312 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 114.7831 | 110.3403 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 115.3706 | 110.739 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TWIN_OAK_BKR_8995_345_OAK_GROVE_SINGLE_B_T0_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0263 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | TWIN_OAK_BKR_9000_345_OAK_GROVE_SINGLE_B_T0_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.0242 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | U3CT1_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.4663 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | U3GSU1_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.3001 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | U3GSU2_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8014 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.874 | 106.0301 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.0989 | 105.3433 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.9485 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | VIKING_CON | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.613 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | Voss Lake - Minerva 138 kV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.3963 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | WAP - HOUDINI & STP - SHAULA | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.9589 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.3713 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1769 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | WHITERIVER-COTTONWOOD (DOUBLE B TO B)-3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9261 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.1091 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | WINDMILL - AJSWOPE (SINGLE B TO B) SUM 2028 - FUTURE | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.9859 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.8977 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C2_345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7466 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-ENNSTRAC_8-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.2236 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-GRHAMSES1_8-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8663 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-HANDLEYC_8-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.8821 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-HANDLEYC_8-3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.3706 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-HANDLEYD_8-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.3682 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-LKHB_1T8-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.6468 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-LKHB_2T8-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.5883 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-MARTINLK_5-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9612 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-MARTINLK_5-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.0105 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-MARTINLK_5-3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.055 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-MDLTHELP_5-5 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8323 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-MDLTHELP_5-6 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8458 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-MDLTHELP_N5-3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9119 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-MDLTHELP_N5-4 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.9112 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-MDLTHELP_S5-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.748 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-MDLTHELP_S5-2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.8601 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-MTCK_8T8-8 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 103.2434 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-SANDYCRK_5-01 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 113.2269 | 105.2575 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-WHCCS2_4-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5325 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-WHCCS2_5-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.1244 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-WLFHMDPT_5-1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.8978 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIESEL_8 ( 3702) -> LAKE_CRK1_8 ( 3410) CKT 1 | XFMR-WLFHOSTR-3 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.7467 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIKER ( 508) -> HILLTOP8 ( 501) CKT 1 | BEPC_242 | 138 | 138 | Branch Amp | 1623.2745 | - | - | - | - | 111.6458 | 105.5026 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIKER ( 508) -> HILLTOP8 ( 501) CKT 1 | L_000541RENO-000595KEETERC1 | 138 | 138 | Branch Amp | 1623.2745 | - | - | - | - | 110.0182 | 103.8028 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIKER ( 508) -> HILLTOP8 ( 501) CKT 1 | L_000579JCKCNTY8-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1623.2745 | - | - | - | - | 112.0792 | 105.802 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIKER ( 508) -> HILLTOP8 ( 501) CKT 1 | L_000595KEETER-000596COTTONDALEC1 | 138 | 138 | Branch Amp | 1623.2745 | - | - | - | - | 110.7633 | 104.5266 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RIKER ( 508) -> HILLTOP8 ( 501) CKT 1 | L_000596COTTONDALE-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1623.2745 | - | - | - | - | 112.0698 | 105.7927 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | RINCON2A ( 8416) -> GREGORY2A ( 8421) CKT 1 | L_008422I_DUPSW4A-008425INGLESID4AC1 | 69 | 69 | Branch Amp | 820.0046 | - | - | 101.863 | 108.0309 | 120.3515 | 105.8809 | -
TLCRA,TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | RINCON4B ( 8437) -> ROCKPORT4A ( 8434) CKT 1 | L_008422I_DUPSW4A-008425INGLESID4AC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | 146.2056 | 153.168 | 169.2843 | 149.3387 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | RINCON4B (8437) -> MELNCRK4A (80065) CKT 1 | Pre-contingency | 138 | 138 | Amps | 656.8405 | - | - | - | - | 126.694 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | RIOHONDO7A ( 8318) -> GULCH7A ( 8704) CKT 1 | MB10000841000093-1A | 345 | 345 | Branch Amp | 1914.4597 | - | - | 109.3127 | - | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | RIOHONDO7A ( 8318) -> GULCH7A ( 8704) CKT 1 | P7/C5-SHRY-3 | 345 | 345 | Branch Amp | 1914.4597 | - | - | 106.28 | - | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | RIOHONDO7A (8318) -> GULCH7A (8704) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1710.2954 | - | - | - | 199.8154 | 198.1221 | 190.3099 | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RIOPECOS4A ( 6601) -> TNGIRVIN__1 (38445) CKT 1 | L_006601RIOPECOS4A-038445TNGIRVIN__1C2 | 138 | 138 | Branch Amp | 2581.3411 | 101.5022 | - | 117.8967 | 118.4036 | 120.8117 | 116.8011 | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RIOPECOS4A ( 6601) -> TNGIRVIN__1 (38445) CKT 2 | L_006601RIOPECOS4A-038445TNGIRVIN__1C1 | 138 | 138 | Branch Amp | 2999.7109 | - | - | 100.8027 | 101.2344 | 103.2938 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RIVERSTR (500207) -> RIVERTON_8 (11083) CKT 2 | 3WT_011084RIVERTON_5_011083RIVERTON_8_011085RIVERTON1_3 C 1 | 138 | 1 | Branch MVA | 750 | - | - | - | 126.8981 | 136.3473 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RIVERSTR (500207) -> RIVERTON_8 (11083) CKT 2 | L_888839BAS_RANCH_POI-011098SANDLAKE_5C1 | 138 | 1 | Branch MVA | 750 | - | - | - | 101.2628 | 106.5609 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RIVERSTR (500207) -> RIVERTON_8 (11083) CKT 2 | QUARRY FIELD - RIVERTON 345 KV 2021 SUM - FUTURE (DOUBLE B TO B) | 138 | 1 | Branch MVA | 750 | - | - | - | 104.15 | 109.4271 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RIVERSTR (500208) -> RIVERTON_8 (11083) CKT 1 | 3WT_011084RIVERTON_5_011083RIVERTON_8_011075RIVERTON2_3 C 2 | 138 | 1 | Branch MVA | 750 | - | - | - | 127.9755 | 139.0371 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RIVERSTR (500208) -> RIVERTON_8 (11083) CKT 1 | L_888839BAS_RANCH_POI-011098SANDLAKE_5C1 | 138 | 1 | Branch MVA | 750 | - | - | - | 102.2342 | 108.3546 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RIVERSTR (500208) -> RIVERTON_8 (11083) CKT 1 | QUARRY FIELD - RIVERTON 345 KV 2021 SUM - FUTURE (DOUBLE B TO B) | 138 | 1 | Branch MVA | 750 | - | - | - | 104.8868 | 110.7112 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RIVERSTR (500208) -> RIVERTON_8 (11083) CKT 1 | RIVERTON-SAND LAKE 345/138 KV DCKT LINE 2021 WIN - FUTURE (DOUBLE B TO B)-1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | 100.3961 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RIVERTON_5 (11084) -> RIVERSTR (500207) CKT 2 | 3WT_011084RIVERTON_5_011083RIVERTON_8_011085RIVERTON1_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | 129.1502 | 136.6773 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RIVERTON_5 (11084) -> RIVERSTR (500207) CKT 2 | L_888839BAS_RANCH_POI-011098SANDLAKE_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | 102.3403 | 106.5766 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RIVERTON_5 (11084) -> RIVERSTR (500207) CKT 2 | QUARRY FIELD - RIVERTON 345 KV 2021 SUM - FUTURE (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | 105.81 | 110.492 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RIVERTON_5 (11084) -> RIVERSTR (500208) CKT 1 | 3WT_011084RIVERTON_5_011083RIVERTON_8_011075RIVERTON2_3 C 2 | 345 | 1 | Branch MVA | 750 | - | - | - | 129.4552 | 139.0371 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RIVERTON_5 (11084) -> RIVERSTR (500208) CKT 1 | L_888839BAS_RANCH_POI-011098SANDLAKE_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | 102.8691 | 108.3546 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RIVERTON_5 (11084) -> RIVERSTR (500208) CKT 1 | QUARRY FIELD - RIVERTON 345 KV 2021 SUM - FUTURE (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | 106.3567 | 111.0629 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RIVERTON_5 (11084) -> RIVERSTR (500208) CKT 1 | RIVERTON-SAND LAKE 345/138 KV DCKT LINE 2021 WIN - FUTURE (DOUBLE B TO B)-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | 100.3961 | - | -
TCNPE | COAST | COAST | COAST, COAST | RIWOOD_X82B8 (43150) -> CLUTE___B138 (42050) CKT 82 | L_042030SAMARI__B138-042050CLUTE___B138C26 | 138 | 138 | Branch Amp | 1213.2722 | 100.6718 | - | - | 105.7866 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | RIWOOD_X82B8 (43150) -> CLUTE___B138 (42050) CKT 82 | L_042030SAMARI__B138-042110ANGLTN_POI_8C&1-MS | 138 | 138 | Branch Amp | 1213.2722 | 100.6859 | - | - | 105.8009 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | RIWOOD_X82B8 (43150) -> CLUTE___B138 (42050) CKT 82 | L_888849CLUTCH_CITY_POI-042960MUSTNG_S04_8C04 | 138 | 138 | Branch Amp | 1213.2722 | - | - | - | 100.3383 | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | RNDRCKNE2_8 ( 3667) -> RNDRCKWH_T_8 ( 3664) CKT 1 | L_003539JONAHT_8-007346L_GABRIE8_1YC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.3564 | 100.3422 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | RNDRCKNE2_8 ( 3667) -> RNDRCKWH_T_8 ( 3664) CKT 1 | LCRA TSC_T378_T642 | 138 | 138 | Branch Amp | 1313.6809 | 103.3049 | - | - | - | - | - | -
TONCOR,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | RNDRCKWH_T_8 ( 3664) -> RNDRCKWH1_8 ( 3669) CKT 1 | LCRA TSC_T378_T642 | 138 | 138 | Branch Amp | 1355.5178 | 100.137 | - | - | - | - | - | -
TONCOR,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | RNDRCKWH1_8 ( 3669) -> L_GEORSO8_1Y ( 7532) CKT 1 | GABRIEL - BELL COUNTY/GEORGETOWN E_8 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | 104.1146 | - | - | - | - | - | -
TONCOR,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | RNDRCKWH1_8 ( 3669) -> L_GEORSO8_1Y ( 7532) CKT 1 | GABRIEL - BELL COUNTY/GEORGETOWN E_8 (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.3742 | 102.7209 | 102.6938 | -
TONCOR,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | RNDRCKWH1_8 ( 3669) -> L_GEORSO8_1Y ( 7532) CKT 1 | GEORGETOWN E - GABRIEL_8 (SINGLE B TO B) B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.3311 | 102.6268 | 102.6504 | -
TONCOR,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | RNDRCKWH1_8 ( 3669) -> L_GEORSO8_1Y ( 7532) CKT 1 | L_003539JONAHT_8-007346L_GABRIE8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | 109.0107 | 111.2619 | 112.5406 | 112.5247 | -
TONCOR,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | RNDRCKWH1_8 ( 3669) -> L_GEORSO8_1Y ( 7532) CKT 1 | L_003539JONAHT_8-007528L_GEOREA8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.3764 | 102.6907 | 102.6921 | -
TONCOR,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | RNDRCKWH1_8 ( 3669) -> L_GEORSO8_1Y ( 7532) CKT 1 | L_003668RNDROCK1_8-007366L_CHIEBR8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | 114.3077 | - | - | - | - | - | -
TONCOR,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | RNDRCKWH1_8 ( 3669) -> L_GEORSO8_1Y ( 7532) CKT 1 | L_007343L_GEORGE8_1Y-007347L_RIVERY8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | 102.7053 | - | - | - | - | - | -
TONCOR,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | RNDRCKWH1_8 ( 3669) -> L_GEORSO8_1Y ( 7532) CKT 1 | L_007343L_GEORGE8_1Y-007366L_CHIEBR8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | 109.0225 | - | - | - | - | - | -
TONCOR,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | RNDRCKWH1_8 ( 3669) -> L_GEORSO8_1Y ( 7532) CKT 1 | L_007346L_GABRIE8_1Y-007528L_GEOREA8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | 104.0164 | - | - | - | - | - | -
TONCOR,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | RNDRCKWH1_8 ( 3669) -> L_GEORSO8_1Y ( 7532) CKT 1 | LCRA TSC_T223_1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.3311 | 102.6268 | 102.6504 | -
TONCOR,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | RNDRCKWH1_8 ( 3669) -> L_GEORSO8_1Y ( 7532) CKT 1 | LCRA TSC_T378_T642 | 138 | 138 | Branch Amp | 861.8416 | 119.9155 | - | 101.7411 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RNRTPL1_5 (2355) -> RNRTPSTR (500068) CKT 1 | Pre-contingency | 345 | 1 | MVA | 478 | - | - | 100.0302 | - | - | - | -
TCNPE | COAST | COAST | COAST, COAST | ROARK__S25_8 (44590) -> ROARK_25T8_8 (44592) CKT 25 | P7-1_E1>>T9899A | 138 | 138 | Branch Amp | 1962.1539 | - | - | - | - | 100.5648 | - | -
TCNPE | COAST | COAST | COAST, COAST | ROARK_25T7_8 (44591) -> ROARK__S25_8 (44590) CKT 25 | P7-1_E1>>T9899A | 138 | 138 | Branch Amp | 2083.4812 | - | - | - | - | 101.7418 | - | -
TCNPE | COAST | COAST | COAST, COAST | ROARK_25T8_8 (44592) -> CLODIN__B138 (44140) CKT 25 | P7-1_E1>>T9899A | 138 | 138 | Branch Amp | 1861.7451 | - | - | - | - | 101.8747 | - | -
TONCOR | EAST | SOUTH_CE | EAST, SOUTH_CE | ROBERTSON ( 32) -> CANNON_8 ( 3707) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 102.3291 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ROCKETTSW ( 214) -> ROCKETT ( 218) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 69 | 69 | Branch Amp | 284.4914 | - | - | - | - | 106.054 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ROCKETTSW ( 214) -> ROCKETT ( 218) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 69 | 69 | Branch Amp | 284.4914 | - | - | - | - | 108.033 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ROCKETTSW ( 214) -> ROCKETT ( 218) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 69 | 69 | Branch Amp | 284.4914 | - | - | - | - | 108.3171 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ROCKETTSW ( 214) -> ROCKETT ( 218) CKT 1 | L_000221TRUMBULL8-012344GAMMA_8C1 | 69 | 69 | Branch Amp | 284.4914 | - | - | - | - | 113.9481 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ROCKETTSW ( 214) -> ROCKETT ( 218) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 69 | 69 | Branch Amp | 284.4914 | - | - | - | - | 106.5168 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ROCKETTSW ( 214) -> ROCKETT ( 218) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 69 | 69 | Branch Amp | 284.4914 | - | - | - | - | 106.0234 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ROCKETTSW ( 214) -> ROCKETT ( 218) CKT 1 | L_012329SHANKLSW_8-012344GAMMA_8C1 | 69 | 69 | Branch Amp | 284.4914 | - | - | - | - | 113.9857 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ROCKETTSW ( 214) -> ROCKETT ( 218) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 69 | 69 | Branch Amp | 284.4914 | - | - | - | - | 108.3488 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ROCKETTSW ( 214) -> ROCKETT ( 218) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 69 | 69 | Branch Amp | 284.4914 | - | - | - | 106.9092 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | ROCKPORT4A ( 8434) -> ARANSASP4A ( 8430) CKT 1 | L_008422I_DUPSW4A-008425INGLESID4AC1 | 138 | 138 | Branch Amp | 1020.8221 | - | - | 113.2722 | 120.2593 | 133.3394 | 117.5881 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ROCKYCRK_5 ( 1880) -> ROCKYSTR (500053) CKT 1 | L_001880ROCKYCRK_5-011886TIMBERVW_5C1 | 345 | 1 | Branch MVA | 750 | - | - | 101.6869 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ROCKYCRK_5 ( 1880) -> ROCKYSTR (500053) CKT 1 | TIMBERVIEW-ROCKY CREEK*BENBROOK 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | 101.4923 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ROCKYCRK_5 ( 1880) -> TIMBERVW_5 (11886) CKT 1 | 3WT_001880ROCKYCRK_5_001881ROCKYCRK_8_011881ROCKYCRK_3 C 1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.6378 | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RONDO1_8 (11173) -> RONDO1_3 (11208) CKT 1 | Pre-contingency | 138 | 38 | MVA | 250 | - | 102.9256 | - | - | 100.697 | 104.9059 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | RONDO1_8 (11173) -> RONDO1_3 (11208) CKT 1 | QUARRY FIELD - BLUE MOUNTAIN DBL CKT 138 KV SUM 2025 - FUTURE (DOUBLE B TO B)_MODIFIED_BY_MZ | 138 | 38 | Branch MVA | 250 | 103.829 | - | - | - | - | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RWMILLER ( 331) -> PALOPNTO_T8 ( 1576) CKT 1 | BEPC_237 | 138 | 138 | Branch Amp | 1200.7211 | - | - | 103.0573 | 100.9247 | - | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RWMILLER ( 331) -> PALOPNTO_T8 ( 1576) CKT 1 | L_000331RWMILLER-033312LONG2C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | 106.5659 | 104.5897 | 102.7619 | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RWMILLER ( 331) -> PALOPNTO_T8 ( 1576) CKT 1 | L_000477FOX8-000482VULCANC1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | 103.9686 | 102.0494 | 100.245 | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RWMILLER ( 331) -> PALOPNTO_T8 ( 1576) CKT 1 | L_000482VULCAN-001595LIPAN_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | 105.0876 | 103.1596 | 101.3496 | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | RWMILLER ( 331) -> PALOPNTO_T8 ( 1576) CKT 1 | L_001595LIPAN_8-033312LONG2C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | 106.5637 | 104.5959 | 102.7688 | - | -
TAEPTC,TCNPE | COAST | COAST | COAST, COAST | S_LANE__B138 (43190) -> LAN_CTY4B ( 8130) CKT 1 | L_042985DYANN__POI_8-043570WHARTN__60B8C&1-MS | 138 | 138 | Branch Amp | 2196.4409 | - | - | - | - | 122.16 | 115.623 | -
TAEPTC,TCNPE | COAST | COAST | COAST, COAST | S_LANE__B138 (43190) -> LAN_CTY4B ( 8130) CKT 1 | L_043090PYTHIA_POI_8-043110SANBER_POI_8C60 | 138 | 138 | Branch Amp | 2196.4409 | - | - | - | - | 103.1198 | - | -
TAEPTC,TCNPE | COAST | COAST | COAST, COAST | S_LANE__B138 (43190) -> LAN_CTY4B ( 8130) CKT 1 | L_043090PYTHIA_POI_8-043380W_COL__POI_8C60 | 138 | 138 | Branch Amp | 2196.4409 | - | - | - | - | 109.3594 | - | -
TAEPTC,TCNPE | COAST | COAST | COAST, COAST | S_LANE__B138 (43190) -> LAN_CTY4B ( 8130) CKT 1 | L_043570WHARTN__60B8-044150HNGFRD_POI_8C&1-MS | 138 | 138 | Branch Amp | 2196.4409 | - | - | - | - | 118.424 | 111.9225 | -
TAEPTC,TCNPE | COAST | COAST | COAST, COAST | S_LANE__B138 (43190) -> LAN_CTY4B ( 8130) CKT 1 | L_044150HNGFRD_POI_8-044190E_BERN__B138C60 | 138 | 138 | Branch Amp | 2196.4409 | - | - | - | - | 129.1766 | 127.8116 | -
TAEPTC,TCNPE | COAST | COAST | COAST, COAST | S_LANE__B138 (43190) -> LAN_CTY4B ( 8130) CKT 1 | L_044640SEALY__S65_8-044700GEBHRT_X65B8C65 | 138 | 138 | Branch Amp | 2196.4409 | - | - | - | - | 101.9611 | - | -
TAEPTC,TCNPE | COAST | COAST | COAST, COAST | S_LANE__B138 (43190) -> LAN_CTY4B ( 8130) CKT 1 | L_044640SEALY__S65_8-046220PETERS__B138C65 | 138 | 138 | Branch Amp | 2196.4409 | - | - | - | - | 100.1324 | - | -
TAEPTC,TCNPE | COAST | COAST | COAST, COAST | S_LANE__B138 (43190) -> LAN_CTY4B ( 8130) CKT 1 | L_044700GEBHRT_X65B8-888872SKYSLY_POIC65 | 138 | 138 | Branch Amp | 2196.4409 | - | - | - | - | 102.5799 | - | -
TAEPTC,TCNPE | COAST | COAST | COAST, COAST | S_LANE__B138 (43190) -> LAN_CTY4B ( 8130) CKT 1 | P7-1_E1>>T6060D | 138 | 138 | Branch Amp | 2196.4409 | - | - | - | - | 122.0629 | 115.7295 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO_S1_8 (13640) -> SONTERRA ( 121) CKT 1 | BELLCNTY8-BARTLETTSW (SINGLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 104.1444 | 115.2864 | 104.2114 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO_S1_8 (13640) -> SONTERRA ( 121) CKT 1 | BELLCNTY8-GABRIEL (LCRA) (SINGLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 103.3097 | - | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO_S1_8 (13640) -> SONTERRA ( 121) CKT 1 | BEPC_215_2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 114.4188 | 103.3674 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO_S1_8 (13640) -> SONTERRA ( 121) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | 102.4493 | - | - | 122.4604 | - | 111.9543 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO_S1_8 (13640) -> SONTERRA ( 121) CKT 1 | L_000114BARTLETTSW-000122SCHWERTNERC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 103.6712 | 114.8365 | 103.7612 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO_S1_8 (13640) -> SONTERRA ( 121) CKT 1 | L_000114BARTLETTSW-000132BELLCNTY8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 104.4652 | 115.6131 | 104.5235 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO_S1_8 (13640) -> SONTERRA ( 121) CKT 1 | L_000122SCHWERTNER-007346L_GABRIE8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.6132 | 112.7331 | 101.692 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO_S1_8 (13640) -> SONTERRA ( 121) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 131.9988 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO_S1_8 (13640) -> SONTERRA ( 121) CKT 1 | LCRA TSC_T359_T21422_1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 109.4118 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO1_8 ( 3640) -> SALADO_S1_8 (13640) CKT 1 | BELLCNTY8-BARTLETTSW (SINGLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 109.6275 | 120.7031 | 109.6076 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO1_8 ( 3640) -> SALADO_S1_8 (13640) CKT 1 | BELLCNTY8-GABRIEL (LCRA) (SINGLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 108.7868 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO1_8 ( 3640) -> SALADO_S1_8 (13640) CKT 1 | BEPC_215_2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 119.8288 | 108.7582 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO1_8 ( 3640) -> SALADO_S1_8 (13640) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | 108.2576 | - | - | 128.4924 | - | 117.7174 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO1_8 ( 3640) -> SALADO_S1_8 (13640) CKT 1 | L_000114BARTLETTSW-000122SCHWERTNERC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 109.1545 | 120.2535 | 109.1578 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO1_8 ( 3640) -> SALADO_S1_8 (13640) CKT 1 | L_000114BARTLETTSW-000132BELLCNTY8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 109.9525 | 121.034 | 109.9233 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO1_8 ( 3640) -> SALADO_S1_8 (13640) CKT 1 | L_000122SCHWERTNER-007346L_GABRIE8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 107.0882 | 118.1415 | 107.0817 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO1_8 ( 3640) -> SALADO_S1_8 (13640) CKT 1 | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.1017 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO1_8 ( 3640) -> SALADO_S1_8 (13640) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 104.828 | 138.3431 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO1_8 ( 3640) -> SALADO_S1_8 (13640) CKT 1 | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 102.9685 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO1_8 ( 3640) -> SALADO_S1_8 (13640) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0381 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO1_8 ( 3640) -> SALADO_S1_8 (13640) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 100.0381 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO1_8 ( 3640) -> SALADO_S1_8 (13640) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 101.5773 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SALADO1_8 ( 3640) -> SALADO_S1_8 (13640) CKT 1 | LCRA TSC_T359_T21422_1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 104.5394 | 114.8568 | 104.5108 | -
TONCOR | SOUTH_CE | NORTH_CE | SOUTH_CE, NORTH_CE | SALADOSS_5 ( 3699) -> HUTTOSS__5 ( 3696) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.4194 | - | -
TONCOR | SOUTH_CE | NORTH_CE | SOUTH_CE, NORTH_CE | SALADOSS_5 ( 3699) -> HUTTOSS__5 ( 3696) CKT 2 | L_003696HUTTOSS__5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.4194 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SALEM_8 (10041) -> BULLDOG_8 (23833) CKT 1 | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 895.3112 | 104.7821 | - | - | 100.6064 | 104.4839 | 100.2112 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SALEM_8 (10041) -> BULLDOG_8 (23833) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 106.7098 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SALEM_8 (10041) -> BULLDOG_8 (23833) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 895.3112 | - | 117.6977 | - | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW - MONTICELLO 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6113 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 108.0681 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.4705 | 120.865 | 102.0348 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 111.7275 | 129.7972 | 110.2854 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.6168 | 119.7167 | 101.0996 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 110.7203 | 128.4795 | 109.2221 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 109.0447 | 128.7552 | 108.7602 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 118.9245 | 138.4126 | 117.6837 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 109.9559 | 129.7247 | 109.5534 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 119.9187 | 139.3749 | 118.617 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 108.1322 | 127.5278 | 107.7358 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 117.8363 | 136.9977 | 116.2398 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 109.0406 | 128.5043 | 108.5751 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 118.8331 | 137.9446 | 117.4262 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.5796 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.3931 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.2882 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.8942 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN-MOSES 345-138 AUTO-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.8818 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLEN-MOSES 345-138 AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.3794 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 117.527 | 139.2791 | 117.3937 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 128.5647 | 150.2441 | 127.5058 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 113.0787 | 133.6445 | 112.8015 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 123.5158 | 143.7738 | 122.3251 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | CARTWHEEL_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.3786 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | L_001685FARMVLSW_5-011689CYCLONE_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 105.525 | 123.1155 | 103.5792 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | L_001695MOSES_5-001697SULSP_SS1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.6513 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6113 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.9098 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | L_001696MOSES1_T5-888854PINEFOREST_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.6113 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | L_001697SULSP_SS1_5-888847CARTWHEEL_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.2236 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | L_011684BRIGHTR_5-011688THORNTRE_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.8305 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | L_011684BRIGHTR_5-011689CYCLONE_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 113.506 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | L_888847CARTWHEEL_POI-002464CASHSW_T5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.9655 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.9098 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | MOSES-SULPHUR SPRINGS SW 345-138 KV AUTO SULPHUR SPRINGS SW 345-138 KV AUTO #1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.0204 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | PARIS SW-PACIFIC SW/VALLEY S SW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.1426 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | PINEFOREST_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.2213 | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | SALTILLO_5 (11700) -> FARMVLSW_5 ( 1685) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.004 | 117.401 | - | -
TCNPE | COAST | COAST | COAST, COAST | SAMARI__B138 (42030) -> ANGLTN26T1_8 (42111) CKT 26 | Pre-contingency | 138 | 138 | Amps | 978.9851 | - | - | - | - | 135.5618 | 141.8301 | -
TCNPE | COAST | COAST | COAST, COAST | SAMARI__B138 (42030) -> CLUTE___B138 (42050) CKT 26 | L_042050CLUTE___B138-043150RIWOOD_X82B8C82 | 138 | 138 | Branch Amp | 1171.4352 | 106.0107 | - | - | 111.3983 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | SAMARI__B138 (42030) -> CLUTE___B138 (42050) CKT 26 | L_042100HUDSON_POI_8-042960MUSTNG_S04_8C04 | 138 | 138 | Branch Amp | 1171.4352 | 104.4052 | - | - | - | - | - | -
TCNPE | COAST | COAST | COAST, COAST | SAMARI__B138 (42030) -> CLUTE___B138 (42050) CKT 26 | L_042110ANGLTN_POI_8-043150RIWOOD_X82B8C82 | 138 | 138 | Branch Amp | 1171.4352 | 106.3329 | - | - | 111.7319 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | SAMARI__B138 (42030) -> CLUTE___B138 (42050) CKT 26 | L_042110ANGLTN_POI_8-043380W_COL__POI_8C&1-MS | 138 | 138 | Branch Amp | 1171.4352 | - | - | - | 100.4455 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | SAMARI__B138 (42030) -> CLUTE___B138 (42050) CKT 26 | L_042570ARCHER_POI_8-044430MANVEL_S26_8C26 | 138 | 138 | Branch Amp | 1171.4352 | - | - | - | 102.2248 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | SAMARI__B138 (42030) -> CLUTE___B138 (42050) CKT 26 | L_042940MONSAN_POI_8-043070PETSON_X04B8C04 | 138 | 138 | Branch Amp | 1171.4352 | 101.0525 | - | - | - | - | - | -
TCNPE | COAST | COAST | COAST, COAST | SAMARI__B138 (42030) -> CLUTE___B138 (42050) CKT 26 | L_042960MUSTNG_S04_8-043500WEBSTR_B138AC&1-MS | 138 | 138 | Branch Amp | 1171.4352 | 103.2365 | - | - | 106.3799 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | SAMARI__B138 (42030) -> CLUTE___B138 (42050) CKT 26 | L_043070PETSON_X04B8-044890SNUG___POI_8C04 | 138 | 138 | Branch Amp | 1171.4352 | 101.7389 | - | - | - | - | - | -
TCNPE | COAST | COAST | COAST, COAST | SAMARI__B138 (42030) -> CLUTE___B138 (42050) CKT 26 | L_888849CLUTCH_CITY_POI-042960MUSTNG_S04_8C04 | 138 | 138 | Branch Amp | 1171.4352 | - | - | - | 107.5251 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | SAMARI__B138 (42030) -> CLUTE___B138 (42050) CKT 26 | P7-1_E1>>T0405 | 138 | 138 | Branch Amp | 1171.4352 | 103.3591 | - | - | 105.8133 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | SAMARI__B138 (42030) -> CLUTE___B138 (42050) CKT 26 | P7-1_E1>>T0463 | 138 | 138 | Branch Amp | 1171.4352 | 103.2851 | - | - | 106.4158 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | SAMARI__B138 (42030) -> CLUTE___B138 (42050) CKT 26 | P7-1_E1>>T0493 | 138 | 138 | Branch Amp | 1171.4352 | 103.0068 | - | - | 106.1474 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | SAMARI__B138 (42030) -> CLUTE___B138 (42050) CKT 26 | P7-1_E1>>T2626D | 138 | 138 | Branch Amp | 1171.4352 | - | - | - | 102.4207 | - | - | -
TCNPE | COAST | COAST | COAST, COAST | SAMARI__B138 (42030) -> CLUTE___B138 (42050) CKT 26 | Pre-contingency | 138 | 138 | Amps | 920.4134 | - | - | - | - | 144.1816 | 150.8538 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | 3WT_076000L_NORTMC5_1Y_076595L_NORTMC8_2Y_076998L_NORTMC2_2Y C 2 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 104.041 | - | 104.2804 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | 3WT_076000L_NORTMC5_1Y_076595L_NORTMC8_2Y_076999L_NORTMC2_1Y C 1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 104.041 | - | 104.2804 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | ALLEN SW - ANNA SW 138 KV (DOUBLE B TO B) A 23 RIDGEVIEW | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.2395 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | ALLEN SW - ANNA SW/BLOOMDALE SW 138 KV (DOUBLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.212 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | BAS_RANCH_CON | 69 | 69 | Branch Amp | 317.961 | - | - | - | 107.9716 | - | 102.1528 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | BROWNWOOD AUTO_8 (SINGLE AUTO ) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1722 | - | 100.1995 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | BROWNWOOD-FIREROCK/BANGS_8_9 (DOUBLE B TO B ) B | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1908 | - | 100.2235 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | BROWNWOOD-FIREROCK_8 (SINGLE B TO B) B | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1676 | - | 100.2034 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | CATTLEMAN - CHAMPION CREEK & MORGAN CREEK SW - BITTER CREEK SW (LCRA) 345 KV (DOUBLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4641 | - | 100.2438 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | Cattleman-Longshore 2 345 kV ONCOR WTIP RPG Submittal | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.2747 | - | 100.708 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | Cattleman-Longshore Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 69 | 69 | Branch Amp | 317.961 | - | - | - | 106.4324 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | CENTRAL BLUFF - BROWN SW & CENTRAL BLUFF - BLUFF CREEK SW 345 KV (DOUBLE B TO B)-2 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0428 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | DUNE - WINK/YUKON 138 KV 2019 SUM - FUTURE (DOUBLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.2032 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | E_NEDIN_CC1_TRAIN | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1038 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | E_OECCS_CC1_TRAIN | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.647 | - | 100.0794 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | E_OECCS_CC2_TRAIN | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.6627 | - | 100.0848 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | E_QALSW_CC1_TRAIN | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.2694 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | E_QALSW_CC2_TRAIN | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.251 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | E5DVA1C1_1_B | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.03 | - | 100.5076 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | E5DVA1C1_1_B_1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5683 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | E5DVA1C1_1_B_2 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.3058 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | FALCON SOUTH - RANGER CAMP 345 KV SUM 2027 - FUTURE(DOUBLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.1086 | - | 100.3603 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_008707DRYFRIOUS1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0018 | - | 100.0256 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_010012METEOR_5US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.3876 | - | 100.2202 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_060716SGSA4AUS1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.033 | - | 100.2071 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_132431SIRIUS_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.0629 | - | 100.7895 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_132436SIRIUS_S2US2 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0185 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_132481RIGGINS_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5379 | - | 100.1713 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_132781CASLGP_UNIT1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.1806 | - | 100.4938 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_132941SPTX12B_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.9266 | - | 100.3187 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_133841WAYMARK_W1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1425 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_134241TAYGETE_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.091 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_134243TAYGETE_S2US2 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1126 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_134751FOWLR_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.8928 | - | 100.545 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_135111ARAGORN_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1496 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_135321REDBARN_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.3526 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_135731APPALOSA_W1UW1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.09 | - | 101.0709 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_136101BLUESKY_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 108.8097 | - | 108.7184 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_136341TRBNT_PV_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.8445 | - | 100.2684 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_162541MCLNSLR_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.2446 | - | 100.2555 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_181751FERMI_WIND1UW1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1839 | - | 100.1504 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_182151EGROVESL_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.544 | - | 100.2745 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_183571SUNRAY_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1081 | - | 100.1343 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_183621ZIER_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.0052 | - | 101.9288 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_888839BAS_RANCH_POIUC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 107.7862 | - | 102.1778 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G_888851TRIFECTA_POIUN1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6012 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | G8DVA1C1_B | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.1871 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | HOLLY_CON | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4808 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.1734 | - | 101.767 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | IRON_BELT_CON | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.4698 | - | 100.6411 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | KILLEEN SS - RUSSELL GAP / BUCKHORN_5 (DOUBLE B TO B ) | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.1074 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_000842GPL_KINGMTSW-000843GPL_KINGMTTPC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.5476 | - | 100.5024 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_000842GPL_KINGMTSW-076000L_NORTMC5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.2033 | - | 100.5529 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.2258 | - | 100.8325 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_000844GPL_NEVILLSW-076000L_NORTMC5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 105.266 | - | 105.2543 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_000844GPL_NEVILLSW-076002L_BAKERS5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 103.3161 | - | 102.9036 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_000860GPL_GIRVINSW-136341TRBNT_PV_S1C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.8447 | - | 100.2685 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_001009YUCCADR_8-011245RIVERVIEW_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.3924 | - | 101.0308 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_001027ODESEHV_8-071230L_PLEAFA8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.435 | - | 100.3922 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_001058LONGSHORE_5-010053CATTLEMEN_5C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.2747 | - | 100.708 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_001058LONGSHORE_5-010053CATTLEMEN_5C2 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.2747 | - | 100.708 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.3927 | - | 100.051 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_001141HOLTSS_8-132313ECEC_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4768 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_001661BRNWD1_8-001671BANGS_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0805 | - | 100.1171 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_001671BANGS_8-006359FIREROCK4BC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1566 | - | 100.194 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_005798AMISTAD8-008686AMISTD4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.333 | - | 100.3028 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0002 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006015MADDUX4A-006490SANTIAGO4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 103.3628 | - | 103.1261 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006015MADDUX4A-060423TREADWEL4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4372 | - | 100.4823 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006036YUCCA4A-006525ESMERALD4AC1 | 69 | 69 | Branch Amp | 317.961 | 117.239 | - | 146.7927 | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006036YUCCA4A-060360CASSAVA4AC1 | 69 | 69 | Branch Amp | 317.961 | 100.9856 | - | 123.2984 | 141.2531 | - | 151.5041 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006228ABNTHWST4A-006476LANCIUM4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.003 | - | 100.1158 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006235ABMULCW7A-060040BLF_CRK7AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.2126 | - | 100.161 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006355SANA4A-006390FIREROCK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1565 | - | 100.1939 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006365YELWJCKT4B-060423TREADWEL4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.1347 | - | 101.186 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006410MILE2A-006412HARI2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4781 | - | 100.4805 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006412HARI2A-006450CONCHO2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4732 | - | 100.4755 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006435STER2A-006641CAMPELIZ2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5234 | - | 100.5764 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006435STER2A-061016MAGNOX2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.2665 | - | 100.297 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006444REDCREEK7A-076009L_TWINBU5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.213 | - | 100.8611 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006450CONCHO2A-006495CRIS2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.2611 | - | 100.1632 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006490SANTIAGO4A-006500LVOK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 106.7316 | - | 106.6844 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006495CRIS2A-006496ARROTT2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.2689 | - | 100.1694 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006496ARROTT2A-006497HULLDALE2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.2514 | - | 100.1523 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006500LVOK4A-060412CARVER4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 110.5394 | - | 110.1512 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006511ATSO2A-006513SONR2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5979 | - | 100.6052 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006511ATSO2A-006552OZNC2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.2948 | - | 100.3143 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006513SONR2A-060433CARVER2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1283 | - | 100.0436 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006517RUSSEKST4A-006535BIGLAKE4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.6953 | 115.9182 | - | 114.537 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006517RUSSEKST4A-006559JERRY4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 103.1484 | 118.0099 | - | 116.8127 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006525ESMERALD4A-006562FDRAN4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 112.3909 | 127.9517 | - | 131.8885 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006530BARNHRT2A-006534BIGLAKE2BC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 110.3628 | - | 110.9432 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006535BIGLAKE4A-060375WOLFBERR2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 105.9058 | - | 106.3798 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006536BIGLAKE4B-060414OWLS4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 110.4686 | - | 110.7661 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006549MIDW2A-006560OZONA2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.3399 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006550FDRAN2A-006552OZNC2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1703 | - | 100.1937 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006550FDRAN2A-006560OZONA2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.2209 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006551OZNR2A-006560OZONA2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.0432 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006551OZNR2A-006567PANDALE2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.1381 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006559JERRY4A-060374PUMPJACK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 107.0365 | 123.5415 | - | 122.506 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006562FDRAN4A-060412CARVER4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.5556 | 108.7101 | - | 109.2074 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006562FDRAN4A-136103BLUESKY_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 108.8735 | - | 108.7842 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006564ILLN4A-060389CORRAL4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.0661 | - | 101.0576 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006565ILLN2A-006567PANDALE2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.2076 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006586MCCAMY4-076001L_TIPPET8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.2178 | - | 101.3272 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006586MCCAMY4-076032L_NORTMC8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.2191 | - | 101.3303 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006601RIOPECOS4A-076026L_SODALA8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0073 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006601RIOPECOS4A-076601L_HORSCR8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5425 | - | 100.2732 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006630FTST4A-132482RIGGINS_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5386 | - | 100.1733 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006641CAMPELIZ2A-011352KINNEBREW_9C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.12 | - | 100.1891 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006648HARGROVE4A-060374PUMPJACK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 110.4812 | 128.4479 | - | 127.4214 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_006648HARGROVE4A-076011L_TWINBU8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 112.0961 | 130.716 | - | 129.6796 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_007389L_PINNAC8_1Y-135019TI_SOLAR_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5239 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_007389L_PINNAC8_1Y-135113ARAGORN_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1496 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_007425L_ODLASW8_1Y-008252BRACKETT4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.042 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008209SHAKEPOI4A-162543MCLNSLR_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.245 | - | 100.2561 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008234UVALDE4A-008246ASPHALT4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.0525 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008234UVALDE4A-008707DRYFRIOC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0787 | - | 100.0396 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008255HAMILTON4A-008680ROUGHCAN4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.337 | - | 101.3576 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008255HAMILTON4A-078255L_PINTCR8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.0664 | - | 102.1261 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008259CAUTHORN4A-008991DLNCRK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.276 | - | 100.3448 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008259CAUTHORN4A-060440TINSLEY4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.312 | - | 100.3636 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008261WHITING4A-008991DLNCRK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0634 | - | 100.2539 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008261WHITING4A-008998MAXWELL4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.0978 | - | 101.2387 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008273PUEBLO4A-008274W_CONOCO4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.3305 | - | 100.4546 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008274W_CONOCO4A-078281L_DIMMIT8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.3484 | - | 100.4716 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008283ASHERTON4A-078280L_BEVO__8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.3912 | - | 100.4037 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008680ROUGHCAN4A-008683COMSTOCK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.1799 | - | 101.2013 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008683COMSTOCK4A-060389CORRAL4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.0547 | - | 101.0519 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008715RADIANT7A-008728COBRA7AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.33 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008728COBRA7A-081003HABER7AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5024 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_008998MAXWELL4A-181754FERMI_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4185 | - | 100.3758 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_010012METEOR_5-011010WOLFSS_5C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0609 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_010049RANGER_5-011048TONKAWAW_5C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0153 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_010049RANGER_5-011048TONKAWAW_5C2 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0153 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_010053CATTLEMEN_5-076030L_GASCCR5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.818 | - | 100.4289 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_011028ODESEHV2_5-059901GRELTONC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4757 | - | 100.0457 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_011245RIVERVIEW_8-900064Other_134C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.3059 | - | 100.9486 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_011270DOGHOUSE_5-023876CLEARFRK_5C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.7224 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_011270DOGHOUSE_5-134805PROSPERO_5C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0313 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_023924FARMLAND_5-888856HOLLY_POIC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0881 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_038340TNAIRPORT41-038355TNLEONCRK_1C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.0369 | - | 101.2191 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_038345TNP900072_TP-038355TNLEONCRK_1C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.224 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_038345TNWOODHOUSE-038355TNLEONCRK_1C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.224 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_059900LONG_DRAW-888842IRON_BELT_POIC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.1445 | - | 100.506 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_059901GRELTON-059910VOLTAC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4744 | - | 100.045 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_059902SAND_BLUFF-059907BERNOULLIC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 103.4029 | - | 102.1034 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_059902SAND_BLUFF-076090L_DIVIDE5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.1024 | - | 100.5145 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_059903BEARKAT-059907BERNOULLIC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 103.1262 | - | 102.4901 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_059904COTTONWOOD-060006HYPERION7AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.0942 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060017HODLRAN27A-060515CLEARCRO7AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0569 | - | 100.3154 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060361SANTARIT4A-060414OWLS4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.7945 | 121.1278 | - | 123.1912 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 102.8501 | 122.4829 | - | 124.6796 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060377CREOSOTE4A-060392LOTEBUSH4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1462 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060383LINTERNA4A-132331REROCK_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1694 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060385SOLSTICE4A-060393PIGCREEK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.2268 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060385SOLSTICE4A-060717FTSW4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.3536 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060392LOTEBUSH4A-060415BASIN4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6728 | - | 100.3795 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060393PIGCREEK4A-134245TAYGETE_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.9957 | - | 100.2395 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060393PIGCREEK4A-134705TYGTEII_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6737 | - | 100.0251 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060397GASPADTA4A-060415BASIN4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.7189 | - | 100.421 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060397GASPADTA4A-900064Other_134C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.2513 | - | 100.9019 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060411BURMA2A-061017GOLOID2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5398 | - | 100.5598 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060412CARVER4A-060440TINSLEY4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.2943 | - | 100.3387 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060723CROSSOVE4A-060728PALOUSE4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 113.551 | - | 115.3817 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060723CROSSOVE4A-076032L_NORTMC8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 113.6268 | - | 115.4846 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 104.0749 | 124.0987 | - | 126.4663 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_060728PALOUSE4A-135734APPALOSA_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.308 | - | 101.2422 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_061016MAGNOX2A-061017GOLOID2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4209 | - | 100.4453 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_076001L_TIPPET8_1Y-076013L_WESTYA8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.564 | - | 100.6649 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_076002L_BAKERS5_1Y-133843WAYMARK_5C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1429 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_076002L_BAKERS5_1Y-135327REDBARN_5C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5016 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_076003L_BIGHIL5_1Y-076009L_TWINBU5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 103.2739 | - | 101.1441 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_076011L_TWINBU8_1Y-900117Other_90_SOC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 109.7283 | - | 109.6672 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_076030L_GASCCR5_1Y-076090L_DIVIDE5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6615 | - | 100.2652 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_076032L_NORTMC8_1Y-900113Other_81_SOC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 105.6778 | - | 106.1634 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_076040L_CASTIL8_1Y-132783CASL_GAP_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.21 | - | 100.514 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_076040L_CASTIL8_1Y-132943SPTX12B_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.0003 | - | 100.3693 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_076579L_FORTLA8_1Y-900074Other_4_OKCC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.2942 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_076601L_HORSCR8_1Y-182154EGROVESL_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.544 | - | 100.2745 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_078255L_PINTCR8_1Y-183623ZIER_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.1998 | - | 102.1164 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_078280L_BEVO__8_1Y-078281L_DIMMIT8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.8468 | - | 100.9443 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_888839BAS_RANCH_POI-011098SANDLAKE_5C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.9432 | - | 100.1657 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_888842IRON_BELT_POI-059910VOLTAC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.4506 | - | 100.7026 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_888856HOLLY_POI-059900LONG_DRAWC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.8581 | - | 100.1259 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_900052Other_115-900110Other_86_MOC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.2256 | - | 100.8622 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_900062Other_118-900113Other_81_SOC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 103.0797 | - | 104.1499 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L_900110Other_86_MO-900117Other_90_SOC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 108.1446 | - | 108.0957 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L10010095 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.9333 | - | 100.9189 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L10010116 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 103.5834 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L10011200 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.239 | - | 100.206 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L2020472-1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.473 | - | 100.4754 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L2020500-1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4809 | - | 100.57 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L2020510-A-1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6073 | - | 100.6287 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L2020616 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1 | - | 100.1185 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L2020900 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.1346 | - | 101.186 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L2020925 | 69 | 69 | Branch Amp | 317.961 | - | - | 102.1125 | 116.3256 | - | 115.0002 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L2020933-B | 69 | 69 | Branch Amp | 317.961 | - | - | - | 105.541 | - | 105.5112 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L2020944-A | 69 | 69 | Branch Amp | 317.961 | - | - | 102.7776 | 122.4133 | - | 124.6184 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L2020944-B | 69 | 69 | Branch Amp | 317.961 | - | - | - | 113.5465 | - | 115.3768 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L2020971-B2 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0034 | - | 100.0524 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | L2021632 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6536 | - | 100.8786 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_BAKERS_CEDACA_DC | 69 | 69 | Branch Amp | 317.961 | - | - | - | 106.4854 | - | 102.2259 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-1 | 69 | 69 | Branch Amp | 317.961 | - | - | 102.7718 | 104.5575 | - | 101.3092 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-2 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.7394 | 103.7594 | - | 100.9365 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-1 | 69 | 69 | Branch Amp | 317.961 | - | - | 102.7717 | 104.5575 | - | 101.3092 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-2 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.7392 | 103.7594 | - | 100.9365 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_NOELK_SNGTR_NOELK_SNGTR2 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.3379 | 103.4909 | - | 100.8272 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_SNGTR_SCHDR_SNGTR_SCHDR2 | 69 | 69 | Branch Amp | 317.961 | - | - | 100.1187 | 103.3059 | - | 100.3861 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_T422_T550 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.4223 | - | 101.0809 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_T423_T551_A | 69 | 69 | Branch Amp | 317.961 | - | - | - | 105.0568 | - | 103.898 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_T429_T9426 | 69 | 69 | Branch Amp | 317.961 | - | - | 111.2915 | 128.8706 | - | 127.821 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_T443_T554 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.0437 | - | 101.1818 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_T451_T682 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.415 | - | 101.0538 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_T454_T484 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.6064 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_T464_1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 103.5365 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_T482_TAEP | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1565 | - | 100.1939 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_T552_T554 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.0425 | - | 101.1788 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LCRA TSC_T571_DC | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1795 | - | 100.2135 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE (DOUBLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 104.8275 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE CKT 1 (SINGLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.2747 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | M100871108255-1B | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0127 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | M100876108254-1B | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0391 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | M2100120997-2 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.1477 | - | 101.1999 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | MB1008710825-1B | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0127 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | MB2039320222 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.403 | - | 100.4339 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | MB2090020948 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.158 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | MB2092520930 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 116.7288 | - | 115.5665 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | MB2093020925 | 69 | 69 | Branch Amp | 317.961 | - | - | 102.7849 | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | MB2094820900 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 101.2096 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | MB2095120950 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 101.4052 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | MB2552825529 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4933 | - | 100.9226 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | MB2726627277 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.3428 | - | 100.3182 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | MOSS - HOLT/YUCCA 138 KV/MIDLAND COUNTY NW SW 345 KV (DOUBLE B TO B) SUM 2025- FUTURE | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6024 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | New Cattleman - Meinan and Champion 345kV Double | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4487 | - | 100.2369 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | New Meinan - Champion and Cattleman 345kV Double | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.3266 | - | 100.1504 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | New Meinan - Sweeteast and BitterCreek 345kV Double | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.0445 | - | 101.3877 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | New P1.2: Leon Creek to Woodhouse 138-kV ckt 1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.224 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | New Sweeteast - Meinan and BitterCreek 345kV Double | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.4912 | - | 100.9977 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | ODESSA EHV - NORTH MCCAMEY 345 KV (SINGLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.3329 | - | 100.7073 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | P7-1_E1>>T1827GX_ERC | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1516 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | P7-WETT-7 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.7766 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.3301 | - | 101.2122 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | RIVERTON-SAND LAKE 345/138 KV DCKT LINE 2021 WIN - FUTURE (DOUBLE B TO B)-1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4993 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | Rockhound-Prong Moss Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.8268 | - | 100.5862 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | S_006517RUSSEKST4A1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0282 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | SEAGOVILLE SW-WATERMILL 138 KV (SINGLE B TO B) WILMER 138/69 TRANSFORMER A GELLER | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.3768 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | SEAGOVILLE SW-WATERMILL/WILMER-FERRIS DCKT (DOUBLE B TO B) A | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.3768 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | STECL_10592 | 69 | 69 | Branch Amp | 317.961 | - | - | 105.3015 | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | STECL_10594 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.3552 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | STECL_4720 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.1806 | 103.272 | - | 100.7557 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | STECL_4721-1 | 69 | 69 | Branch Amp | 317.961 | - | - | 102.7719 | 104.5577 | - | 101.3094 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | STECL_4721-2 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.7394 | 103.7596 | - | 100.9366 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | SWEETWATER EAST - CENTRAL BLUFF CKT 1 & SWEETWATER EAST - CENTRAL BLUFF CKT 2 345 KV (DOUBLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.9827 | - | 100.7626 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | T_006359FIREROCK4B-006390FIREROCK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1566 | - | 100.194 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | T_006364YELWJCKT4A-006365YELWJCKT4BC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.1345 | - | 101.1857 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | T_006533BIGLAKE2A-006535BIGLAKE4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.3976 | - | 101.0084 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | T_006534BIGLAKE2B-006535BIGLAKE4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.2602 | - | 100.8934 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | T_006535BIGLAKE4A-006536BIGLAKE4BC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 108.9784 | - | 109.3491 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | T_006565ILLN2A-006564ILLN4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.2003 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | T_060359CASSAVA2A-060360CASSAVA4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 109.3109 | - | 112.5074 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | T_060433CARVER2A-060412CARVER4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1302 | - | 100.0453 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | T200007 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.2067 | - | 100.2444 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | TRIFECTA_CON | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5912 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | WETT LONG DRAW - WETT VOLTA 345 KV LINE (SINGLE B TO B)-1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.1445 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | WETT LONG DRAW - WETT VOLTA 345 KV LINE (SINGLE B TO B)-2 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.4506 | - | 100.7026 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | WOLF - METEOR/REITER 345 KV 2026 SUM - FUTURE (DOUBLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.6268 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | WOLF - REITER AND METEOR - MOSS 345 KV 2026 SUM - FUTURE (DOUBLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1485 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A ( 6477) -> TANK2A ( 6528) CKT 1 | YUCCA DRIVE - LOTEBUSH (AEP) 138 KV 2021 SUM - FUTURE (SINGLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0051 | - | 100.0524 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A (6477) -> SANW2A (6527) CKT 1 | Pre-contingency | 69 | 69 | Amps | 317.961 | - | - | 101.653 | 111.6352 | 125.0076 | 111.6394 | -
TAEPTN | WEST | WEST | WEST, WEST | SAMATHIS2A (6477) -> TANK2A (6528) CKT 1 | Pre-contingency | 69 | 69 | Amps | 317.961 | - | - | - | - | 112.5803 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.0875 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.0826 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | BAS_RANCH_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5135 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.9658 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | BEPC_015_2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.7343 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.2725 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | BIGBRN__5-JEWETT_S5 & BIGBRN__5-JEWETT_N5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.9937 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.1566 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | BLUBIRD_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.5354 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | CLY_PHNT1P7F1-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.2299 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | DRY_CREEK_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.1602 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.3003 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | E_FRNYPP_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.4555 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | E_FRNYPP_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.5068 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | E_JACKCNTY_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.2466 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | E_JCKCNTY2_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.8078 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | E_KMCHI_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.342 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | E_KMCHI_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.374 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | E_LPCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5728 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | E_LPCCS_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.2309 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | E_PANDA_S_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.5406 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | E_TGCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.6482 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | E_WCPP_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.1532 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | E_WHCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.5711 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | E_WHCCS2_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.8414 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.4463 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_000575JCKCNTY5UN1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.9933 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_000579JCKCNTY8UN1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.7481 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_120041MLSES_UNIT1UL1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5055 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_120042MLSES_UNIT2UL2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5833 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_120043MLSES_UNIT3UL3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.6494 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_150023MCSES_UNIT8UN8 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.273 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_150051HLSES_UNIT3UN3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.2894 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_150052HLSES_UNIT4UN4 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.3092 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_150053HLSES_UNIT5UN5 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.9919 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_150091LHSES_UNIT1UN1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.4495 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_150092LH2SES_UNIT2UN2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.0334 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_150111CPSES_UNIT1UU1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.2697 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_150112CPSES_UNIT2UU2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.7699 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_150151MDANP_CT1UN1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.0289 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_150152MDANP_CT2UN2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.3423 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_150155MDANP_CT5UN5 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.2642 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_150156MDANP_CT6UN6 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.3019 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_152331FILESSLR_S1US1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.49 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_154331CMPDREPV_S1US1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 113.1582 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_5920EASTDCTIE | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.0445 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_888839BAS_RANCH_POIUC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5222 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | G_888879BLUBIRD_POIUS1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.6823 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | GLASGOW_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.6465 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.3136 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.4898 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_001880ROCKYCRK_5-888879BLUBIRD_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.351 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 117.0443 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_001906VENUS_S5-888857OYSTER_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 114.6737 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.1448 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 107.7047 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_001907VENUS_N5-015200FORBESR1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.8799 | 135.3619 | 109.3076 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_001921LIGGETTA1_5-002632MILLERRD_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.9961 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.2725 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.4463 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.8899 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.8899 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.1959 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.6041 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.4913 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.4614 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.5058 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.0359 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.6875 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.7001 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.5114 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_003381BIGBRNW_5-003391JEWETT_N5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.9882 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_003386OUTLAW_5-046020LIMEST_POI_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.0205 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_003386OUTLAW_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.693 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_003389FORTSMITH_5-152333FILESSLR_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.7333 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_003404BELFALLS_8-003414TEMP_SS__5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.3647 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.6657 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 108.6301 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.819 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_011688THORNTRE_5-143625SAMSON_1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.4741 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | 100.0907 | 111.8123 | 147.9584 | 120.7589 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_046020LIMEST_POI_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.2949 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_081003HABER7A-081005ACME7AC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.3245 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.4165 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_888857OYSTER_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 111.485 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.1903 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | LATIMER_REATA_P7F1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 110.5222 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.6152 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | MB2551525514 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.4666 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | MB255152551420840 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.4436 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 111.3944 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.1532 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.5362 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.597 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.7894 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 122.6549 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | OYSTER_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 115.5987 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 119.7802 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | PINEFOREST_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.7066 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (COMMON TOWER) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.2045 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | RAMHORN - WILLOW CREEK DC 345 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5665 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | RICH-BBROWN (DOUBLE B TO B)A | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.7369 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | SCUR_CLY_P7 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5114 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.959 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | TEMPLE - BELFALLS_5 (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.3647 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | TEMPLE PECAN CREEK/BELFALLS - TRADINGHOUSE/STEAKLEYDAM_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.8833 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | TEMPLE PECAN CREEK/STEAKLEYDAM - TRADINGHOUSE/LAKE CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.8865 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | TIMBERVIEW-COMANCHE PEAK*CARMICHAEL BEND 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.3559 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | TIMBERVIEW-COMANCHE PEAK*DECORDOVA 345 KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.5228 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.6758 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 111.7944 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.3559 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.8934 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 119.944 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 116.6942 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 122.0979 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | VENUS-SAM SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 109.4193 | 143.3953 | 118.4812 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | VIKING_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.3768 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.1539 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5231 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | WSHACK_LATIMER_P7 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 111.7453 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | XFMR-HANDLEYC_8-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.2894 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | XFMR-HANDLEYC_8-3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.9919 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | XFMR-HANDLEYD_8-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.3092 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | XFMR-LKHB_1T8-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.4495 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | XFMR-LKHB_2T8-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.0334 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | XFMR-MARTINLK_5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5055 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | XFMR-MARTINLK_5-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5833 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | XFMR-MARTINLK_5-3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.6494 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | XFMR-MDLTHELP_5-5 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.2642 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | XFMR-MDLTHELP_5-6 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.3019 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | XFMR-MDLTHELP_S5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.0289 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | XFMR-MDLTHELP_S5-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.3423 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | XFMR-MTCK_8T8-8 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.273 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | XFMR-WHCCS2_5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 102.9474 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FILESVALY_5 ( 3374) CKT 1 | XFMR-WLFHMDPT_5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 100.5217 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.0563 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.0924 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.1914 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.0936 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.1928 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.2298 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.2775 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | BAS_RANCH_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.8558 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 116.1548 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 111.828 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 107.7209 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.8458 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | BIGBRN__5-JEWETT_S5 & BIGBRN__5-JEWETT_N5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.4093 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.1697 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | BLUBIRD_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 106.6562 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.5893 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | CLEAR CROSSING - COODY CROSSING/THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.4718 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | CLY_PHNT1P7F1-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.4417 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | CLY_PHNT1P7F1-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.1173 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 106.4213 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 107.4811 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | COODY CROSSING - TECUMSEH AND CLEAR CROSSING - THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.973 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | DES_WILL_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 105.6919 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | DRY_CREEK_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.6982 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | E_ETCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.3972 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | E_FRNYPP_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.3538 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | E_FRNYPP_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.3816 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | E_JACKCNTY_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.2577 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | E_JCKCNTY2_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.3428 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | E_KMCHI_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.3162 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | E_KMCHI_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.3461 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | E_LPCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.7935 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | E_LPCCS_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.4379 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | E_PANDA_S_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.5811 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | E_TGCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.8456 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | E_WCPP_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.7489 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | E_WHCCS_CC1_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.0025 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | E_WHCCS2_CC2_TRAIN | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 107.7819 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.4374 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_000575JCKCNTY5UN1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.7473 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_006100OKLA7AUC0 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.2523 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_120041MLSES_UNIT1UL1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.7256 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_120042MLSES_UNIT2UL2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.7877 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_120043MLSES_UNIT3UL3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.8086 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_150023MCSES_UNIT8UN8 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.0347 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_150051HLSES_UNIT3UN3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.1419 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_150052HLSES_UNIT4UN4 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.045 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_150053HLSES_UNIT5UN5 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.732 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_150091LHSES_UNIT1UN1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.5717 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_150092LH2SES_UNIT2UN2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.6123 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_150111CPSES_UNIT1UU1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 108.6144 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_150112CPSES_UNIT2UU2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 108.6723 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_150153MDANP_CT3UN3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.8358 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_150154MDANP_CT4UN4 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.8289 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_153911PNGT1_PV_S1US1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.5953 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_5920EASTDCTIE | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.1986 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_888839BAS_RANCH_POIUC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.8717 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | G_888879BLUBIRD_POIUS1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.7652 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | GLASGOW_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.1124 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 107.7737 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 108.3593 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | KRUMW-WEST DENT/DUNHAM 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.5865 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_000436GRANDVIEW-000443SANDFLATSWC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.4521 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_000443SANDFLATSW-000444COVINGTONC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.5921 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_000444COVINGTON-888859HIGHNOON_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.7598 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 106.6466 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.5815 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001880ROCKYCRK_5-888879BLUBIRD_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.1366 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001885EVRMNTIE1_5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.0912 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001900COMCHPKW_5-001902JHNSONSW_P5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.7606 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001902JHNSONSW_P5-015106LILLIAN1C_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 106.1116 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.2084 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.743 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.2891 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 105.0761 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001906VENUS_S5-015201FORBESR2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | 100.5009 | - | 102.8001 | 132.5599 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001906VENUS_S5-888880DES_WILL_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 105.1479 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 106.3573 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001907VENUS_N5-015106LILLIAN1C_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.653 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001907VENUS_N5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 110.9062 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001930CENTURY3_5-001932KENNDALE1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.5905 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001930CENTURY3_5-001934SHRYAUTO2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.0745 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_001932KENNDALE1_5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.7035 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.8458 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.4374 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_002291CLEBRN_W_8-037810TNHILL_CO_8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.2111 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.3852 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.3852 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.3557 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.6621 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.3538 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.3816 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.4459 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.4515 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.3288 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_003134RICHLND1_5-003380BIGBRNE_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.12 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.8843 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_003306STEKLY_DAM_5-003404BELFALLS_8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.1753 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 1793.9694 | 101.5475 | - | 106.3716 | 136.2564 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_003374FILESVALY_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 1793.9694 | 100.9062 | - | 105.3976 | 127.0248 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.3224 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_003381BIGBRNW_5-003391JEWETT_N5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.0849 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_003386OUTLAW_5-046020LIMEST_POI_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.4411 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_003386OUTLAW_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.6716 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_003404BELFALLS_8-003414TEMP_SS__5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.3725 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.2561 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 107.0568 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_003518BLUMPUMP1_8-037810TNHILL_CO_8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.305 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.0364 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_011688THORNTRE_5-143625SAMSON_1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.3668 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_011688THORNTRE_5-143705DELILA_1_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.1885 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 345 | 345 | Branch Amp | 1793.9694 | 101.7944 | - | 106.787 | 140.5595 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_046020LIMEST_POI_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.692 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_068035HELIX-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.059 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_081003HABER7A-081005ACME7AC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.8329 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.2931 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.7893 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_888880DES_WILL_POI-001916LIGGETTA2_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 105.4461 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | L_888889MIDPOINT_POI-003518BLUMPUMP1_8C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.329 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | LATIMER_REATA_P7F1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.378 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.0463 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.3671 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.5581 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.8771 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 105.6748 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 105.429 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | LIMESTONE - OUTLAW / NAVARRO_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 112.7185 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.166 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.6888 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | MB210160210165 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.4754 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | MB255152551420840 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.4549 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 107.8995 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 106.6447 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNIT 4 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.1229 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.7599 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.1282 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 115.4975 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | NEW-GRAHAM-PARKER 345 KV-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.0953 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | PINEFOREST_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.8907 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (COMMON TOWER) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.6219 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | RAMHORN - WILLOW CREEK DC 345 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.9049 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | RICH-BBROWN (DOUBLE B TO B)A | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.5704 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | SCUR_CLY_P7 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.7333 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.4011 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | TEMPLE - BELFALLS_5 (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.3725 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | TEMPLE PECAN CREEK/BELFALLS - TEMPLE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.1948 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | TEMPLE PECAN CREEK/BELFALLS - TRADINGHOUSE/STEAKLEYDAM_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.0811 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | TEMPLE PECAN CREEK/STEAKLEYDAM - TRADINGHOUSE/LAKE CREEK_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.1293 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | TIMBERVIEW-COMANCHE PEAK*CARMICHAEL BEND 345 KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.4632 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | TIMBERVIEW-COMANCHE PEAK*DECORDOVA 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.8386 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.1066 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 106.9388 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.0929 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.7473 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 111.6821 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 115.0397 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 113.0433 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.8387 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | VENUS-FORT SMITH SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | 101.4351 | - | 105.5992 | 138.0065 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | VENUS-JOHNSON 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.0288 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | VENUS-JOHNSON 345KV/DECORDOVA-CLEBURNE 138KV (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.67 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.5657 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.1946 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.4601 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.7805 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.1591 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.8595 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | VENUS-NAVARRO 345 KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 114.1089 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | VIKING_CON | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.0181 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 111.5906 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | WILLOW CREEK - CLEAR CROSSING (THOMAS PRICE) & COODY CROSSING - TECUMSEH 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV SUM 2026 - FUTURE (TRIPLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.4917 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | WILLOW CREEK - HENDERSON RANCH 345 KV & WILLOW CREEK - JACKSBORO 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.0653 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | WILLOW CREEK - TECUMSEH/THOMAS PRICE 345 KV DCKT WIN 2023 - FUTURE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.4248 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | WILLOW CREEK - THOMAS PRICE\TECUMSEH CREEK 345 KV DCKT & GRAHAM SES - PAINT CREEK 138 KV WIN 2023 - FUTURE (TRIPLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.2132 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.7495 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.6932 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | WSHACK_LATIMER_P7 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 105.5169 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | XFMR-HANDLEYC_8-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.1419 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | XFMR-HANDLEYC_8-3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.732 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | XFMR-HANDLEYD_8-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 102.045 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | XFMR-LKHB_1T8-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.5717 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | XFMR-LKHB_2T8-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.6123 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | XFMR-MARTINLK_5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.7256 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | XFMR-MARTINLK_5-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.7877 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | XFMR-MARTINLK_5-3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.8086 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | XFMR-MDLTHELP_N5-3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.8358 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | XFMR-MDLTHELP_N5-4 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.8289 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | XFMR-MTCK_8T8-8 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 103.0347 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | XFMR-WHCCS2_4-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 100.1229 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | XFMR-WHCCS2_5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.3782 | - | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SAMSW (68090) -> FORBESR1_5 (15200) CKT 1 | XFMR-WLFHMDPT_5-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 101.6941 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SANA2A ( 6353) -> SANA4A ( 6355) CKT 1 | L_006340BALLINGE4A-006360COLE_IVI4AC1 | 69 | 138 | Branch MVA | 50 | - | - | - | 131.485 | 111.8013 | 131.74 | -
TAEPTN | WEST | WEST | WEST, WEST | SANA2A ( 6353) -> SANA4A ( 6355) CKT 1 | L_006347COLETAP4A-006355SANA4AC1 | 69 | 138 | Branch MVA | 50 | - | - | - | 122.7953 | 102.9629 | 122.9909 | -
TAEPTN | WEST | WEST | WEST, WEST | SANA2A ( 6353) -> SANA4A ( 6355) CKT 1 | L_006347COLETAP4A-006360COLE_IVI4AC1 | 69 | 138 | Branch MVA | 50 | - | - | - | 129.3643 | 109.7919 | 129.6689 | -
TAEPTN | WEST | WEST | WEST, WEST | SANA2A ( 6353) -> SANA4A ( 6355) CKT 1 | L2020903 | 69 | 138 | Branch MVA | 50 | - | - | - | 123.9125 | 104.1977 | 123.7521 | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SAND_STR (500225) -> SANDOW_SR1_8 (13441) CKT 2 | L_003717TORTOISE_5-013429SAND_TXU_5C1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | 101.047 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SAND_STR (500225) -> SANDOW_SR1_8 (13441) CKT 2 | TORTOISE - SANDOW_8_5 (DOUBLE B TO B ) | 138 | 1 | Branch MVA | 750 | - | - | - | - | 100.7809 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SAND_TXU_5 (13429) -> SAND_STR (500225) CKT 2 | L_003717TORTOISE_5-013429SAND_TXU_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | 104.1222 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SAND_TXU_5 (13429) -> SAND_STR (500225) CKT 2 | TORTOISE - SANDOW_8_5 (DOUBLE B TO B ) | 345 | 1 | Branch MVA | 750 | - | - | - | - | 103.8183 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SAND_TXU_5 (13429) -> SAND_STR (500226) CKT 3 | L_003717TORTOISE_5-013429SAND_TXU_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | 103.0432 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SAND_TXU_5 (13429) -> SAND_STR (500226) CKT 3 | TORTOISE - SANDOW_8_5 (DOUBLE B TO B ) | 345 | 1 | Branch MVA | 750 | - | - | - | - | 102.7424 | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SAND_TXU_5 (13429) -> TORTOISE_5 ( 3717) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 3199.6917 | - | - | - | 100.2139 | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SAND_TXU_5 (13429) -> TORTOISE_5 ( 3717) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 3199.6917 | - | - | - | 103.9332 | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SAND_TXU_5 (13429) -> TORTOISE_5 ( 3717) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 3199.6917 | - | - | - | - | 114.2433 | - | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_003414TEMP_SS__5_013415TEMP_SS_R_8_013414TEMP_SS__3 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0979 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_003696HUTTOSS__5_003666HUTTOSS1_8_003660HUTTOSS1_3 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0555 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_003696HUTTOSS__5_003666HUTTOSS1_8_024992HUTTO2_3 C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0366 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_003717TORTOISE_5_003713TOR_SR2_8_003715TORTOISE2_3 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0254 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_003717TORTOISE_5_003714TOR_SR1_8_003716TORTOISE_3 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0254 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_007040L_AUSTRO5_1Y_009328AUSTROP8_009329AUSTROP_T1 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2385 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_007040L_AUSTRO5_1Y_009328AUSTROP8_009330AUSTROP_T2 C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2279 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_007042L_ZORN__5_1Y_007180L_ZORN__8_1Y_007832L_ZORN13_1Y C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0309 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_007042L_ZORN__5_1Y_007180L_ZORN__8_1Y_007834L_ZORN_3_1Y C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.047 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_007042L_ZORN__5_1Y_007180L_ZORN__8_1Y_077180L_ZORN__2_1Y C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0464 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_007340L_GILLCR5_1Y_007336L_GILLCR8_1Y_077340L_GILLCR2_1Y C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4888 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_007340L_GILLCR5_1Y_007336L_GILLCR8_1Y_077341L_GILLCR2_2Y C 3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4902 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_007356L_MARSFO8_1Y_007354L_MARSFO9_1Y_170031MAR_MARSFOG1 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.01 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_007356L_MARSFO8_1Y_007354L_MARSFO9_1Y_170033MAR_MARSFOG3 C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0393 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_007770L_BERGHE5_1Y_007170L_BERGHE8_1Y_007771L_BERGHE1_1Y C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_009044DUNLAP5_009045DUNLAP8_090001DUNLAP_TR C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6871 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_009044DUNLAP5_009045DUNLAP8_090007DUNLAP_TR2 C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6871 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_009074LYTTON5_009075LYTTON8_009078LYTTON_T1 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5644 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_009074LYTTON5_009075LYTTON8_009081LYTTON_T2 C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4783 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_009074LYTTON5_009075LYTTON8_077075L_LYTTSP2_1Y C 3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4838 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_013429SAND_TXU_5_013441SANDOW_SR1_8_013440SAND3_ONC_3 C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1013 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | 3WT_013429SAND_TXU_5_013442SANDOW_SR2_8_013439SAND2_ONC_3 C 3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.095 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_AU-DG¦DL_2013 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1519 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_DE-SK¦SK | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.3284 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_DL-AU¦LP_2013 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 105.6373 | 104.8302 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_DP-SK¦MC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.113 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_DP-WC¦EB | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.3737 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_FPP-HO¦LY | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.955 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_FPP-WH.DC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1003 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_GF-SR: EP-HC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.007 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_GF-SR¦EP | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.2786 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_HC-EP¦PK | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1628 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_HC-SW.DC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3376 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_KB-WC¦EB | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6631 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_LP-AU¦DL_2013 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 106.1367 | 101.0088 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_LY-BF¦TV_2017 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.7703 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_LY-FPP:CIS-HO | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 102.6865 | 102.4485 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_LY-FPP¦CIS | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 107.0197 | - | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_MC-DP_1013¦W_S | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3913 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_MC-DP¦DE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4129 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_P1-1_GEN_SH5A+5C | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 107.0197 | 106.332 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_P7 FPP-LP.DC_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8007 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_P7 FPP-LP.DC_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.2769 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AEN_P71TR_HL_AW_138_DBLCKT_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.6472 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | AUSTROP - BEULAH/TORTOISE_5 (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1966 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | BAS_RANCH_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 102.6516 | 100.8668 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2749 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.23 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 101.9013 | 100.1979 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0316 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | BELLCNTY8-BARTLETTSW (SINGLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5254 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1423 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | BEPC_215_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3863 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | BEPC_23_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0472 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | BEPC_311_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.027 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | BLUBIRD_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1525 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | BROWNWOOD SW - GOLDTHWAITE/BROWNWOOD 138 KV (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0168 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | CARLSON - STEGER (LCRA)_8 (SINGLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7187 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | DVCPA1C21B_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 101.7223 | 100.0994 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | DVCPA1C21B_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.021 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_B_DAVIS_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 100.0352 | 100.1168 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_BASTEN_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 101.8339 | 102.6764 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_BRAUNIG_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.154 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_DUKE_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0207 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_FERGCC_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 104.0684 | 104.2344 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_FRNYPP_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2112 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_FRNYPP_CC2_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2093 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_GUADG_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2006 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_GUADG_CC2_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1981 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_JACKCNTY_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0209 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_JCKCNTY2_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0661 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_KMCHI_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0055 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_KMCHI_CC2_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0078 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_LOSTPI_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7549 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_NEDIN_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1868 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_NUECES_B_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 100.841 | 100.112 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_OECCS_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0988 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_OECCS_CC2_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1001 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_PANDA_S_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0864 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_PANDA_T1_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4123 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_PANDA_T2_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3588 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_SANDHSYD_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | 107.0197 | - | - | - | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_TGCCS_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.054 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_WCPP_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1808 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_WHCCS_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1383 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E_WHCCS2_CC2_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3894 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E5DVA1C1_1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.4986 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | E5DVA1C1_1_B_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0498 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_000575JCKCNTY5UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1002 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_003717TORTOISE_5US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1937 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_003717TORTOISE_5US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0429 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_006100OKLA7AUC0 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1374 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_007041L_JOHNDU5_1YUN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3079 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_007044L_MARION5_1YUN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1932 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_007048L_GARFIE5_1YUN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 100.9166 | 102.417 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_010012METEOR_5US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.049 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_079000GRAYUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0266 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_120041MLSES_UNIT1UL1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.037 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_120042MLSES_UNIT2UL2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0379 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_120043MLSES_UNIT3UL3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0412 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_150023MCSES_UNIT8UN8 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0366 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_150111CPSES_UNIT1UU1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4631 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_150112CPSES_UNIT2UU2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4616 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_150741SCES_UNIT1UL1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1113 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_153911PNGT1_PV_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0052 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170033MAR_MARSFOG3UH3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0225 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170071GID_GIDEONG1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7922 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170072GID_GIDEONG2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4387 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170073GID_GIDEONG3UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 100.0081 | 102.4554 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170126CALAVER_JKS2UL2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 104.2971 | 100.4516 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170191HAY_HAYSENG1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0437 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170192HAY_HAYSENG2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0629 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170193HAY_HAYSENG3UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0607 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170194HAY_HAYSENG4UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0466 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170213SANDHSYD_SH3UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9541 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170214SANDHSYD_SH4UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.971 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170217SANDHSYD_SH6UN6 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0078 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170218SANDHSYD_SH7UN7 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9011 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170521E_BLACK_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7631 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170571N_FORK_BTUB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.567 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170671CACHENA_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0607 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_170871GIGABATT_B1UB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1325 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_171091MPP_N1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2801 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_171161SYPBRNCH_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3279 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_5920EASTDCTIE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0013 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_888839BAS_RANCH_POIUC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 102.631 | 100.8615 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_888851TRIFECTA_POIUN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0359 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_888879BLUBIRD_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1578 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G_RIO_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 104.5213 | 101.4083 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | G8DVA1C1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.5576 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | HOLLY_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1196 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | HUTTO - ROUND ROCK CKT 2 (SINGLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6736 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | HUTTO - ROUND ROCK/GEORGETOWN SOUTH (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.6954 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | 100.7681 | - | 102.7229 | - | - | 106.2565 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | J5GSU4_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2417 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | J5LCA1C1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 104.5933 | 101.4359 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | J5ST1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2417 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | KILLEEN SS - RUSSELL GAP / BUCKHORN_5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4293 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.285 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 13.8 | 138 | Branch MVA | 107 | - | - | 100.3497 | - | - | 102.6877 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | 102.2888 | - | - | 105.1753 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_000113TURNBOR-000115DINGDONGC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1162 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_000113TURNBOR-000117CEDARVALLYC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1153 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_000114BARTLETTSW-000122SCHWERTNERC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.542 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_000114BARTLETTSW-000132BELLCNTY8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5951 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_000115DINGDONG-003630COPPERCV1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0589 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_000117CEDARVALLY-000136TRIMMIERC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3649 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_000121SONTERRA-003688JARRELL_E_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3511 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_000121SONTERRA-013640SALADO_S1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.457 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_000122SCHWERTNER-007346L_GABRIE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4258 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_000128CHAPPARAL-000136TRIMMIERC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4345 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_000128CHAPPARAL-003423KILL_SS__8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4321 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_000132BELLCNTY8-003415TEMP_SS__8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.9655 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_000132BELLCNTY8-003640SALADO1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8025 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.026 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_001655BRNWDSW_8-007070L_GOLDTH8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0508 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3861 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0864 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2542 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2112 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2093 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4017 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | 100.0942 | - | 107.0193 | 101.9871 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003415TEMP_SS__8-003485TINROOF_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4199 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003415TEMP_SS__8-013415TEMP_SS_R_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0979 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003541BRUSHYCRK_8-170665RVRVLYS3_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1055 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003640SALADO1_8-013640SALADO_S1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5773 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003657HUTTO_SUB1_8-013657STARRANCH2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3633 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003658TAYLOR1_8-003659THORNDLN1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1105 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003659THORNDLN1_8-003701ROOKIE_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1517 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003664RNDRCKWH_T_8-003667RNDRCKNE2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.2606 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003664RNDRCKWH_T_8-003669RNDRCKWH1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.2624 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.0314 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003666HUTTOSS1_8-003670RNDRCKNE1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.9204 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003668RNDROCK1_8-003670RNDRCKNE1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1347 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003669RNDRCKWH1_8-007532L_GEORSO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4229 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003677MIDNIGHT_8-007532L_GEORSO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1233 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003688JARRELL_E_8-007346L_GABRIE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1052 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 102.599 | 104.7593 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 102.599 | 104.7593 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003712TORTOISE_8-003713TOR_SR2_8C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0254 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_003712TORTOISE_8-003714TOR_SR1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0254 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 107.0196 | 100.8126 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 102.2423 | 100.2499 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 105.5098 | 100.4086 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0715 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_005380SHAULA-005915SO_TEX__345AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0646 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 103.524 | - | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 104.2378 | - | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007040L_AUSTRO5_1Y-007042L_ZORN__5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.342 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007040L_AUSTRO5_1Y-009041LOSTPINESC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0058 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007040L_AUSTRO5_1Y-009044DUNLAP5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2427 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007041L_JOHNDU5_1Y-007047L_HORNSB5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | 100.7354 | - | 100.9526 | 100.0992 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007041L_JOHNDU5_1Y-007050L_CLEASP5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0492 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007042L_ZORN__5_1Y-007510L_EUCLID5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 104.5289 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007042L_ZORN__5_1Y-009074LYTTON5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1889 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007047L_HORNSB5_1Y-007738L_WHISVA5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 104.5086 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 101.8427 | 102.6812 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007055L_FPPYD25_1Y-009074LYTTON5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8439 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007056L_FPPYD15_1Y-009041LOSTPINESC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.153 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007087L_CORONA8_1Y-007518L_FAIRLA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2251 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007100L_BURNET8_1Y-007104L_WIRTZ_8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1156 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007100L_BURNET8_1Y-070520P_BERTRA8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4934 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007104L_WIRTZ_8_1Y-070111P_FLATRO8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5054 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007126L_FERGUS8_1Y-180015FERGGT1_1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4955 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007126L_FERGUS8_1Y-180016FERGGT2_2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4958 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007126L_FERGUS8_1Y-180017FERGST1_1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6379 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007147L_KENDCT8_1Y-007150L_KENDAL8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0016 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007148L_MOUNTO8_1Y-007479L_MILLER8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0798 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007182L_MCCALA8_1Y-007184L_RATTLE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.3496 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007184L_RATTLE8_1Y-007188L_REDWOO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.2016 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007188L_REDWOO8_1Y-007192L_SANMAR8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6962 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007192L_SANMAR8_1Y-007200L_CANYON8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2526 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007192L_SANMAR8_1Y-070502P_KYLE__8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3377 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007200L_CANYON8_1Y-007515L_ROHR__8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1886 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007310L_SIMGID8_1Y-007319L_BASTCI8_2YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.5318 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007310L_SIMGID8_1Y-007322L_BASTCI8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0432 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007310L_SIMGID8_1Y-007324L_BUTLER8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0017 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007310L_SIMGID8_1Y-007327L_SETTLE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1433 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007310L_SIMGID8_1Y-007555L_BASTWE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.66 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007319L_BASTCI8_2Y-007326L_SWIFTE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.5418 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007323L_SHADGL8_1Y-007330L_MANOR_8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0509 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007326L_SWIFTE8_1Y-007331L_CEDAHI8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1653 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007330L_MANOR_8_1Y-007331L_CEDAHI8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4234 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007334L_MCNEIL8_1Y-007336L_GILLCR8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1329 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007336L_GILLCR8_1Y-170582SLCNHLS_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3536 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007337L_KIMBRO8_1Y-170523E_BLACK_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7632 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007340L_GILLCR5_1Y-007341L_LIMMER5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8734 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007340L_GILLCR5_1Y-007738L_WHISVA5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.5982 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007341L_LIMMER5_1Y-007510L_EUCLID5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.5907 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007348L_MARBFA8_1Y-007538L_LAKEWA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2715 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007351L_STARCK8_1Y-007476L_PALEFA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.075 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007356L_MARSFO8_1Y-007538L_LAKEWA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0736 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007356L_MARSFO8_1Y-070477P_PALEPE8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.195 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007462L_FREIHE8_1Y-007758L_WELTRO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0082 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007476L_PALEFA8_1Y-007540L_BEECRE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6868 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007479L_MILLER8_1Y-070513P_HENLY_8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1326 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007500L_TURNER8_1Y-009075LYTTON8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8017 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007514L_YARRIN8_1Y-007515L_ROHR__8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0316 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007555L_BASTWE8_1Y-007556L_BLUEBO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3366 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_007680L_CLEASP8_1Y-007758L_WELTRO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0348 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_008715RADIANT7A-008728COBRA7AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2391 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_008728COBRA7A-081003HABER7AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3776 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009041LOSTPINES-009042WINCHESC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0564 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009041LOSTPINES-009044DUNLAP5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9524 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009043CISTERN-009073HOLMANC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2951 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009043CISTERN-009074LYTTON5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.0285 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009045DUNLAP8-009188DECKER_MB3C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3465 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009045DUNLAP8-009188DECKER_MB3C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3465 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009045DUNLAP8-009195EAST_VILLAGEC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9044 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009054GILLE138-009191TRIDGE_MB2C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.5409 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009071GARFIELD8-009143EASTONPARKC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.5235 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009075LYTTON8-009262BLUFFSPGC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8451 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009079MCNEIL_MB1-009279SUMMIT_MB1C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0792 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009082MC1013BT-009188DECKER_MB3C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1075 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009117PE_MB3-009151AMDC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0337 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009121BURLSN_MB2-009179CARDINALC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4191 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009143EASTONPARK-009147HICROS_DB1C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.3205 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009169BRODIE-009267SLAUGHTRC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.111 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009175CARSON-009259PILOTKNOBC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0335 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009184DAFFIN-009271SPRNKL_MB2C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7773 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009184DAFFIN-009328AUSTROP8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.136 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009187DECKER_MB1-009196EDBLUESTNC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0841 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009187DECKER_MB1-009284WALNUTCKC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1525 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009190TRIDGE_MB1-009195EAST_VILLAGEC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6486 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009190TRIDGE_MB1-009226ASHTONW_MB1C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2873 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009191TRIDGE_MB2-009217HOWARDLNC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6435 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009223JOLLYVIL-009224ASHTONW_MB2C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2944 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_009262BLUFFSPG-009267SLAUGHTRC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6883 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_011270DOGHOUSE_5-023876CLEARFRK_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0079 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_013430SAND_TXU_8-013441SANDOW_SR1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1013 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_013430SAND_TXU_8-013442SANDOW_SR2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.095 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_059909NOVA_138-059998NOVA8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0196 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_070111P_FLATRO8_1_-070477P_PALEPE8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4413 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_070198P_LEHIGH8_1_-070502P_KYLE__8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0338 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_070512P_DRIPSP8_1_-070513P_HENLY_8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0297 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_070520P_BERTRA8_1_-070522P_ANDICE8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1663 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_070522P_ANDICE8_1_-170572N_FORK_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5676 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | L_080071ZORILLO7A-080076AJO7AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LAKE CREEK - RATTLE SNAKE 345 KV WITH SANDY UNIT (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1114 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_BF_BUS7184 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1226 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T142_TAE926_927 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5989 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T142_TAE929 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1485 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T143_TAE988_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2761 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T150_T608 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.4372 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T150_T608_A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.4636 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T180_T525 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.308 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T182_T185 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1768 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T185_T246 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 106.3193 | 102.7456 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T187_T188 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0921 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T187_T376 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2383 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T189_T376 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0781 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T196_T497_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7869 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T201_T202_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7493 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T218_T654 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2692 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T227_T388 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4666 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T237_T389_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0704 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T248_T250 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1686 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T255_TAE3121_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 107.0196 | 104.6106 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T359_T21422_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T376_T654 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0519 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T389_T493_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0689 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T389_T518 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0657 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T389_T610 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0642 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T458_T497 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.5089 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T497_T525 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.528 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T510_1 | 13.8 | 138 | Branch MVA | 107 | - | - | 100.3744 | - | - | 103.5337 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T510_T511_3 | 13.8 | 138 | Branch MVA | 107 | - | - | 100.6272 | - | - | 103.9894 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T510_T512_1 | 13.8 | 138 | Branch MVA | 107 | - | - | 100.4641 | - | - | 103.7916 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T510_T738_1 | 13.8 | 138 | Branch MVA | 107 | - | - | 101.5411 | - | - | 103.0803 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T510_T775 | 13.8 | 138 | Branch MVA | 107 | - | - | 104.5988 | - | 101.1018 | 104.2621 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T511_T625_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.2342 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T608 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.5519 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRATSC_1_HUTTO__LIMMER | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.597 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRATSC_2_LIMMER_GILLCR | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.5258 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRATSC_3_GILLCR_WHISVA | 13.8 | 138 | Branch MVA | 107 | - | - | 101.2773 | - | - | 104.0235 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRATSC_4_WHISVA_HORNSB | 13.8 | 138 | Branch MVA | 107 | - | - | 103.2155 | - | 100.1757 | 101.8478 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRATSC_5_HORNSB_EUCLID | 13.8 | 138 | Branch MVA | 107 | - | - | 104.6522 | - | 104.4989 | 104.943 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRATSC_6_EUCLID_JOHNDU | 13.8 | 138 | Branch MVA | 107 | - | - | 107.0197 | - | 107.0196 | 106.2195 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRATSC_7_JOHNDU_ZORN__ | 13.8 | 138 | Branch MVA | 107 | - | - | 103.1186 | - | 100.4688 | 101.8641 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LCRATSC_8_ZORN___CLEASP | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.5639 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | LIMMER SS - GILLELAND/ZORN_5 (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.71 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | M10000271115801 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1613 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | M115851115803 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | MALLARD - TAYLOR/BRUSHY CREEK 138 KV (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.546 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | MB100002711580 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1613 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | MB1158011585 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | MB210140210145-AAAAA | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0536 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | MB210140210145-AAAAB | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0853 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | MB210140210145-AABA | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0182 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1374 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1525 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | N4P3A1C1_B_MODIFIED_BY_MZ | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0614 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | N5GSU2_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 104.2971 | 100.4516 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2799 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T1827GX_ERC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.804 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T1839X1_ERC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0125 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T1839X2_ERC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 101.5629 | 100.0933 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T2764Y_ERCa | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0494 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T3944Z_ERC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 103.9579 | - | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1718 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | PEC_T180_T323 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7362 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | PEC_T219_T311_A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.469 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | PEC_T323_T458 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.5208 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | PEC_T323_T497 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9678 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | PEC_T325_T965 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1017 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | R4U2A5C1_1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1536 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | R5S2S1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1496 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | RAT_SNAKE-SNDY_CREEK_5 (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1113 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | ROOKIE-TAYLOR_8 (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0871 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_003371SKYBOX_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7044 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_003422KILL_SS__51 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0104 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_003485TINROOF_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1071 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_003668RNDROCK1_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.7512 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_003672RNDRCK_S1_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3825 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_003693MALLARD_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.694 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_003750VOSSLAKE_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5224 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_007041L_JOHNDU5_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1561 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_007346L_GABRIE8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0792 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_007366L_CHIEBR8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.161 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_007523L_GLASSC8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.084 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_007530L_KENTST8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2782 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_007534L_AVERRA8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2882 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_007555L_BASTWE8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0743 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009001BA138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4012 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009002BC138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5001 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009003CL138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5553 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009005CF138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3544 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009006FV138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4495 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009008HV138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2853 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009009JV138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2946 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009010MP138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3844 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009011MC138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3587 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009012OH138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4041 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009014PE138MB1_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6162 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009015PK138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6876 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009016SW138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4409 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009017BAL138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3899 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009018WI138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3447 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009160BEECREEK_MB11 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009165BRSTRM_MB11 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9455 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009195EAST_VILLAGE1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8929 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009224ASHTONW_MB21 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2709 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_009262BLUFFSPG1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3604 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_013430SAND_TXU_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.5258 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_070352P_LAGOVI8_1_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2171 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_070498P_BUDA__8_1_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1513 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_070507P_FRIEND8_1_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1463 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_070522P_ANDICE8_1_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0908 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_070524P_SEWAJU8_1_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1817 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_070525P_LEANDE8_1_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2194 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | S_070527P_BLOCKH8_1_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2407 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0462 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | STP - HOUDINI & STP - SHAULA | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0413 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | T_059908NOVA_345-059998NOVA8CT1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0196 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 103.0304 | 102.9046 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0337 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | TRIFECTA_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0359 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0796 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5712 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | WAP - HOUDINI & STP - SHAULA | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0855 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1808 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | XFMR-MARTINLK_5-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.037 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | XFMR-MARTINLK_5-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0379 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | XFMR-MARTINLK_5-3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0412 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | XFMR-MTCK_8T8-8 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0366 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | XFMR-SANDYCRK_5-01 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1113 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD ( 9216) CKT 1 | XFMR-WHCCS2_5-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1639 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH1 (170211) -> SANDHSYD (9216) CKT 1 | Pre-contingency | 13.8 | 138 | MVA | 107 | - | - | - | 100.2611 | - | - | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_001440COMCHESS1_5_001441COMCHESS1_8_011440CMCHE_SS_3 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0542 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0303 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_003363TEAL_5_003362TEAL_8_003364TEAL_3 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2599 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_003363TEAL_5_003362TEAL_8_013364TEAL2_3 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2599 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_003412TEMP_PEC__5_003420TEMP_PEC__8_013420TEMP_PEC__3 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2427 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_003414TEMP_SS__5_013415TEMP_SS_R_8_013414TEMP_SS__3 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4461 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_003422KILL_SS__5_003423KILL_SS__8_013424KILL_SS2__3 C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0625 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_003696HUTTOSS__5_003666HUTTOSS1_8_003660HUTTOSS1_3 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.487 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_003696HUTTOSS__5_003666HUTTOSS1_8_024992HUTTO2_3 C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.4664 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_003717TORTOISE_5_003713TOR_SR2_8_003715TORTOISE2_3 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3676 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_003717TORTOISE_5_003714TOR_SR1_8_003716TORTOISE_3 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3676 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007040L_AUSTRO5_1Y_009328AUSTROP8_009329AUSTROP_T1 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.599 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007040L_AUSTRO5_1Y_009328AUSTROP8_009330AUSTROP_T2 C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5875 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007042L_ZORN__5_1Y_007180L_ZORN__8_1Y_007832L_ZORN13_1Y C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3736 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007042L_ZORN__5_1Y_007180L_ZORN__8_1Y_007834L_ZORN_3_1Y C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3911 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007042L_ZORN__5_1Y_007180L_ZORN__8_1Y_077180L_ZORN__2_1Y C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3905 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007044L_MARION5_1Y_007178L_MARION8_1Y_007822L_MARION1_1Y C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0792 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007044L_MARION5_1Y_007178L_MARION8_1Y_077044L_MARION1_2Y CT3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0757 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007046L_KENDAL5_1Y_007150L_KENDAL8_1Y_077150L_KENDAL1_2Y C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.153 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007046L_KENDAL5_1Y_007152L_KENDAL8_2Y_077152L_KENDAL1_1Y C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1078 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007050L_CLEASP5_1Y_007680L_CLEASP8_1Y_077680L_CLEASP2_1Y C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0601 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007050L_CLEASP5_1Y_007680L_CLEASP8_1Y_077683L_CLEASP3_1Y C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0422 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007057L_FAYETT5_1Y_007286L_FAYETT8_1Y_0078537853 C 3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0053 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007340L_GILLCR5_1Y_007336L_GILLCR8_1Y_077340L_GILLCR2_1Y C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.871 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007340L_GILLCR5_1Y_007336L_GILLCR8_1Y_077341L_GILLCR2_2Y C 3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8726 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007356L_MARSFO8_1Y_007354L_MARSFO9_1Y_170031MAR_MARSFOG1 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3494 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007356L_MARSFO8_1Y_007354L_MARSFO9_1Y_170033MAR_MARSFOG3 C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3813 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_007770L_BERGHE5_1Y_007170L_BERGHE8_1Y_007771L_BERGHE1_1Y C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4556 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_009044DUNLAP5_009045DUNLAP8_090001DUNLAP_TR C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0863 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_009044DUNLAP5_009045DUNLAP8_090007DUNLAP_TR2 C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0863 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_009048GARFIELD5_009071GARFIELD8_090002GARFIELD_TR1 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.294 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_009048GARFIELD5_009071GARFIELD8_090003GARFIELD_TR2 C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.297 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_009074LYTTON5_009075LYTTON8_009078LYTTON_T1 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9531 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_009074LYTTON5_009075LYTTON8_009081LYTTON_T2 C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8596 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_009074LYTTON5_009075LYTTON8_077075L_LYTTSP2_1Y C 3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8656 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_009077MCNEIL_MB3_009080MCNEIL_090004MCNEIL_TR C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2907 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_009118PE_MB1_009119PE_MB2_090005PE_TR C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0924 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_009122KINGSB_MB1_009125KINGSBERY_090006KINGSBERY_TR C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2772 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_009128NORTHL_MB1_009129NORTHL69_009130NORTHL_T1 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1056 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_013125TDADTMOD_5_003127TRINIDAD_8_120151TRSES_UNIT6 C 1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0768 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_013429SAND_TXU_5_013441SANDOW_SR1_8_013440SAND3_ONC_3 C 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.45 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | 3WT_013429SAND_TXU_5_013442SANDOW_SR2_8_013439SAND2_ONC_3 C 3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4431 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_AU-DG¦DL_2013 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.5916 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_DE-SK¦SK | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.7832 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_DL-AU¦LP_2013 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 106.3979 | 105.5991 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_DP-SK¦MC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4621 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_DP-WC¦EB | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.833 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_FPP-HO¦LY | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.3773 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_FPP-WH.DC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4487 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_GF-SR: EP-HC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.4337 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_GF-SR¦EP | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.7291 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_HC-EP¦PK | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.6033 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_HC-SW.DC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7066 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_KB-WC¦EB | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0603 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_LP-AU¦DL_2013 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 106.9432 | 101.4316 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_LY-BF¦TV_2017 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 103.353 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_LY-FPP:CIS-HO | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 103.1806 | 103.0012 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_LY-FPP¦CIS | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 107.9078 | 100.107 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_MC-DP_1013¦W_S | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7649 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_MC-DP¦DE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7882 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_MC-JL¦FV | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1694 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_NL-MP¦ST | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.195 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_P1-1_GEN_SH5A+5C | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 107.9078 | 107.2259 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_P2HLJ345_RB_570_610_1(94OF224): | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0047 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_P7 FPP-LP.DC_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.2083 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_P7 FPP-LP.DC_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.7257 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_P71TR_HL_AW_138_DBLCKT_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 103.2192 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AEN_RP-HM¦JE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0182 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW - MONTICELLO 345 KV (SINGLE B TO B)-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW - PLANO TENNYSON 345 KV & ALLEN SW - RENNER 345 KV (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0239 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW 345-138 KV AUTO #1 (SINGLE AUTO) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0281 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.05 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0317 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0745 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0319 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0746 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0374 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0826 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0418 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0887 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0377 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0838 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0421 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.089 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0752 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1142 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0752 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1141 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN-MOSES 345-138 AUTO-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLEN-MOSES 345-138 AUTO-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0511 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0361 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0841 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0344 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0811 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ANNA SW - VALLEY SOUTH 345 KV & ANNA SW - FARMERSVILLE 345 KV (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0273 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ARGENTA_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1613 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | AUSTROP - BEULAH/TORTOISE_5 (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5536 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | B2-COD-1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.049 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | B4D5A121_C-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0062 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BARRETT_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0217 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BAS_RANCH_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 103.1427 | 101.2154 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6278 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5809 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BAY5_BF | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0794 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BELL CNTY - SALADOSOUTH_GABRIEL(LCRA)_8 (SINGLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2433 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 102.3263 | 100.5435 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 100.2209 | 100.3647 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BELLCNTY8-BARTLETTSW (SINGLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9108 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4582 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BEPC_104 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0569 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BEPC_105_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0216 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BEPC_211 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0247 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BEPC_215_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7603 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BEPC_22 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0752 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BEPC_227-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0393 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BEPC_227-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0393 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BEPC_23_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3844 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BEPC_230_4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0035 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BEPC_247_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.327 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BEPC_311_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3624 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BEPC_460 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0129 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2026 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BIGBRN__5-JEWETT_S5 & BIGBRN__5-JEWETT_N5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1559 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1225 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BIGSAMPSON_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0141 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BITTER CREEK SW (LCRA) - CATTLEMEN SW & BITTER CREEK SW (LCRA) - SWEETWATER EAST 345 KV (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1154 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BLUBIRD_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4692 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1883 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BROWN SS - RUSSELL GAP / BUCKHORN_5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0498 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BROWN SW - RED CREEK SW (AEP) 345 KV WIN 2020 - FUTURE (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0173 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | BROWNWOOD SW - GOLDTHWAITE/BROWNWOOD 138 KV (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3604 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | C4L2A111_B_MODIFIED_BY_MZ | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0348 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | C4L2A131_B_MODIFIED_BY_MZ | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0167 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | C4P3A2C1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0225 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | C4P3A4C1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.017 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | C4P3A5C1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0043 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | CACTUS_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.101 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | CARLSON - STEGER (LCRA)_8 (SINGLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1156 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | CARTWHEEL_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0083 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0067 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | CHINA GROVE SW - AEP PAINT CREEK 138 KV & GRAHAM SES - TONKAWA/COOKFIELD/LONGCREEK 345 KV (DOUBLE B TO B) 2019 SUM - FUTURE-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0516 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | CHINA GROVE SW - AEP PAINT CREEK 138 KV & GRAHAM SES - TONKAWA/COOKFIELD/LONGCREEK 345 KV (DOUBLE B TO B) 2019 SUM - FUTURE-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0056 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | CLY_PHNT1P7F1-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1222 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | CLY_PHNT1P7F1-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1064 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | CLY_PHNT2P7F1-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0632 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | CLY_PHNT2P7F1-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0489 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | COMANCHE - BROWNWOOD SW 138 KV (SINGLE B TO B )B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1088 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | COMANCHE PEAK-COMANCHE SW*STEPHENVILLE 345 138 KV (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0002 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | D5GSU1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0608 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | D5GSU2_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0609 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | DERMOTT - COTTONWOOD/MHOS (WETT) CKT 1 345 KV (SINGLE B TO B) C | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0434 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | DERMOTT - COYOTE WIND 345 KV (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0452 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | DERMOTT - FLAVIANA/GOPHER WIND 138 KV (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0155 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | DERMOTT - KIRCHHOF CKT 1 & DERMOTT - KIRCHHOF CKT 2 345 KV (DOUBLE B TO B) C | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2299 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | DERMOTT - KIRCHHOF CKT 1 345 KV WIN 2023 - FUTURE (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2167 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | DES_WILL_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0397 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | DRY_CREEK_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1423 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | DUNE - WINK/YUKON 138 KV 2019 SUM - FUTURE (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1106 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | DVCPA1C21B_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 102.1317 | 100.4472 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | DVCPA1C21B_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 100.109 | 100.3617 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_AMOCOOIL_CC2_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0297 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_AMOCOOIL_CC2_TRAIN_NSO | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.04 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_B_DAVIS_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 100.2998 | 100.4367 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_BASTEN_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 102.253 | 103.2233 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_BOSQUESW_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0867 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_BOSQUESW_CC2_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2292 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_BRAUNIG_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4819 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_BTE_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0491 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_BVE_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0305 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_BYU_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0047 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_CBECII_CC3_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1107 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_CBY4_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0304 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_CCEC_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2451 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_CHE_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0527 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_CVC_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0527 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_DDPEC_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1235 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_DIB_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0027 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_DUKE_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3409 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_ETCCS_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1775 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_FERGCC_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 104.6862 | 104.9234 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_FLCNS_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0886 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_FORMOSA_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1488 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_FREC_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1238 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_FREC_CC2_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1768 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_FRNYPP_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5275 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_FRNYPP_CC2_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5255 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_FTR_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1616 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_GUADG_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5352 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_GUADG_CC2_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5326 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_INGLCOSW_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3097 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_JACKCNTY_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3373 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_JCKCNTY2_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3835 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_KMCHI_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3197 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_KMCHI_CC2_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.322 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_LGE_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2209 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_LOSTPI_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1354 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_LPCCS_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2818 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_LPCCS_CC2_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2599 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_NEDIN_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 100.0988 | 100.5117 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_NUECES_B_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 101.1741 | 100.4316 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_OECCS_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.422 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_OECCS_CC2_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4233 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_PANDA_S_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4023 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_PANDA_T1_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7525 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_PANDA_T2_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6942 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_PSA_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.027 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_PSG_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0289 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_QALSW_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1741 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_QALSW_CC2_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1706 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_RAYBURN_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0447 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_SANDHSYD_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | 107.9078 | - | - | - | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_SILASRAY_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.014 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_TEN_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1423 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_TGCCS_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.363 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_THW_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_THW_CC2_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_TNSKA_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0924 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_TXCTY_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0086 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_VICTORIA_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0988 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_WCPP_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4999 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_WFCOGEN_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0053 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_WHCCS_CC1_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4559 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E_WHCCS2_CC2_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7112 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E5DVA1C1_1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 103.0493 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E5DVA1C1_1_B_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.4779 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E5LCA1C1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1902 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E5P4A1C1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2054 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | E5SCA1C1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0254 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ELGIN-BUTLER-GIDEON (SINGLE B TO B ) B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1969 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ELMAX_POI_Con | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0324 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ELPATR_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0893 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1848 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ERIKA_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0985 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_000099BENHURUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0219 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_000575JCKCNTY5UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4182 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_000579JCKCNTY8UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3083 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_000971PRUITT_8US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0344 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_001700TOCO_8US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0015 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_001729VAL_STH_5UB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0016 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_001777PARIS_8US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.036 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_001877MITCHBND_5UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1703 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_003306STEKLY_DAM_5US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0652 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_003321REDLAND_5UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.247 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_003377LITTLEPOND_5US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0259 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_003391JEWETT_N5US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0052 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_003420TEMP_PEC__8US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1291 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_003423KILL_SS__8UB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0583 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_003478NAVARRO1_8US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0398 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_003706GIBSON_5US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0117 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_003707CANNON_8US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2433 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_003717TORTOISE_5UB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1786 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_003717TORTOISE_5US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5432 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_003717TORTOISE_5US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3814 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_005506FURHMANSW8US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0013 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_005660ORANGEGRVSW8US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0398 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_005700MIRCLLAKSUB8US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0449 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_006100OKLA7AUC0 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.458 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_006111RILEY7BUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0992 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_007041L_JOHNDU5_1YUN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6655 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_007044L_MARION5_1YUN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5287 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_007048L_GARFIE5_1YUN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 101.2562 | 102.9456 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_007351L_STARCK8_1YUB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3281 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_007532L_GEORSO8_1YUBT | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.127 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_007599L_LEESVI8_1YUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1017 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_007680L_CLEASP8_1YUB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2074 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_007751L_HEADWA8_1YUB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0688 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_008003PRIMAVER4AUB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.004 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_008249ANGSTRM7AUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0942 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_008573BONILLA7AUW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1148 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_008573BONILLA7AUW2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0325 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_008707DRYFRIOUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0994 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_008736SNAPDRAG4AUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0381 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_010012METEOR_5US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3711 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_011419COODYCROSS_5UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.016 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_023906AJSWOPE_5US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0808 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_023908DEAFSMITH_5US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1801 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_023909WALLABY_5US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2442 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_023912OGALLALA_5US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0827 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_023913KRESS_5US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0714 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_040000CEDARP_B345AUC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0581 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_040700GRNBYU__B345UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0262 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_040710GRNBYU_POI8AUN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0235 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_043060SPEDWY_POI_5US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0124 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_043060SPEDWY_POI_5US4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0376 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_043990ELMATO_POI_5US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0336 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_045500T_H_W__POI_5UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0287 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_045515T_H_W__POI_8UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0249 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_059904COTTONWOODUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0753 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_060700GAUSS7AUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2111 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_060716SGSA4AUB2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0088 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_060716SGSA4AUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1718 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_068004PHNTMHLUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0723 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_068014OPENSKYUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0671 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_068025WRANGLERUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0548 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_068051REATAUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1728 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_071213L_BENEDU8_1YUB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0192 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_076026L_SODALA8_1YUB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0015 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_079000GRAYUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3454 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_079000GRAYUW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1329 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_079007YELLOWWOLFUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0667 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_080039LUCERO7AUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1261 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_080039LUCERO7AUS2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0978 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_080219LOBO7AUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1547 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_080219LOBO7AUS2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0904 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_080229CAVAZOS4AUB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0076 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_080355DELSOL7AUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0856 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_085000N_SHARPE7AUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0456 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_110014WAP_WAP_G4UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0028 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_110016WAP_WAP_G6UL6 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0502 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_110017WAP_WAP_G7UL7 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0382 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_110018WAP_WAP_G8UL8 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0373 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_110071CBY_CBY_G1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0643 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_110072CBY_CBY_G2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0646 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_110351STP_STP_G1UU1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2477 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_110352STP_STP_G2UU2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2446 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_112261SPACECI_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0206 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_112351OLDHCKRY_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0541 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_113051GARCITAS_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0562 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_113111LUNIS_CK_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1199 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_113921PARLIMNT_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0317 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120041MLSES_UNIT1UL1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3463 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120042MLSES_UNIT2UL2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3473 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120043MLSES_UNIT3UL3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3505 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120071TNP__TNP_O_1UL1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0064 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120072TNP__TNP_O_2UL2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0064 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120131OGSES_UNIT1AUL1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2179 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120132OGSES_UNIT2UL2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2181 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120141SCSES_UNIT1AUN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0387 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120142SCSES_UNIT2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1943 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120151TRSES_UNIT6UN6 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0768 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120261TREB_SLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.015 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120391STARRSOL_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0458 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120441BR_ARROW_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0189 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120442BR_ARROW_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.04 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120591STAM_SLR_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0398 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120691GLENPINE_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0101 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120751GRIMES_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0032 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120821HOPKINS_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0387 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_120871AZALEA_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.024 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_130011PB2SES_CT1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0188 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_130012PB2SES_CT2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0197 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_130013PB2SES_CT3UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0197 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_130014PB2SES_CT4UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0197 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_130015PB2SES_CT5UN5 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0206 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_132111SRWE1_UNIT1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0005 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_132311ECEC_G1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0877 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_132312ECEC_G2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0877 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_132332REROCK_UNIT1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0165 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_132333REROCK_UNIT2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0165 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_132431SIRIUS_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0403 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_132481RIGGINS_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0709 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_132731BOOTLE_UNIT1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0453 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_132781CASLGP_UNIT1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0845 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_132881LMESASLR_G1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0267 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_132941SPTX12B_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0693 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_132991BEARKAT_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0006 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_133341W_PECOS_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.03 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_133841WAYMARK_W1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0865 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134091OBERON_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0809 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134141JUNO_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0605 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134142JUNO_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0492 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134241TAYGETE_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0509 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134243TAYGETE_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0529 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134341LDRAW_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0227 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134343LGDRAW_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0407 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134441LAPETUS_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0277 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134591QUEEN_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0315 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134592QUEEN_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0315 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134593QUEEN_S3US3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0282 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134594QUEEN_S4US4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0348 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134654WHMESA_U2UW3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0003 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134701TYGTEII_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0345 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134702TYGTEII_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0345 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134751FOWLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0663 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134801PROSPERO_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0609 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134802PROSPERO_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0587 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134901GREASEW_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0472 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134902GREASE_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0511 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134951EUNICE_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0845 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_134953EUNICE_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1149 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_135011TI_SOLAR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0543 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_135012TI_SOLAR_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0504 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_135111ARAGORN_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0875 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_135181PRSPERO2_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0437 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_135182PRSPERO2_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0437 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_135321REDBARN_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1135 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_135501RDOSLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0912 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_136101BLUESKY_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0434 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_136281SHAMROCK_WUW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0042 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_136341TRBNT_PV_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1725 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_136441SWIFTAIR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0608 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_141607AEEC_5UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1164 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_141609ELK_G3UN6 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1027 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_141662SOLARA_UNIT1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0345 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_142661CBREAKS_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0058 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_142811MISAE_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0287 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_142812MISAE_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0272 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_143111NOVA1SLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.033 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_143112NOVA1SLR_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.033 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_143116SRNOVA2_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0773 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_143261CONGLI_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0178 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_143311AZURE_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0031 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_143312AZURE_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0447 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_143421PHOENIX_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0001 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_143572SAMSON_3_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0173 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_143701DELILA_1_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0274 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_143752DELILA_2_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0059 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_143961MISAE2_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2531 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_144011BRSFORK_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1268 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_144064INERTIA_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0707 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_144161NOVA2SLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0742 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_144211HRNTSLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2974 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_144261EIFSLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0658 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_144311FRYE_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0956 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_144312FRYE_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0956 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_144511TROJAN_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0393 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_144561BAKE_SLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0653 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_144562BAKE_SLR_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0653 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_144721TWOFORKS_B1UB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0066 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150021MCSES_UNIT6UN6 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0506 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150022MCSES_UNIT7UN7 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0512 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150023MCSES_UNIT8UN8 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3524 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150041GRSES_UNIT1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.136 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150042GRSES_UNIT2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2488 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150051HLSES_UNIT3UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2194 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150052HLSES_UNIT4UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2641 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150053HLSES_UNIT5UN5 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2582 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150071SPNC_SPNCE_4UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0019 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150072SPNC_SPNCE_5UN5 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0045 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150082OLIN_OLING_2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0309 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150083OLIN_OLING_3UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.062 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150084OLIN_OLING_4UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0149 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150091LHSES_UNIT1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2265 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150092LH2SES_UNIT2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3087 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150101LEG_LEG_G1UL1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2459 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150102LEG_LEG_G2UL2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2495 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150111CPSES_UNIT1UU1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7863 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150112CPSES_UNIT2UU2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7851 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150131MIL_MILLERG1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.01 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150132MIL_MILLERG2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0422 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150133MIL_MILLERG3UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1035 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150134MIL_MILLERG4UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0302 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150135MIL_MILLERG5UN5 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0302 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150151MDANP_CT1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1107 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150152MDANP_CT2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1199 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150153MDANP_CT3UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1239 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150154MDANP_CT4UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1238 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150155MDANP_CT5UN5 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1176 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150156MDANP_CT6UN6 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1187 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150721DCSES_CT10UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0089 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150722DCSES_CT20UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0089 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150723DCSES_CT30UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0082 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150724DCSES_CT40UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0089 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150741SCES_UNIT1UL1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4194 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_150962GWEC_G1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2284 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_151191DEC_AGR_AUN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0025 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_151192DEC_AGR_BUN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0025 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_151193DEC_AGR_CUN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0024 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_151194DEC_AGR_DUN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0025 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_151371LILY_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.028 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_151421STRATEGC_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0295 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_151551VISION_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0149 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_151751RADN_SLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0771 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_151752RADN_SLR_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0801 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_151971GRIZZLY_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.035 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_152081NOBLESLR_R1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0376 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_152082NOBLESLR_R2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0284 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_152131ROSELAND_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0029 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_152181SUNVASLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0288 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_152231MARKUM_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0422 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_152281ELLISSLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0111 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_152331FILESSLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0268 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_152381PISGAH_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0303 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_152431MERCURY_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0427 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_152481MERCURY_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0427 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_152581ESTONIAN_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0004 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_152582ESTONIAN_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0113 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_152731FENCESLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0134 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_153031AGUAYO_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0183 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_153141PORT_SLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0939 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_153241ANGUSSLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0121 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_153291BIGELM_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0367 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_153381FIVEWLLS_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0531 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_153382FIVEWLLS_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0215 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_153388FIVEWLLS_B1UB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0336 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_153532ELIZA_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0412 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_153631DORADO_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1635 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_153681HALO_SLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0464 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_153731TNS_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0015 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_153732TNS_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0015 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_153781JAGUARSP_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0736 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_153861TOKIO_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0809 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_153911PNGT1_PV_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3222 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_153961GAIA_SOL_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.021 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_154011MIDPOINT_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0099 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_154061DIVER_PV_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0367 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_154161LANGER_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0645 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_154221ASHCRKSL_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1329 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_154281CLINGHAM_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1296 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_154331CMPDREPV_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1468 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_154411ANOLEBES_B1UB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0055 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160002LARDVFTN_G4UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.039 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160003LARDVFTN_G5UN5 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0366 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160074PEARSAL_ENG1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0095 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160075PEARSA_ENG10UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0095 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160076PEARSA_ENG13UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0095 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160077PEARSA_ENG19UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0095 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160101B_D_B_DAVIG1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1755 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160131SAN_SANMIGG1UL1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3001 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160151INGLCOS_CTG1UPE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0713 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160152INGLCOS_CTG2UPE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0713 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160153INGLCOSW_STGUPE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0689 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160201LGE_LGE_GT1UPE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0635 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160202LGE_LGE_GT2UPE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0633 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160203LGE_LGE_STGUPE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0149 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160261CCEC_GT1UPE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0527 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160262CCEC_GT2UPE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0527 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160263CCEC_ST1UPE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0613 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160274SIL_SILAS_10UNA | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.003 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160291PENA_UNIT1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0377 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160292PENA_UNIT2UW2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0288 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160293PENA_UNIT3UW3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0099 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160296BAFFIN_UNIT1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0095 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160297BAFFIN_UNIT2UW2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0104 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160391PAP1_PAP1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0379 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160392COTTON_PAP2UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0482 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160491TGW_T1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0289 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160492TGW_T2UW2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.029 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160691REDFISH_G1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0118 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160693REDFISH_G2UW2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0136 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160741LV1_LV1AUW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0619 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160742LV1_LV1BUW2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0622 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_160982CAMWIND_G1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0451 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_161032REDGATE_G1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_161033REDGATE_G2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_161034REDGATE_G3UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_161035REDGATE_G4UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_161103BRDS_JAVEL20UW2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0037 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_161451CHAWND_UNIT1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0296 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_161452CHAWND_UNIT2UW2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0066 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_161501MIDWIND_UNIUW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.031 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_161602SANROMAN_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0123 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_161651PATWND_UNIT1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_161751BBREEZE_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.021 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_161752BBREEZE_W2UW2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0153 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_161951STELLA_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0559 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162001KNKWA1_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.01 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162002KNKWA1_W2UW2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.01 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162051KNKWA2_W3UW3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0088 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162152ELRAYO_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0111 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162153ELRAYO_W2UW2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0102 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162251CHALUPA_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0487 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162301PALMWIND_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0345 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162541MCLNSLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1043 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162691ELTRUENO_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0202 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162692ELTRUENO_W2UW2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0233 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162741LMJDSW_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0175 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162742LMJDSW_W2UW3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0317 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162791HRZN_SLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1037 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162841ELARA_SL_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0554 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162861MORRLAKE_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0326 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162862MORRLAKE_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0327 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162911BLACKJAK_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0123 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_162912BLACKJAK_W2UW2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0123 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_163021NEBULA_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0504 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_163071ALGODON_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0378 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_163221CORAZON_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0891 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_163321SPARTA_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0539 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_163322SPARTA_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0279 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_163411ELSAUZ_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0369 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_163412ELSAUZ_W2UW2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0346 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_163521PEREGRN_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1246 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_163571JACKALOPE_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0035 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_163572JACKALOPE_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0037 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_163641CHARGER_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1797 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_163691REDONDA_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1195 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_163811SIETWIND_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0307 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_163881TULSITA_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1127 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_163931OUTPOST_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.291 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_164071MONTECR1_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0051 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170011INKS_INKS_G1UH1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0435 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170021AUS_AUSTING1UH1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0491 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170021AUS_AUSTING1UH2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0546 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170031MAR_MARSFOG1UH1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.331 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170032MAR_MARSFOG2UH2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3223 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170033MAR_MARSFOG3UH3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3631 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170041WIR_WIRTZ_G1UH1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.114 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170042WIR_WIRTZ_G2UH2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1239 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170051MAR_MARBFAG1UH1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.136 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170052MAR_MARBFAG2UH2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1353 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170063LEON__LCPCT1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0119 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170064LEON__LCPCT2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0118 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170065LEON__LCPCT3UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.012 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170066LEON__LCPCT4UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.012 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170071GID_GIDEONG1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1946 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170072GID_GIDEONG2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8102 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170073GID_GIDEONG3UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 100.2704 | 102.9942 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170126CALAVER_JKS2UL2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 104.9355 | 100.7932 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170137BRAU_VHB6CT5UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0223 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170138BRAU_VHB6CT6UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0223 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170139BRAU_VHB6CT7UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0223 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170140BRAU_VHB6CT8UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0211 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170153DECKE_DPGT_1UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1146 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170154DECKE_DPGT_2UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1143 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170155DECKE_DPGT_3UN5 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1103 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170156DECKE_DPGT_4UN6 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1173 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170191HAY_HAYSENG1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3777 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170192HAY_HAYSENG2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3976 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170193HAY_HAYSENG3UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3953 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170194HAY_HAYSENG4UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3807 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170211SANDHSYD_SH1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.2576 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170212SANDHSYD_SH2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.4732 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170217SANDHSYD_SH6UN6 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.433 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170218SANDHSYD_SH7UN7 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.317 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170341WEBBER__WSP1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1531 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170521E_BLACK_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1638 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170571N_FORK_BTUB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.955 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170581SLCNHLS_BT1UB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3033 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170583SLCNHLS_BT2UB2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3033 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170651BIG_STAR_BTUB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0067 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170661RVRVLYS_G1UB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1831 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170662RVRVLYS_G2UB2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1832 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170671CACHENA_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.385 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170721PADUA_B1UB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0098 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170821EBELLSLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0131 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170871GIGABATT_B1UB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4828 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170881LIBRA_B1UB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0189 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170891EBONY_B1UB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0497 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170901SHLA_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0493 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_170951SHLA_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0493 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_171021AURE_SLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.023 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_171071FERDINAN_B1UB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0084 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_171091MPP_N1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6357 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_171111MANDORLA_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0241 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_171161SYPBRNCH_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6869 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_171221GRANSLR1_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1811 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_171271JNGMN_SL_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0044 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_180001BUC_BUCHANG1UH1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0554 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_180002BUC_BUCHANG2UH2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0533 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_180003BUC_BUCHANG3UH3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0593 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_180031MGSES_CT1UN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0185 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_180032MGSES_CT2UN2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0176 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_180033MGSES_CT3UN3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0176 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_180034MGSES_CT4UN4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0193 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_180035MGSES_CT5UN5 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0193 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_180036MGSES_CT6UN6 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0193 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_180456H_HOLLO_WND1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0076 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_180460HHOLLO_WND_1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0096 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_180751CAPRIDGE_CR1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0081 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_180756CAPRIDGE_CR3UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0022 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_181732HELIOS_G1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.036 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_182151EGROVESL_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0384 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_182201WL_RANCH_W1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0038 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_182251HOLSTN_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0301 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_182252HOLSTN_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0302 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_182303PHOEBE_3US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0458 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_182305PHOEBE_5US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0477 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_182501RAMBLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1002 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_182601NORTON_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0526 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_182725AVIATOR_W3UW3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.002 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_182771MAVCRK1_W_S1UW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0046 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_182821ANSON1_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0174 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_182822ANSON1_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0174 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_183071CAPRIDG4_S1US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0303 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_183172GALLOWAY_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1425 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_183221GALLOWAY2_S1US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0421 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_183271BATCAVE_BES1UB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.041 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_183351RATLIFF_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0734 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_183401JADE_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0528 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_183402JADE_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0553 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_183451CROWDEDS_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0821 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_183521ANDMDSLR_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0519 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_183522ANDMDSLR_S2US2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0541 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_183571SUNRAY_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1176 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_183621ZIER_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0835 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_183681TENNYSON_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.07 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_183781ANG_PV_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0976 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_5920EASTDCTIE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.315 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_6103NORTHDCTIE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1212 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888839BAS_RANCH_POIUC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 103.1203 | 101.2096 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888840SKULLCREEK_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0064 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888841ELMAX_POIUN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.032 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888842IRON_BELT_POIUB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0294 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888845DRY_CREEK_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0391 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888848BARRETT_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0208 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888851TRIFECTA_POIUN1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3574 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888853BIGSAMPSON_POIUW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0161 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888854PINEFOREST_POIUB1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.025 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888854PINEFOREST_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1112 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888856HOLLY_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2118 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888856HOLLY_POIUS2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1184 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888857OYSTER_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0647 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888858ARGENTA_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1595 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888859HIGHNOON_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0427 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888860RUBICONALPHA_POIUW1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0032 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888861LEON_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.023 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888865MALDIVES_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0892 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888866HANSON_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2462 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888867INDIGO_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0321 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888868CACTUS_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0325 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888868CACTUS_POIUS2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0326 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888871ELPATR_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.088 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888874VIKING_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1143 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888875THRESLR_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.011 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888877GLASGOW_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0541 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888878ERIKA_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0585 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888879BLUBIRD_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4756 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888881SOLAC_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1792 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888882BUZIOS_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1015 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888883QUANT_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1636 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888885GALAC_POIUS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0605 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_888888FEWELL_S1US1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0136 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G_RIO_TRAIN | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 105.18 | 101.8332 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | G8DVA1C1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.0284 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | GALAC_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0769 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | GLASGOW_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2685 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | GRAHAM PLANT SWITCH-TONKAWA SWITCH/COOK FIELD ROAD SWITCH 345 KV (DOUBLE B TO B)-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0215 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | GRAHAM UNIT 2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2488 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | GRAPHIC_GAS_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.001 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | GreenRD Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0499 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | HANSON_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2459 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | HART_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0125 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | HC-SW¦MF | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1998 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | HIGHNOON_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0576 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | HOLLY_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4446 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | HUTTO - ROUND ROCK CKT 2 (SINGLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0748 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | HUTTO - ROUND ROCK/GEORGETOWN SOUTH (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.192 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | 101.6298 | - | 103.2203 | - | - | 107.1509 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | INDIGO_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0623 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | IRON_BELT_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0636 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | J5CT1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2874 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | J5CT2_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2463 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | J5CT3_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2581 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | J5GSU1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2874 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | J5GSU2_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2463 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | J5GSU3_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2581 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | J5GSU4_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5883 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | J5LCA1C1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 105.2586 | 101.8633 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | J5ST1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5883 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | JEWETT-BALE*TWINOAK_5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0333 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | JUNG_SLR_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.006 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | JW-CROCKETT (SINGLE B TO B)-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0104 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | JW-CROCKETT (SINGLE B TO B)-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0104 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | KILLEEN SS - RUSSELL GAP / BUCKHORN_5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8062 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | KILLEEN SS - SALADO SS_5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.7365 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 13.8 | 138 | Branch MVA | 107 | - | - | 100.6411 | - | - | 103.2616 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | 102.7478 | - | - | 105.9713 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000004IOLA-120332BLUEJAY_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0047 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000064MILANO-003683MINERVA1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3242 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000064MILANO-003707CANNON_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.331 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000113TURNBOR-000115DINGDONGC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4661 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000113TURNBOR-000117CEDARVALLYC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4651 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000114BARTLETTSW-000122SCHWERTNERC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9287 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000114BARTLETTSW-000132BELLCNTY8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9864 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000115DINGDONG-003630COPPERCV1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4039 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000116SALTY-003701ROOKIE_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2878 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000116SALTY-003712TORTOISE_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2983 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000117CEDARVALLY-000136TRIMMIERC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7361 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000120TALBRTRIDG-003678ROCKDALE1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2159 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000120TALBRTRIDG-003683MINERVA1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2326 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000121SONTERRA-003688JARRELL_E_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7213 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000121SONTERRA-013640SALADO_S1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8364 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000122SCHWERTNER-007346L_GABRIE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8025 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000126POAGE-000131SEATON9C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0598 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000126POAGE-003636TEMPTAYV1_9C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0974 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000128CHAPPARAL-000136TRIMMIERC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8116 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000128CHAPPARAL-003423KILL_SS__8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8089 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000130SEATON8-003415TEMP_SS__8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0152 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000132BELLCNTY8-003415TEMP_SS__8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.4766 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000132BELLCNTY8-003640SALADO1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.2117 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000133BELLCNTY9-003636TEMPTAYV1_9C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0216 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000137MOODY-000138JUDITHC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0257 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000137MOODY-000141MOFFATC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0216 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000138JUDITH-000161MCGREGORC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0241 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000139LAKEBELTON-000141MOFFATC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0115 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000157GATESVILLE-000158PANCAKEC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0766 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000157GATESVILLE-000250FRTGATESSWC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0193 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000161MCGREGOR-000165WINDSORSWC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0274 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000165WINDSORSW-000173CRAWFORDC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0484 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000173CRAWFORD-000177BOSQUEC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0574 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0119 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0126 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000240WHITNEY5-000246BOSQUESW5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0035 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000842GPL_KINGMTSW-000843GPL_KINGMTTPC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2382 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.348 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000860GPL_GIRVINSW-136341TRBNT_PV_S1C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1725 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000902POES31569-000981SPNCRINT69C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.049 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_000967GIBN_CREK_5-044920MISSIO_POI_5C18 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0003 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001067GOLDENSW_8-180653CSEC_1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0067 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2649 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001141HOLTSS_8-132313ECEC_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2149 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001163LAMESA_8-132883LMESASLR_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0581 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001333MCDONALD_8-131143MCDLD_1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0054 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001441COMCHESS1_8-001653MERCERSGAP_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0091 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001444BROWN_5-003348RUSSELLGAP_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0131 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001444BROWN_5-151756RADN_TLINEC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1997 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001466BYRDSW_5-143525AJAX_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.02 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001653MERCERSGAP_8-001654ZEPHYR_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0639 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001653MERCERSGAP_8-151035LGW_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0366 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001654ZEPHYR_8-001655BRNWDSW_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0589 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001655BRNWDSW_8-007070L_GOLDTH8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3952 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001656BRNWD_S_8-001661BRNWD1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0039 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001685FARMVLSW_5-011689CYCLONE_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0062 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001690VALLYSES1_5-002373ANNASW_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0085 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.705 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.051 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001696MOSES1_T5-888854PINEFOREST_POIC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001730W_KRUM_5-152087NOBLESLR_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1255 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001739DENISND_T8-006949DENISDMA_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0055 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4023 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0186 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0256 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5708 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001906VENUS_S5-011886TIMBERVW_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0003 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0282 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001906VENUS_S5-015201FORBESR2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0693 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001906VENUS_S5-888857OYSTER_POIC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.103 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001906VENUS_S5-888880DES_WILL_POIC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0175 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2844 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0078 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001907VENUS_N5-015200FORBESR1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0756 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_001907VENUS_N5-068091NAVARROC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1225 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2026 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1848 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0066 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002263GELLER_8-003079SSWWT2T_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0049 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002263GELLER_8-003083WILMER1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0039 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002320WAX_N_8-002321WAX_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.003 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0051 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0018 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0005 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002372COLLINSS1_5-002373ANNASW_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0165 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1728 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1638 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002432TRICRN1_5-888878ERIKA_POIC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0216 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002434SGVLSW1_8-003076SGVL1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0116 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5275 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5255 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002461ROYSE_N5-002513ALLENSW1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0284 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1829 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_002478ROYSE_S5-002485POETRY_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0224 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003076SGVL1_8-003077KLEBRG1T_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0086 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003077KLEBRG1T_8-003079SSWWT2T_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0052 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003100MARTINLK_5-003102TYLERGND_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0274 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0555 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0685 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1243 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003133RICHLND2_5-003199CALFRESTN_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1772 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003134RICHLND1_5-003186CALPFREST_5C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1239 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003134RICHLND1_5-003380BIGBRNE_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0291 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1604 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003307BEULAH_5-007040L_AUSTRO5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2824 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003348RUSSELLGAP_5-003422KILL_SS__5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3037 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003361ROSENTHAL_8-003544CASTLEMAN_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0031 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003366WARRIORTRL_8-013610BELTONSW1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0064 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0985 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003374FILESVALY_5-068090SAMSWC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0445 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003377LITTLEPOND_5-003687BELL_E_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0826 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0469 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003381BIGBRNW_5-003391JEWETT_N5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0962 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003381BIGBRNW_5-068091NAVARROC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0161 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003384STJOHNS_5-003409LAKE_CRK1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1343 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003384STJOHNS_5-003711BALE_S5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0963 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003385COWBAYOU_8-003420TEMP_PEC__8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0332 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003385COWBAYOU_8-151703CROWN_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0069 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003385COWBAYOU_8-152033GOLINDA_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0082 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003386OUTLAW_5-046020LIMEST_POI_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.139 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003386OUTLAW_5-068091NAVARROC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2201 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003386OUTLAW_5-120545BOARDCRK_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.011 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003388FOURBTHRS_5-068090SAMSWC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0125 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003389FORTSMITH_5-152333FILESSLR_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0352 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003390JEWETT_S5-003711BALE_S5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0298 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003390JEWETT_S5-044645SNGLTN__B345C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0226 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003391JEWETT_N5-044645SNGLTN__B345C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.01 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003403LAKE_HALL_5-003405THOUSE__5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0157 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003403LAKE_HALL_5-151317PHILLWND_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0029 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003404BELFALLS_8-003414TEMP_SS__5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0349 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003410LAKE_CRK1_8-003567ROBINSON1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0036 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003410LAKE_CRK1_8-003702RIESEL_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0007 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7761 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | 100.3638 | - | 107.9074 | 102.4958 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003415TEMP_SS__8-003485TINROOF_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7951 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003415TEMP_SS__8-013415TEMP_SS_R_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4461 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003422KILL_SS__5-003424BUCK_H_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2991 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003422KILL_SS__5-003699SALADOSS_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1969 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003422KILL_SS__5-003699SALADOSS_5C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1969 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003424BUCK_H_5-151856PRIDDY_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0445 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003485TINROOF_8-003675ROGERS1A_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0913 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003490LNGPRAIRIE_8-152736FENCESLR_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0565 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003494DBLCREEK_8-003654RNDRCKSE1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0072 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003494DBLCREEK_8-013657STARRANCH2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2488 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003541BRUSHYCRK_8-003690BATTLEGRND_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0138 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003541BRUSHYCRK_8-003693MALLARD_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1507 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003541BRUSHYCRK_8-003712TORTOISE_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2476 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003541BRUSHYCRK_8-170665RVRVLYS3_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4537 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003549DONAHOE_9-003647BARTLETT1_9C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0255 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003610BELTON1_8-003617NOLANVIL1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0069 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003610BELTON1_8-013610BELTONSW1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0284 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003630COPPERCV1_8-007061L_COPPCO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0741 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003640SALADO1_8-013640SALADO_S1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9671 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003643TEMP_SS__9-003644TEMPLE1_9C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1742 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003643TEMP_SS__9-888873JUNG_SLR_POIC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.006 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003644TEMPLE1_9-003645LITRIVER1_9C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1758 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003645LITRIVER1_9-013646CATHEY_CR_9C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0517 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003646HOLLAND_9-013646CATHEY_CR_9C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0236 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003646HOLLAND_9-013647BARTLET_T_9C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0247 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003647BARTLETT1_9-013647BARTLET_T_9C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0247 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003654RNDRCKSE1_8-013664PFLGRVILS2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0344 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003656HUTTO_SUB2_8-013656STARRANCH1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0318 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003657HUTTO_SUB1_8-013657STARRANCH2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7345 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003658TAYLOR1_8-003659THORNDLN1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4599 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003658TAYLOR1_8-003690BATTLEGRND_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0044 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003658TAYLOR1_8-003693MALLARD_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2864 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003659THORNDLN1_8-003701ROOKIE_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5047 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003664RNDRCKWH_T_8-003667RNDRCKNE2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.7096 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003664RNDRCKWH_T_8-003669RNDRCKWH1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.7116 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003665PFLGRVIL1_8-013656STARRANCH1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0354 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.5482 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003666HUTTOSS1_8-003670RNDRCKNE1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.4279 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003668RNDROCK1_8-003670RNDRCKNE1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.573 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003668RNDROCK1_8-007367L_SPANOA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3021 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003669RNDRCKWH1_8-007532L_GEORSO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7993 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003672RNDRCK_S1_8-007288L_WELLBR8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0318 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003675ROGERS1A_8-003750VOSSLAKE_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.093 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003677MIDNIGHT_8-007532L_GEORSO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4739 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003678ROCKDALE1_8-003740SLRPRTY_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0634 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003687BELL_E_5-003705BRANGUS_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1729 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003688JARRELL_E_8-007346L_GABRIE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4543 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 103.0854 | 105.522 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 103.0854 | 105.522 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003696HUTTOSS__5-007341L_LIMMER5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0322 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003696HUTTOSS__5-007341L_LIMMER5_1YC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0321 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003702RIESEL_8-153195CORAL_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0239 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003705BRANGUS_5-003706GIBSON_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0591 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003711BALE_S5-153733TNS_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0404 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003712TORTOISE_8-003713TOR_SR2_8C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3676 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003712TORTOISE_8-003714TOR_SR1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3676 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_003717TORTOISE_5-007040L_AUSTRO5_1YC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2898 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005003ANDERSON-005054CAGNON2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0162 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005056CAGNON_5-005231HOWARD_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0722 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005056CAGNON_5-005231HOWARD_5C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0791 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 107.9077 | 101.2185 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 102.6972 | 100.6099 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005133ELMCREEK-005371SKYLINE_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0301 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005133ELMCREEK-005371SKYLINE_5C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0301 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 106.2587 | 100.7815 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005133ELMCREEK-007044L_MARION5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0179 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005133ELMCREEK-007044L_MARION5_1YC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0179 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005145FALLSCTY-008186KENEDYSW4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0012 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005165FRATT-005250KIRBYC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0029 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005180GREEN_MT-170893EBONY_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0497 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005200HELOTES-005358RANCHTWNC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0069 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005231HOWARD_5-005901MIGUEL5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0174 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005231HOWARD_5-005901MIGUEL5C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0174 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005295MARTINEZ_5-005400SPRUCEC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0141 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_00529MARTINEZ_5-005400SPRUCEC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0141 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4169 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005362RIONOG_1_5-007050L_CLEASP5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1697 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005362RIONOG_1_5-007050L_CLEASP5_1YC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1689 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005380SHAULA-005915SO_TEX__345AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4093 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005400SPRUCE-005725PAWNEESW5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0013 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005400SPRUCE-005725PAWNEESW5C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0013 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005412STCKDALE-005418SUTHRLNDC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0033 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005470FAIRRA-007169L_FAIROA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.03 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005470FAIRRA-007710L_ESPERA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0214 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005502RAYBURN8-005506FURHMANSW8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.03 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005502RAYBURN8-005513RAYBURNPLNT8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0447 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005502RAYBURN8-005730FORCORNERSB8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0244 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005521GALOWSW8-005523ETPSUB8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.02 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005725PAWNEESW5-008164COLETO7AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0011 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005727PAWNEESUB8-005728CHOATESUB8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0001 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005728CHOATESUB8-005730FORCORNERSB8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0223 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005760PALMASSW8-005764ERIOHONDOSB8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0346 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005761PAREDESSW8-160981CAMWIND_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0481 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005779REDSWTAP8-005784REDGATESW8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1394 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005779REDSWTAP8-161031REDGATE_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1394 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005798AMISTAD8-008686AMISTD4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0027 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005804CSTROVILESB8-008248QUIHI4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0254 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005805RIOMEDINASB8-005804CSTROVILESB8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0047 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005819HONDOCREEK8-005827MOORESW8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0068 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005827MOORESW8-005895PEARSALLSUB8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0345 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005866PALODUROSW8-005890ELARA8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0554 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005885DOWNIESW8-181731HELIOS_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0371 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005895PEARSALLSUB8-005896MORROWSW8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1043 | -