RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005895PEARSALLSUB8-005897HORIZONSW8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1046 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005895PEARSALLSUB8-058959PEARSALLSCB8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1526 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005897HORIZONSW8-162793HRZN_SLR_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1046 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 104.0928 | 100.2345 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005915SO_TEX__345A-042400REFUGE_POI_5C27 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0146 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005915SO_TEX__345A-043990ELMATO_POI_5C64 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0095 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 104.9514 | - | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_006015MADDUX4A-060423TREADWEL4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0875 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_006015MADDUX4A-183353RATLIFF_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0734 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_006076FOXTAIL7A-060791PERIGEE7AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0055 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_006104SMOKYHIL7A-142062SALVTION_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0018 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_006111RILEY7B-141351ELECTRA_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0275 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_006216BLF_CRK4A-170250PONY_4_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0096 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_006216BLF_CRK4A-180455BUFF_GAP_2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0632 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_006216BLF_CRK4A-180457H_HOLLOW_1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0076 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_006235ABMULCW7A-888860RUBICONALPHA_POIC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0275 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_006365YELWJCKT4B-060423TREADWEL4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1685 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_006562FDRAN4A-136103BLUESKY_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0435 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_006601RIOPECOS4A-076601L_HORSCR8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0384 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_006630FTST4A-132482RIGGINS_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0709 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_006802RY_RYMOND_RC-120692GLENPINE_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0101 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_006903BOZE-151372LILY_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0349 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007040L_AUSTRO5_1Y-007042L_ZORN__5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7116 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007040L_AUSTRO5_1Y-009041LOSTPINESC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.4324 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007040L_AUSTRO5_1Y-009044DUNLAP5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6036 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007041L_JOHNDU5_1Y-007047L_HORNSB5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | 101.0594 | - | 101.2953 | 100.4465 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007041L_JOHNDU5_1Y-007050L_CLEASP5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.48 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007042L_ZORN__5_1Y-007043L_HAYSEN5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1185 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007042L_ZORN__5_1Y-007043L_HAYSEN5_1YC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.124 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007042L_ZORN__5_1Y-007044L_MARION5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1117 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007042L_ZORN__5_1Y-007044L_MARION5_1YC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.109 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007042L_ZORN__5_1Y-007050L_CLEASP5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2789 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007042L_ZORN__5_1Y-007510L_EUCLID5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 105.2705 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007042L_ZORN__5_1Y-009074LYTTON5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.6322 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007043L_HAYSEN5_1Y-007770L_BERGHE5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3271 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007044L_MARION5_1Y-007050L_CLEASP5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.004 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007046L_KENDAL5_1Y-007770L_BERGHE5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.142 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007046L_KENDAL5_1Y-060618EDISON7BC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0791 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007046L_KENDAL5_1Y-060621EDISON7DC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.079 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007047L_HORNSB5_1Y-007738L_WHISVA5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 105.249 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 102.2626 | 103.2285 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007055L_FPPYD25_1Y-009074LYTTON5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.2564 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007056L_FPPYD15_1Y-007057L_FAYETT5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0165 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007056L_FPPYD15_1Y-007058L_SALEM_5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0472 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007056L_FPPYD15_1Y-009041LOSTPINESC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5057 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007056L_FPPYD15_1Y-009042WINCHESC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2176 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007060L_EBABSM8_1Y-007063L_NARUNA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1556 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007060L_EBABSM8_1Y-007100L_BURNET8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1421 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007063L_NARUNA8_1Y-007064L_LAMPAS8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2132 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007064L_LAMPAS8_1Y-007066L_ADAMSV8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0538 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007066L_ADAMSV8_1Y-007068L_EVANT_8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.072 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007068L_EVANT_8_1Y-007070L_GOLDTH8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0976 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007070L_GOLDTH8_1Y-077074L_SASASW8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2556 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007070L_GOLDTH8_1Y-150961GWEC_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2304 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007077L_AMOSCR5_1Y-182777MAVCRK_W_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0661 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007077L_AMOSCR5_1Y-183171GALLOWAY_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2172 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007078L_SANSAB8_1Y-007080L_LOMETA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0081 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007078L_SANSAB8_1Y-077074L_SASASW8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2227 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007087L_CORONA8_1Y-007103L_BUCKRA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1186 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007087L_CORONA8_1Y-007518L_FAIRLA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5845 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007092L_BUCHAN9_1Y-007094L_INKSDA9_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0439 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007100L_BURNET8_1Y-007104L_WIRTZ_8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4654 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007100L_BURNET8_1Y-070520P_BERTRA8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8759 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007101L_CTECBU9_1Y-007116L_SANDMO9_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0084 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007102L_SHERSH8_1Y-007103L_BUCKRA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1567 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007102L_SHERSH8_1Y-007126L_FERGUS8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1977 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007104L_WIRTZ_8_1Y-007126L_FERGUS8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1057 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007104L_WIRTZ_8_1Y-007126L_FERGUS8_1YC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1088 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007104L_WIRTZ_8_1Y-007351L_STARCK8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0784 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007104L_WIRTZ_8_1Y-070111P_FLATRO8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.889 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007104L_WIRTZ_8_1Y-070516P_JOHNCI8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0494 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007114L_CASTEL8_1Y-007120L_PITSBU8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0219 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007114L_CASTEL8_1Y-076389L_MASOCT8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0286 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007121L_SANDCR9_1Y-007400L_SUNRBE9_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0505 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007126L_FERGUS8_1Y-007474L_GRANMO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2514 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007126L_FERGUS8_1Y-180015FERGGT1_1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8701 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007126L_FERGUS8_1Y-180016FERGGT2_2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8705 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007126L_FERGUS8_1Y-180017FERGST1_1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0242 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007145L_HOLLMI8_1Y-007149L_FREDER8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0351 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007145L_HOLLMI8_1Y-007150L_KENDAL8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0562 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007147L_KENDCT8_1Y-007150L_KENDAL8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3418 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007147L_KENDCT8_1Y-007419L_MAENRO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3038 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007148L_MOUNTO8_1Y-007419L_MAENRO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2247 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007148L_MOUNTO8_1Y-007479L_MILLER8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4267 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007148L_MOUNTO8_1Y-070516P_JOHNCI8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0253 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007152L_KENDAL8_2Y-007153L_WELFAR8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0336 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007153L_WELFAR8_1Y-007168L_BOERNE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0133 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007168L_BOERNE8_1Y-007710L_ESPERA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0417 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007169L_FAIROA8_1Y-007170L_BERGHE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0173 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007170L_BERGHE8_1Y-007171L_ANTLER8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0279 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007170L_BERGHE8_1Y-070493P_DEVIHI8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3326 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007171L_ANTLER8_1Y-007177L_HIGH468_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0107 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007172L_HENNE_8_2Y-007176L_COMAL_8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0792 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007172L_HENNE_8_2Y-007182L_MCCALA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.002 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007174L_HENNE_8_1Y-007179L_HUECSP8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0018 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007175L_HORTON8_1Y-007176L_COMAL_8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1475 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007175L_HORTON8_1Y-007462L_FREIHE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2369 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007176L_COMAL_8_1Y-007179L_HUECSP8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0247 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007178L_MARION8_1Y-007459L_GPISWI8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0715 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007180L_ZORN__8_1Y-007182L_MCCALA8_1YC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3238 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007180L_ZORN__8_1Y-007182L_MCCALA8_1YC3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0603 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007180L_ZORN__8_1Y-007187L_BEBACK8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.305 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007180L_ZORN__8_1Y-007222L_POOLRO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1394 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007182L_MCCALA8_1Y-007184L_RATTLE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.8066 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007182L_MCCALA8_1Y-007186L_RARO128_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2574 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007182L_MCCALA8_1Y-007187L_BEBACK8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2714 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007184L_RATTLE8_1Y-007188L_REDWOO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.6457 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007185L_LACIMA8_1Y-007186L_RARO128_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1923 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007185L_LACIMA8_1Y-007190L_HILLTO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0709 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007188L_REDWOO8_1Y-007192L_SANMAR8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0963 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007190L_HILLTO8_1Y-007193L_STRAHA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0145 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007192L_SANMAR8_1Y-007196L_CAMPGA9_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0388 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007192L_SANMAR8_1Y-007200L_CANYON8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6143 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007192L_SANMAR8_1Y-070502P_KYLE__8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7068 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007194L_ROBRJR9_1Y-007195L_CLEAFO9_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0244 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007194L_ROBRJR9_1Y-007196L_CAMPGA9_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0322 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007195L_CLEAFO9_1Y-007216L_LOCKHA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0506 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007200L_CANYON8_1Y-007515L_ROHR__8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5449 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007200L_CANYON8_1Y-070546P_HIGH328_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0394 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007202L_HICROS8_1Y-007356L_MARSFO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.114 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007208L_COLTON8_1Y-007325L_MENDOZ8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.029 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007210L_WYLDWO8_1Y-007212L_WOLFLA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2459 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007210L_WYLDWO8_1Y-007556L_BLUEBO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3175 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007216L_LOCKHA8_1Y-007560L_REDROC8_1YC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0479 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007222L_POOLRO8_1Y-007224L_LULING8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1004 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007223L_LULING9_1Y-078579L_MALONE9_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0283 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007228L_SEGUIN8_1Y-007595L_DEERCR8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0015 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007228L_SEGUIN8_1Y-007695L_JIMBRI8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0044 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007232L_WAELDE9_1Y-007247L_FLATON9_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.039 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007234L_PILOGR8_1Y-007235L_SWEEHO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0131 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007234L_PILOGR8_1Y-007242L_YOAKUM8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0038 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007235L_SWEEHO8_1Y-007249L_MONT__8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0155 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007236L_MOULTO8_1Y-007237L_MOULSO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0898 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007236L_MOULTO8_1Y-007248L_FLATON8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0937 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007237L_MOULSO8_1Y-007238L_SHINER8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0441 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007238L_SHINER8_1Y-007242L_YOAKUM8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0342 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007242L_YOAKUM8_1Y-007244L_CUERO_8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1626 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007243L_CHEAPS8_1Y-007245L_GONZAL8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0119 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007243L_CHEAPS8_1Y-007251L_LINDEN8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0469 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007244L_CUERO_8_1Y-089450THOMASTN4BC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0079 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007246L_HALLET8_1Y-007248L_FLATON8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0347 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007246L_HALLET8_1Y-007249L_MONT__8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0213 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007248L_FLATON8_1Y-007279L_MULDOO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2817 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007251L_LINDEN8_1Y-007253L_GUADAL8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0589 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007288L_WELLBR8_1Y-007335L_HOWALA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0687 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007289L_SALEM_8_1Y-007564L_GUYBUR8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0346 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007302L_GIDDIN8_1Y-007568L_LINCOL8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0086 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007306L_WINCHE8_1Y-007307L_PINECR8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0922 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007306L_WINCHE8_1Y-007308L_PAIGE_8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1096 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007306L_WINCHE8_1Y-007310L_SIMGID8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0615 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007306L_WINCHE8_1Y-007314L_SMITHV8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1401 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007310L_SIMGID8_1Y-007319L_BASTCI8_2YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.0048 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007310L_SIMGID8_1Y-007322L_BASTCI8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.387 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007310L_SIMGID8_1Y-007324L_BUTLER8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.342 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007310L_SIMGID8_1Y-007327L_SETTLE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4956 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007310L_SIMGID8_1Y-007555L_BASTWE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0567 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007310L_SIMGID8_1Y-007575L_TAHIVI8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1251 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007310L_SIMGID8_1Y-009328AUSTROP8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0375 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007319L_BASTCI8_2Y-007326L_SWIFTE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.0157 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007321L_ELGISW8_1Y-007324L_BUTLER8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2709 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007321L_ELGISW8_1Y-007338L_CARLSO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1958 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007322L_BASTCI8_1Y-007328L_SETTLE8_2YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2806 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007323L_SHADGL8_1Y-007330L_MANOR_8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3953 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007323L_SHADGL8_1Y-007333L_HARRBR8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1082 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007326L_SWIFTE8_1Y-007331L_CEDAHI8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.6062 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007330L_MANOR_8_1Y-007331L_CEDAHI8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7999 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007334L_MCNEIL8_1Y-007336L_GILLCR8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.5712 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007334L_MCNEIL8_1Y-007356L_MARSFO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0024 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007336L_GILLCR8_1Y-007339L_STEGER8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2191 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007336L_GILLCR8_1Y-013664PFLGRVILS2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0236 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007336L_GILLCR8_1Y-170582SLCNHLS_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7232 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007337L_KIMBRO8_1Y-007338L_CARLSO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1778 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007337L_KIMBRO8_1Y-007339L_STEGER8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2845 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007337L_KIMBRO8_1Y-170523E_BLACK_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1639 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007340L_GILLCR5_1Y-007341L_LIMMER5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.2889 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007340L_GILLCR5_1Y-007738L_WHISVA5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.0775 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007341L_LIMMER5_1Y-007510L_EUCLID5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.0691 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007346L_GABRIE8_1Y-007523L_GLASSC8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1402 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007348L_MARBFA8_1Y-007474L_GRANMO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0619 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007348L_MARBFA8_1Y-007538L_LAKEWA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6349 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007349L_LAKEAE8_1Y-007540L_BEECRE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1532 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007351L_STARCK8_1Y-007476L_PALEFA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4215 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007356L_MARSFO8_1Y-007538L_LAKEWA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.42 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007356L_MARSFO8_1Y-070352P_LAGOVI8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0979 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007356L_MARSFO8_1Y-070477P_PALEPE8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5519 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007356L_MARSFO8_1Y-070535P_BULLHO8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2803 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007361L_BERRCR8_1Y-007521L_FLOREN8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1084 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007361L_BERRCR8_1Y-070522P_ANDICE8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1474 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007367L_SPANOA8_1Y-007368L_RIDGMA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1726 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007368L_RIDGMA8_1Y-070525P_LEANDE8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0971 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007389L_PINNAC8_1Y-135019TI_SOLAR_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1433 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007389L_PINNAC8_1Y-135113ARAGORN_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0875 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007400L_SUNRBE9_1Y-007404L_KINGS19_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0273 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007456L_LOP3378_1Y-007459L_GPISWI8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0344 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007462L_FREIHE8_1Y-007758L_WELTRO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3489 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007476L_PALEFA8_1Y-007540L_BEECRE8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0861 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007479L_MILLER8_1Y-070513P_HENLY_8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4841 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007500L_TURNER8_1Y-009075LYTTON8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.2108 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007501L_GOFORT8_1Y-007514L_YARRIN8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0628 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007514L_YARRIN8_1Y-007515L_ROHR__8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3744 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007518L_FAIRLA8_1Y-070352P_LAGOVI8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2403 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007521L_FLOREN8_1Y-007523L_GLASSC8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0206 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007534L_AVERRA8_1Y-009223JOLLYVILC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2367 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007555L_BASTWE8_1Y-007556L_BLUEBO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7055 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007560L_REDROC8_1Y-007576L_HILBIG8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0777 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007575L_TAHIVI8_1Y-007576L_HILBIG8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0911 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007595L_DEERCR8_1Y-007599L_LEESVI8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0983 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007597L_DEERCR9_1Y-078195L_DARSCR9_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0552 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007604L_GERONI8_1Y-007680L_CLEASP8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0974 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007604L_GERONI8_1Y-007695L_JIMBRI8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0136 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007672L_ESCARP8_1Y-070504P_MANCHA8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0567 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_007680L_CLEASP8_1Y-007758L_WELTRO8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3778 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008117GANADO4A-008118EDNA4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0564 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008117GANADO4A-008192PULSAR4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0587 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008118EDNA4A-008172VICTORIA4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0475 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008127LAN_CTY4A-008130LAN_CTY4BCS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0399 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008140JOSLIN4A-120263TREB_SLR_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.015 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008144SEADRFTC4A-008189TUNGSTEN4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0153 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008144SEADRFTC4A-080065MELNCRK4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0153 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008162COLETO4A-008172VICTORIA4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0282 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008162COLETO4A-008172VICTORIA4AC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0332 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008172VICTORIA4A-008174LPLDPOI4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0046 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008172VICTORIA4A-110883VIC_SU5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0293 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008172VICTORIA4A-110884VIC_SU6C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0412 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008186KENEDYSW4A-008590TULETA4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0133 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008209SHAKEPOI4A-162543MCLNSLR_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1044 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008221BIG_FOOT4A-008732DEVINE4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.003 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008241RZBK4A-008248QUIHI4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0289 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008241RZBK4A-008707DRYFRIOC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0318 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008266MARCONI4A-161601SANROMAN_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0127 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008318RIOHONDO7A-162745LMJDSW_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.099 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008319RIOHONDO4A-160750LV1_AB_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1628 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008380NEDIN4A-160234NEDIN_1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1335 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008380NEDIN4A-160235NEDIN_2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1335 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.194 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008458B_DAVIS4A-160105B_DAVIS_1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1755 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008458B_DAVIS4A-160106B_DAVIS_2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1956 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008458B_DAVIS4A-160107B_DAVIS_3_9C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0764 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008458B_DAVIS4A-160108B_DAVIS_4_9C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0764 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008574POMELO7A-161705MIRASOLE_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0169 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008590TULETA4A-008731BASIL4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0121 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008601CEBOLLA7A-008902RIOHONDO7CC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0078 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008640KELVIN4A-088640CHLPAPOI4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0614 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008663ELSUZPOI7A-163415ELSAUZ_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1093 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008715RADIANT7A-008728COBRA7AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5979 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008728COBRA7A-081003HABER7AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7473 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008732DEVINE4A-008962LYTLE4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0037 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008795ROMA_SW4A-088795STARRPOI4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0458 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008963HEC4A-008981HECGT14AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0808 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008963HEC4A-008983HECST14AC3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.096 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008980FRONTERA4A-160180FRONT_EC_C1TC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1048 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008980FRONTERA4A-160181FRONT_EC_C2TC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1048 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_008980FRONTERA4A-160182FRONT_EC_STTC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1108 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009041LOSTPINES-009042WINCHESC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4008 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009041LOSTPINES-009044DUNLAP5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.3745 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009043CISTERN-009073HOLMANC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6598 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009043CISTERN-009074LYTTON5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.5445 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009045DUNLAP8-009188DECKER_MB3C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7163 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009045DUNLAP8-009188DECKER_MB3C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7163 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009045DUNLAP8-009195EAST_VILLAGEC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.3223 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009054GILLE138-009191TRIDGE_MB2C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.0151 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009071GARFIELD8-009143EASTONPARKC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.9958 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009075LYTTON8-009259PILOTKNOBC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2096 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009075LYTTON8-009262BLUFFSPGC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.258 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009076MCNEIL_DB1-009193DESSAUC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2028 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009077MCNEIL_MB3-009276KRAMERC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2091 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009079MCNEIL_MB1-009193DESSAUC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2056 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009079MCNEIL_MB1-009217HOWARDLNC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0032 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009079MCNEIL_MB1-009279SUMMIT_MB1C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.426 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009080MCNEIL-009225JUSTINLNC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3106 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009082MC1013BT-009188DECKER_MB3C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4566 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009117PE_MB3-009151AMDC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3766 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009119PE_MB2-009166BRACKC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0181 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009120BURLSN_MB1-009175CARSONC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.276 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009121BURLSN_MB2-009148HICROS_MB1C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.03 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009121BURLSN_MB2-009179CARDINALC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7952 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009122KINGSB_MB1-009196EDBLUESTNC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2326 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009122KINGSB_MB1-009200GROVEC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1287 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009122KINGSB_MB1-009284WALNUTCKC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2916 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009123KINGSB_DB1-009342MUELLERC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.163 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009125KINGSBERY-009214HOLLY_MB3C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2805 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009128NORTHL_MB1-009238MAGPLANTC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1059 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009132SEAHOLM-009139AUSTNDAMC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2256 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009132SEAHOLM-009179CARDINALC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2719 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009139AUSTNDAM-009160BEECREEK_MB1C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0966 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009143EASTONPARK-009147HICROS_DB1C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.775 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009148HICROS_MB1-009263SALEMWLKC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0385 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009148HICROS_MB1-009263SALEMWLKC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0387 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009151AMD-009200GROVEC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2287 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009158BARTON-009183COMMONFDC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0697 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009158BARTON-009263SALEMWLKC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2849 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009169BRODIE-009247OAKHILLC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1713 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009169BRODIE-009267SLAUGHTRC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4605 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009171CAMERON-009199FISKVILC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1706 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009171CAMERON-009291WHELESSC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.119 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009175CARSON-009259PILOTKNOBC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3763 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009184DAFFIN-009271SPRNKL_MB2C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1844 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009184DAFFIN-009328AUSTROP8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.5743 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009187DECKER_MB1-009196EDBLUESTNC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4314 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009187DECKER_MB1-009284WALNUTCKC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5056 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009190TRIDGE_MB1-009195EAST_VILLAGEC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0443 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009190TRIDGE_MB1-009226ASHTONW_MB1C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.652 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009191TRIDGE_MB2-009217HOWARDLNC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0391 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009193DESSAU-009271SPRNKL_MB2C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1404 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009193DESSAU-009272SPRNKL_MB1C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1514 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009202HAMLTN_MB2-009280SUMMIT_MB2C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1327 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009207HIDDENVL-009260RIVERPLACEC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0526 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009220JETT-009260RIVERPLACEC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0015 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009223JOLLYVIL-009224ASHTONW_MB2C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6596 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009223JOLLYVIL-009245NORTHWESTC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0015 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009225JUSTINLN-009227KOENIGC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1162 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009238MAGPLANT-009276KRAMERC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1575 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009247OAKHILL-009253PATTON_MB1C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0011 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009262BLUFFSPG-009267SLAUGHTRC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0876 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009275STECK-009283UTBALCC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0376 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009279SUMMIT_MB1-009295WILIAMSNC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0382 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009287WEBBERSOL-009328AUSTROP8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1557 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_009291WHELESS-009342MUELLERC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1642 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_011048TONKAWAW_5-011318SCURCNTYS_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0029 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_011048TONKAWAW_5-011318SCURCNTYS_5C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0029 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_011083RIVERTON_8-133342W_PECOS_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.03 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_011270DOGHOUSE_5-023876CLEARFRK_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3287 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_011270DOGHOUSE_5-134805PROSPERO_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.158 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_011270DOGHOUSE_5-135183PRSPERO2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1245 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_011273NELSON_8-135503RDOSLR_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0912 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_011306DERMOTT_8-181953FLUVANNA_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0155 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_011319SCURCNTYS_8-183025CANYONWD_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0149 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_011406CENTBLUF_5-182255HOLSTN_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0972 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_011418TECUMSEH_5-151808VORTEX_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0336 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_011688THORNTRE_5-143625SAMSON_1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1027 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_011688THORNTRE_5-143705DELILA_1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1243 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_011809COPPERHD_8-143424PHOENIX_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0001 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_013401TIGERCK_5-068090SAMSWC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0205 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_013430SAND_TXU_8-013441SANDOW_SR1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.45 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_013430SAND_TXU_8-013442SANDOW_SR2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4431 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1267 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1181 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_023900ALIBATES_5-140653GRANDVW1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0461 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_023906AJSWOPE_5-140442SSPURTWO_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0344 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_023910WINDMILL_5-140753HRFDWIND_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0637 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_023910WINDMILL_5-141765MARIAH_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0096 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_023914TULECNYN_5-140853LHORN_NC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0041 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_023920ABERNATH_5-141607AEEC_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2642 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_023924FARMLAND_5-133641TAHOKAW_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0722 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_023924FARMLAND_5-888856HOLLY_POIC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0118 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_038021TNWORSHAM_1-136153RODEORNCH_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0174 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_038745TNATTWATER1-111971TOPAZ_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0188 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_040000CEDARP_B345A-110076CBY4_1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0304 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_040010CEDARP_B138A-049201GENGBY2_02_8CGL | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0646 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_040600ROANS__POI_5-044645SNGLTN__B345C75 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0775 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_040715GRNBYU_POI8B-049211GENGBY7_08_8CGL | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0056 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_042010P_H_R___B138-111131BAC_8C92 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0049 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_042150BASF___POI_8-042210BRZPRT_S02_8C02 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0004 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_042150BASF___POI_8-042810HOFMAN_X02B8C02 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0077 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_042215COPPER_X02B8-042540JONCRK__B138C&1-MS | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0209 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_042420BEASLY_POI_8-044190E_BERN__B138C60 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1005 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_042420BEASLY_POI_8-044541ORCHRD_T60_8C60 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2352 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_042810HOFMAN_X02B8-042880LKJACK_S02_8C02 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0081 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_042880LKJACK_S02_8-043170RETREV__B138C&1-MS | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0149 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_042985DYANN__POI_8-043190S_LANE__B138C60 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0331 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_043090PYTHIA_POI_8-043110SANBER_POI_8C60 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0192 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_043090PYTHIA_POI_8-043380W_COL__POI_8C60 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.027 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_043110SANBER_POI_8-043340GLFTIE_POI_8C&1-MS | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0054 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_044000W_A_P__POI5A-049205GENWAP6_06_5CGL | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0502 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_044000W_A_P__POI5A-049206GENWAP7_07_5CGL | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0382 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_044005W_A_P__POI5B-049207GENWAP8_08_5CGL | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0373 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_044200HILLJE__B345-111637DANISH_5C01 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0281 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_044200HILLJE__B345-112147PLN_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0106 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_044280FTBEND__B138-044615ROSNBG_S60_8C60 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1689 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_044540ORCHRD_S60_8-044615ROSNBG_S60_8C&1-MS | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2277 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_044650SMTHRS_POI_5-112419RABBS_5C01 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0053 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_044860TWINWD_S25_8-046220PETERS__B138C25 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0037 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_044880WATERH_POI_5-112878GSTAR_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0061 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_045500T_H_W__POI_5-049204GENTHW5X05_5CGL | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0111 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_045515T_H_W__POI_8-049202GENTHW3X03_8CGL | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_045515T_H_W__POI_8-049203GENTHW4X04_8CGL | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_045880HOCKLY__B138-046220PETERS__B138C&1-MS | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0202 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_046020LIMEST_POI_5-068091NAVARROC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1545 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_046020LIMEST_POI_5-079007YELLOWWOLFC50 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.011 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_047170H_O_C__POI_8-111800PRO_8C01 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0016 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_059900LONG_DRAW-132114SRWE1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0293 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_059900LONG_DRAW-181553MESQCRK_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0005 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_059903BEARKAT-132993BEARKAT_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0314 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_059904COTTONWOOD-140903WAKE_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0172 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_059906LONGDRAW_138-134145JUNO_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1485 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_059906LONGDRAW_138-134342LGDRAW_S8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1005 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_059907BERNOULLI-133442LACY_CRK_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0216 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_059909NOVA_138-059998NOVA8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3388 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_059909NOVA_138-143115NOVA1SLR_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2192 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_059909NOVA_138-144163NOVA2SLR_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0742 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_059911MHOS-183406JADE_HI_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1709 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060011NEBULA7A-183525ANDMDSLR_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.144 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060383LINTERNA4A-060385SOLSTICE4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0306 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060383LINTERNA4A-132331REROCK_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0699 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060387HENDRICK4A-141663SOLARA_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0347 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060393PIGCREEK4A-134245TAYGETE_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1419 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060393PIGCREEK4A-134705TYGTEII_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1064 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060451GARNET4A-182603NORTON_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0526 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060464AZUREPOI7A-060514CLEARCRO7BC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0956 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060500EDITHCLA7A-142563FOARDCITY_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.018 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060504TESLA7B-142815MISAE_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0936 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060616EDISON7A-060709OERSTED7BC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0843 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060619EDISON7C-060711OERSTED7DC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0843 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060708OERSTED7A-076003L_BIGHIL5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0839 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060710OERSTED7C-076003L_BIGHIL5_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0838 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060715FIGARO7A-182404WKNAMAD1C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0037 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060722COULOMB7A-143015VERA_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0011 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060728PALOUSE4A-135734APPALOSA_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.001 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_060791PERIGEE7A-143222APOGEE_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0298 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_061001JIMTREEC7A-140383BLSMT1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0363 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_068001CLAYTON_345-068014OPENSKYC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0247 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_068001CLAYTON_345-182455WHITHRSE_4_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0339 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_068008LATIMER-151265BAIRDWND_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0134 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_068011ASPIRE-151602ANCHOR_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0097 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_068051REATA-153433SHEEPCRK_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0038 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_068090SAMSW-068092LIBERTYC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1602 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_068092LIBERTY-152433MERCURY_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1233 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070111P_FLATRO8_1_-070477P_PALEPE8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8194 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070198P_LEHIGH8_1_-070498P_BUDA__8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0959 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070198P_LEHIGH8_1_-070502P_KYLE__8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3768 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070352P_LAGOVI8_1_-070526P_NAMELE8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1972 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070390P_PIPELI8_1_-070522P_ANDICE8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2148 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070390P_PIPELI8_1_-070524P_SEWAJU8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1548 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070482P_BLANCO8_1_-070493P_DEVIHI8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0252 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070487P_CANYHY8_1_-070488P_SATTLE8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1852 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070487P_CANYHY8_1_-070492P_FISCHE8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1906 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070488P_SATTLE8_1_-070489P_PURGRO8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1462 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070488P_SATTLE8_1_-070490P_CRANMI8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0194 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070489P_PURGRO8_1_-070491P_HUNTER8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2075 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070490P_CRANMI8_1_-070493P_DEVIHI8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1036 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070496P_WIMBER8_1_-070511P_CEBOCR8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0798 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070496P_WIMBER8_1_-070546P_HIGH328_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1999 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070498P_BUDA__8_1_-070504P_MANCHA8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1615 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070498P_BUDA__8_1_-070509P_RUTHER8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0431 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070506P_CEDAVA8_1_-070507P_FRIEND8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2004 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070507P_FRIEND8_1_-070509P_RUTHER8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.078 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070509P_RUTHER8_1_-070511P_CEBOCR8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1948 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070511P_CEBOCR8_1_-070512P_DRIPSP8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0564 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070512P_DRIPSP8_1_-070513P_HENLY_8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3723 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070520P_BERTRA8_1_-070522P_ANDICE8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5207 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070522P_ANDICE8_1_-170572N_FORK_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9556 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070524P_SEWAJU8_1_-070525P_LEANDE8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1592 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070526P_NAMELE8_1_-070536P_HEROWA8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0436 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070531P_BUTTER8_1_-070533P_BALCON8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0575 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_070533P_BALCON8_1_-070535P_BULLHO8_1_C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2723 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_071050L_BITTCR5_1Y-180161SWEETWN4_1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0554 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076002L_BAKERS5_1Y-132732BOOTLEG_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0453 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076002L_BAKERS5_1Y-133843WAYMARK_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0865 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076002L_BAKERS5_1Y-135327REDBARN_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1326 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076003L_BIGHIL5_1Y-182203WL_RANCH5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0054 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076004L_SINGTR5_1Y-136283SHAMROCK_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0084 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076005L_SCHNDR5_1Y-132632SANTRITA_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0814 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076005L_SCHNDR5_1Y-134651WHMESA_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0641 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076006L_BOWWOO5_1Y-182051RTS_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0333 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076015L_CEDACA5_1Y-134512HILO_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0823 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076026L_SODALA8_1Y-135485CROSBAT_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0001 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076040L_CASTIL8_1Y-132783CASL_GAP_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0863 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076040L_CASTIL8_1Y-132943SPTX12B_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0738 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076090L_DIVIDE5_1Y-180759CAPRIDG4_1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0841 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076090L_DIVIDE5_1Y-182727AVIATOR_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0651 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076389L_MASOCT8_1Y-076390L_FORTMA8_1NC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0556 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076390L_FORTMA8_1N-183272BATCAVE_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0411 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_076601L_HORSCR8_1Y-182154EGROVESL_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0384 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_078195L_DARSCR9_1Y-078579L_MALONE9_1YC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0061 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_078207L_HIDDVA8_1Y-078220L_BARETA8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.006 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_078255L_PINTCR8_1Y-183623ZIER_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0917 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_079000GRAY-140473MIAMI_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0212 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_079005RAILHEAD-140503PH1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0071 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_079005RAILHEAD-140603PH2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0017 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080013LARDVNTH4A-160009LARDVFTN_1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.039 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080013LARDVNTH4A-160010LARDVFTN_2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0366 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080071ZORILLO7A-080076AJO7AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3857 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080071ZORILLO7A-080171SARITA7AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2475 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080072STELPOI7A-080076AJO7AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0562 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080072STELPOI7A-161953STELLA_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.056 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080171SARITA7A-160299BAFFIN_2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2474 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080210TORRPOI7A-161257TORCILAS_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0171 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080219LOBO7A-163223CORAZON_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1229 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080220CENIZO7A-161105BORDAS_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0423 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080224TIEMPO7A-162499RELOJ_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0005 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080227RAPIDO7A-161855CABEZONC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0055 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080259PELICAN4A-160394COTTON_1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0482 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080259PELICAN4A-160395PAP1_1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0379 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080260GILA4A-160095NUECES_B_2_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0757 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080260GILA4A-160096NUECES_B_3_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0756 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080309LASPULGA4A-160694REDFISH_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0628 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080355DELSOL7A-080368LV4BRDG7AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0343 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080439LAQUINTA4A-160592CEDROHIL_1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.004 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080503SANTASW4A-085001N_SHARPE4AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0738 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080503SANTASW4A-161455CHAWIND_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0738 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_080509LADKPOI7A-161753BBREEZE_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0734 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_085008PATPOI7A-161653PATWIND_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0652 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_088173JCKSLPOI4A-163575JACKALOPE_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0445 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_088573ERAYPOI7A-162151EASTRAY_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0581 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_088574WRAYPOI7A-162695ELTRUENO_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0807 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_088606JRVKPOI7A-162005KNKWA1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.057 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_088607WLDRPOI7A-162053KNKWA2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0088 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_088640CHLPAPOI4A-162253CHALUPA_138C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0614 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_088656ASTRSPOI4A-163023NEBULA_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0505 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_088670BLACKPOI7A-162915BLACKJAK_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0646 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_088689FOXPOI7A-163477FOXTROT_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0124 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_131753PC_SOUTH_1_5-131754PC_SOUTH_2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0439 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_131753PC_SOUTH_1_5-131755PC2_SWYD_1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0665 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_132632SANTRITA_5-182355OVEJA_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0231 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_133641TAHOKAW_5-134543SAGEDRAWC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.021 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_140442SSPURTWO_5-140803SPURTRES_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0022 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_140753HRFDWIND_5-141053JRDWIND_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0235 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_143575SAMSON_3_5-143625SAMSON_1_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0356 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_143705DELILA_1_5-143757DELILA_2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0364 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_144365GOODNITE_5-144417GOODNIT2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0157 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_160298BAFFIN_5-160299BAFFIN_2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0568 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_160750LV1_AB_8-160751LV1_A_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0619 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_160750LV1_AB_8-160752LV1_B_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0622 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_170250PONY_4_8-180461HHOLLOW3_1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0096 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_170663RVRVLYS_8-170665RVRVLYS3_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1831 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_170664RVRVLY2_8-170665RVRVLYS3_8C2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1832 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_180161SWEETWN4_1_5-180163SWEETWN5_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0122 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_180454BUFF_GAP_1_8-180455BUFF_GAP_2_8CS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0075 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_180752CAPRIDGE_1_8-180757CAPRIDGE_3_8CS1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0081 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_180754DIVIDE_1_8-180757CAPRIDGE_3_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0761 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_180755CAPRIDGE_2_8-180757CAPRIDGE_3_8CS2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0022 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_180955TKWSW_1_5-180956KIO_SWYD_2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0009 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_180958PYRON_1_5-180959KIO_SWYD_3_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0165 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_180961IND_1_5-180962KIO_SWYD_4_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0003 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_181853DERMOTT_H-182101COYOTE_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0036 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_182051RTS_5-182653RTS2_5_1C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0007 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_182727AVIATOR_5-182728DEWOLF_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.002 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_182777MAVCRK_W_5-182778E_MAVERICK_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0104 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_888839BAS_RANCH_POI-011098SANDLAKE_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0175 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0773 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.051 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_888856HOLLY_POI-059900LONG_DRAWC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0872 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_888857OYSTER_POI-068091NAVARROC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0698 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_888860RUBICONALPHA_POI-060791PERIGEE7AC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0187 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1394 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L_888880DES_WILL_POI-001916LIGGETTA2_5C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0197 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L1000027 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0562 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L1000032 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0581 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L1000097 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0078 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10005-2B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0144 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10010060-1A-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0052 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10010116 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.086 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10010434_MODIFIED_BY_MZ | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0753 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10010717 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0808 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10010870_MODIFIED_BY_MZ | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0213 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10011226 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0321 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10011585 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2475 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10011690 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0951 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10011910-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0893 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10012085 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0171 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10012087 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0652 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10012089 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0088 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10012091 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.057 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10012100 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0293 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10012105 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0412 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10012900 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0399 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L10012915 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0738 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L11000047 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0807 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L11000087 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0124 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L11000090 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1191 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L11000095 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0734 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L11000105 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0548 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L11000171 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0614 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L201000169 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2422 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L2020900 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1685 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L2025540 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0747 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L2025541 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0746 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | L20255426 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2422 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LAKE CREEK - LAKE HALL/TRADINGHOUSE_5 (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0962 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LAKE CREEK - LAKE HALL_5 (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.021 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LAKE CREEK - RATTLE SNAKE 345 KV WITH SANDY UNIT (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4196 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LAKE CREEK-RATTLESNAKE/RIESEL_5_8 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0007 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LAKE CREEK-RATTLESNAKE/ST JOHNS_5 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1343 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LATIMER_REATA_P7F1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1909 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_BF_BUS7184 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.5606 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T107_T635_A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1719 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T120 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0103 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T122_T123 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0176 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T123_T225 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0048 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T134_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0924 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T140 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0149 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T140_T614 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0092 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T142_TAE926_927 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9904 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T142_TAE929 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5011 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T142_TAE931 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2438 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T143_TAE988_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6396 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T150_T608 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.9019 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T150_T608_A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.931 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T151_T670 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.066 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T153_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0794 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T158 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0853 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T158_T203_A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1517 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T158_T203_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1664 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T158_T203_C | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0856 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T162_T197 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0266 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T163_T972 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0673 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T177_T211_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0647 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T179_T180 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2197 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T180_T525 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6747 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T182_T185 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5321 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T184_T578 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0621 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T185_T246 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 107.1427 | 103.327 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T187_T188 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4401 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T187_T376 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5989 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T189_T376 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4249 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T195_T654 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2011 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T196_T497_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1949 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T197_T242 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0306 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T201 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2088 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T201_T202_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1546 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T204_T205 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0049 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T205_T233 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1131 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T210_T211 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1687 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T21451 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0761 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T21457 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0833 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T218_T654 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6322 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T219 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.08 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T219_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1214 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T220_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.017 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T227_T388 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8466 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T228_T503 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0181 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T228_T656 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2174 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T234_T235_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.21 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T234_T235_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1697 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T237_T389_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4163 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T238_T656 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2373 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T248_T250 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5231 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T248_T419 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1719 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T255_TAE3121_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 107.9078 | 105.3503 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T267 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0054 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T268 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0136 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T302_T705 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0051 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T339_T340 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1227 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T342_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1974 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T345 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.024 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T359_T21422_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8908 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T376_T654 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3964 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T389_T493_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4147 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T389_T518 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4113 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T389_T610 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4096 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T407_T606 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0011 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T451_T682 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0444 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T458_T497 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.9801 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T490_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2399 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T497_T525 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9136 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T503_T656 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2018 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T510_1 | 13.8 | 138 | Branch MVA | 107 | - | - | 100.679 | - | - | 104.2054 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T510_T511_3 | 13.8 | 138 | Branch MVA | 107 | - | - | 100.9525 | - | - | 104.7028 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T510_T512_1 | 13.8 | 138 | Branch MVA | 107 | - | - | 100.7762 | - | - | 104.4869 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T510_T738_1 | 13.8 | 138 | Branch MVA | 107 | - | - | 101.9523 | - | - | 103.7289 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T510_T775 | 13.8 | 138 | Branch MVA | 107 | - | - | 105.2739 | - | 101.4762 | 104.999 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T511_T625_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.6812 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T538_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0293 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T558 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0747 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T558_T559_A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.269 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T558_T559_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2816 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T558_T559_C | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2859 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T559 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0746 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T579 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0447 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T584_T656_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2437 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T595 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2467 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T608 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.0267 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T626 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0161 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T635 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0769 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T656_T657 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2687 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T672 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0396 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRA TSC_T715_T713_A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3157 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRATSC_1_HUTTO__LIMMER | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9881 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRATSC_2_LIMMER_GILLCR | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 103.0871 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRATSC_3_GILLCR_WHISVA | 13.8 | 138 | Branch MVA | 107 | - | - | 101.6479 | - | - | 104.7201 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRATSC_4_WHISVA_HORNSB | 13.8 | 138 | Branch MVA | 107 | - | - | 103.7567 | - | 100.4521 | 102.3482 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRATSC_5_HORNSB_EUCLID | 13.8 | 138 | Branch MVA | 107 | - | - | 105.3228 | - | 105.1557 | 105.7219 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRATSC_6_EUCLID_JOHNDU | 13.8 | 138 | Branch MVA | 107 | - | - | 107.9078 | - | 107.9078 | 107.1143 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRATSC_7_JOHNDU_ZORN__ | 13.8 | 138 | Branch MVA | 107 | - | - | 103.6511 | - | 100.7701 | 102.3652 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LCRATSC_8_ZORN___CLEASP | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.0398 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LEON_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0228 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0396 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0197 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0713 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LIMMER SS - GILLELAND/ZORN_5 (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.2187 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0596 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LONGCREEK SW - COOK FIELD ROAD SW & LONGCREEK SW - GRAHAM SW 345 KV (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0618 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | LONGCREEK SW - SWEETWATER EAST & MULBERRY CREEK 345 KV SUM 2025 - FUTURE (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0414 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M10000254106503-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0009 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M10000271115801 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 100.0321 | 100.4845 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M100052100072 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0866 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M100472111263 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0123 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M100473111262 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0117 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M100473111265-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0159 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M100871108255-1A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0269 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M100876108254-1A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0289 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M105311105321 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2209 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M108702151602_MODIFIED_BY_MZ | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0282 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M1101410110507-1_MODIFIED_BY_MZ | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0382 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M115851115803 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3857 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M128103100534 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0527 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M128104100523 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0472 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M128152129153 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.074 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M151601108703_MODIFIED_BY_MZ | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0305 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M2099620668 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0113 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | M2100120997-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1736 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MALDIVES_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0911 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MALLARD - TAYLOR/BRUSHY CREEK 138 KV (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.933 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1606 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1888 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MARTINEZ_51_P1_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0141 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MARTINEZ_51_P7 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3367 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MARTINEZ_52_P7 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0584 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MARTINEZ_82_P7 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0131 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB100002711580 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 100.0321 | 100.4845 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB1000710005-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0526 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB1005312810 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0484 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB1008710825-1A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0269 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB1087010087_MODIFIED_BY_MZ | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0164 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB1101411110-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1524 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB1158011585 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3857 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB1281010052 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0429 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB1291012930 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0155 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB1291512815a | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0729 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB1516010870_MODIFIED_BY_MZ | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.023 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB2084520840 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0349 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB2089220893 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0581 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB2094820900 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.163 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB210140210145-AAAAA | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3728 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB210140210145-AAAAB | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4052 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB210140210145-AAABA | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2763 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB210140210145-AABA | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3367 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB210140210145-AABB | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2405 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB210140210145-ABAAA | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3122 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB210140210145-ABAAB | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2801 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB210140210145-ABABB | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3083 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB210140210145-ABBA | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2441 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB210140210145-BAAA-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0517 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB210140210145-BAAA-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0546 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB210140210145-BABA | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0524 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MB2726627277 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2578 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MINERVA - CANNON_8 (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3237 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4523 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4693 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNIT 4 345 KV (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1842 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3035 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0338 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | MOSS - HOLT/YUCCA 138 KV/MIDLAND COUNTY NW SW 345 KV (DOUBLE B TO B) SUM 2025- FUTURE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0639 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | N4P3A1C1_B_MODIFIED_BY_MZ | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4057 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | N4P3A2C1_B_MODIFIED_BY_MZ | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.036 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | N5GSU2_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 104.9356 | 100.7932 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.639 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | NEW_CTG_P1.2_5400_5725_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0013 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | NEW_CTG_P7.1_5400_5725_1_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.081 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | NEW_CTG_P7.1_5725_8689_1_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0347 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0339 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | NEW-COMANCHE_8-BROWNWOOD_8/STPHNVIL_8(DOUBLE B TO B) C-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0123 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | NEW-HILLSBORO-CLEBURNE_SW_8 (SINGLE B TO B )-1-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0339 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | NEW-LAUNCH PAD - SPRING VALLEY - PEPPERVINE_8 (SINGLE B TO B)-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0111 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | NEW-PEPPERVINE - LAUNCH PAD_8 (SINGLE B TO B)-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0111 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ODESSA EHV - NORTH MCCAMEY 345 KV (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2489 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | OYSTER_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1842 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_BTE_1_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0083 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_BTE_2_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0083 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_BTE_3_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0083 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_BVE_1_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0116 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_BVE_2_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0116 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_CBT_1_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.062 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_CBT_2_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0629 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_CBY_1_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.008 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_CBY_2_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.008 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_CHE_1_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0025 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_CHE_2_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0089 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_CHE_3_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0104 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_CVC_1_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0056 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_CVC_2_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.005 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_CVC_3_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.005 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_CVC_4_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0044 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_DPEC_1_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0225 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_DPEC_2_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0238 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_DPEC_3_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0225 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_DPEC_4_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0238 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_DPEC_5_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0204 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_FTR_1_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0868 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_FTR_2_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0868 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_FTR_3_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0869 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_GEN_BLY-CBT_C0_111143 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0186 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_GEN_BLY-CBT_C1_111141 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0005 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_GEN_BLY-CBT_C2_111142 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0012 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_GEN_RNS-FTR_C0_120094 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0506 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_PSG_1_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-1_PSG_2_COMBINED-CYCLE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0065 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-2_(21.2_SODG_44541) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2348 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-2_(40015-49200-GL) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0643 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-2_(40450-110666-02) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0109 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-2_(40600-120095-1) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1616 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-2_(40890-113219-01) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0166 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-2_(41430-110825-03) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0056 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-2_(44015-49215-GL) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0028 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-2_(44090-111865-1) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0017 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-2_(44200-112261-1) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0206 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-2_(46020-49208-GL) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2458 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-2_(46020-49209-GL) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2495 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P1-2_(8130-43190-1) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0399 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P3T4A1C2_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0197 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1/C5-CTT-13-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0463 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1/C5-CTT-38 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0453 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T0202C | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0076 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T0202H | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0209 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T0226 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0082 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T0960A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.015 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T0960B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0058 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T1827BY | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0322 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T1827D | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0812 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T1827GX_ERC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.2115 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T1839X1_ERC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3526 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T1839X2_ERC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 101.9583 | 100.4405 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T1850A1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0427 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T2682EX1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0047 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T2682EX2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0063 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T2682GY1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0064 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T2682GY2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0064 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T2764Y_ERCa | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3927 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T3944Z_ERC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 104.5657 | 100.2079 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T7199 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0063 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T7475A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1707 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T7475B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0529 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T7498C_ERC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0975 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>>T9797B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1223 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5227 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1_E1>T0202GX | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0194 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-1>>T2727L | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0524 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | P7-WETT-4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0193 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | PARIS NW-PARIS-PARIS SW138 KV (SINGLE B TO B) A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0223 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | PARIS SW-MOSES 345 KV-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0252 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | PARIS SW-PACIFIC SW/VALLEY S SW 345 KV (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0386 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | PEC_T180_T323 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1398 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | PEC_T197_T325 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3118 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | PEC_T219_T311_A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8496 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | PEC_T315_T323 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0796 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | PEC_T319 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1922 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | PEC_T323_T458 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.9931 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | PEC_T323_T497 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.3916 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | PEC_T324_T699_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2458 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | PEC_T325_T965 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4505 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | PHNT_WSHACK_P7-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0181 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | PHNT_WSHACK_P7-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0027 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | PINEFOREST_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2191 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | QUANT_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1624 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | R4T4A1C1_B_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0308 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | R4T4A1C1_B_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0157 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | R4T4A2C2_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0311 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | R4U2A5C1_1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4814 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | R5S2S1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5018 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0767 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | RAT_SNAKE-SNDY_CREEK_5 (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4194 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | RENNER - NORTHWEST CARROLLTON 345 KV & RENNER - ALLEN SW 345 KV (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0024 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | RICH-BBROWN (DOUBLE B TO B)A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0771 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ROOKIE-TAYLOR_8 (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4349 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | ROOKIE-TORTOISE_8 (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2817 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | RUBICONALPHA_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0612 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | RYBRN_P1-2_VINSON-LORING_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0099 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_003371SKYBOX_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.1053 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_003415TEMP_SS__81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0308 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_003422KILL_SS__51 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3514 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_003423KILL_SS__81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2716 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_003484PEPPERCRK_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.123 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_003485TINROOF_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4564 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_003630COPPERCV1_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0295 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_003630COPPERCV1_82 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0477 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_003668RNDROCK1_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 102.244 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_003669RNDRCKWH1_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0584 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_003672RNDRCK_S1_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7555 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_003693MALLARD_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.094 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_003750VOSSLAKE_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9076 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_005470FAIRRA1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0452 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007041L_JOHNDU5_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5097 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007064L_LAMPAS8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1342 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007168L_BOERNE8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0588 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007176L_COMAL_8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0118 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007192L_SANMAR8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.301 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007228L_SEGUIN8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0329 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007294L_BRENNO8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.014 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007346L_GABRIE8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4261 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007366L_CHIEBR8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5149 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007476L_PALEFA8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3114 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007523L_GLASSC8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4314 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007530L_KENTST8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6423 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007534L_AVERRA8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6531 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007555L_BASTWE8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4208 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007567L_LYLEWO8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0083 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007568L_LINCOL8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0774 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_007606L_MCQUEE8_1Y1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0176 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009001BA138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7758 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009002BC138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8833 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009003CL138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.9434 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009005CF138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7251 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009006FV138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8284 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009008HV138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.65 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009009JV138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6601 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009010MP138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7576 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009011MC138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7297 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009012OH138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.779 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009014PE138MB1_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0096 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009015PK138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.0871 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009016SW138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.819 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009017BAL138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7636 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009018WI138_CAP1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7145 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009160BEECREEK_MB11 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8833 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009165BRSTRM_MB11 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.3675 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009195EAST_VILLAGE1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.3103 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009224ASHTONW_MB21 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6343 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_009262BLUFFSPG1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.7316 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_013430SAND_TXU_81 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 101.9986 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_070352P_LAGOVI8_1_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5759 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_070498P_BUDA__8_1_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5044 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_070507P_FRIEND8_1_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.499 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_070522P_ANDICE8_1_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4388 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_070524P_SEWAJU8_1_2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5375 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_070525P_LEANDE8_1_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5784 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_070527P_BLOCKH8_1_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.6015 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_070533P_BALCON8_1_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2195 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_070546P_HIGH328_1_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3273 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S_170251OMEGA_1_51 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2465 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | S2SM1_B_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1162 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0385 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2381 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1837 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3863 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | SAM_NAV_P7F1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0952 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | SAN_PAT_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2908 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | SAND LAKE - SOLSTICE 345 KV DCKT LINE (DOUBLE B TO B) WIN 2027 - FUTURE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0046 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | SCUR_CLY_P7 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1312 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 1 & SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 2 345 KV (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0742 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | SKULLCREEK_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0066 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | SOLACE_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1884 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STECL_10128 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0227 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STECL_10131 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.021 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STECL_10247 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0501 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STECL_10248 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0501 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STECL_10262 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3001 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STECL_10263 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0095 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STECL_10264 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0095 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STECL_10265 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0095 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STECL_10266 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0095 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STECL_10288 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0481 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STECL_10289 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0371 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STECL_10588 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0566 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STECL_10597 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0012 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STECL_10601 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0059 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STECL_4703 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0116 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STECL_4720 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0082 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STONE CREEK SW-BONHAM SW 69 KV & VALLEY -COMMERCE 138 KV LINE A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0023 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | STP - HOUDINI & STP - SHAULA | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3839 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | T_000131SEATON9-000130SEATON8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0146 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | T_000133BELLCNTY9-000132BELLCNTY8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0215 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | T_000981SPNCRINT69-000982DN_STEAM_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.049 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | T_006364YELWJCKT4A-006365YELWJCKT4BC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1684 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | T_007121L_SANDCR9_1Y-007127L_SANDCR8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0501 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | T_007248L_FLATON8_1Y-007247L_FLATON9_1YC2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0364 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | T_007597L_DEERCR9_1Y-007595L_DEERCR8_1YC1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0689 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | T_059908NOVA_345-059998NOVA8CT1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3388 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | T_120545BOARDCRK_5-120544BOARDCRK_SUBCT3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0105 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | T_151856PRIDDY_5-151855PRIDDY_T1CT3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0328 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | T_180760DIVIDE_SC1-180754DIVIDE_1_8C1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0761 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | T200004 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0037 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | 103.5551 | 103.499 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | TEMPLE - BELFALLS_5 (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0349 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | TEMPLE ELM CREEK SWITCH - PASCA RISE (DOUBLE B TO B ) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1762 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | TEMPLE PECAN CRK-TEMPLE_ELM_CRK (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.095 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0192 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | THOUSE-LCRK*PCNCRK_5 (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0099 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | THRESLR_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.021 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | TIMBERVIEW-VENUS 345 KV DOUBLE-CIRCUIT LINE (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.014 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2449 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | TORTOISE - BEULAH/AUSTROP_5 (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1183 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1077 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3692 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | TRIFECTA_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3574 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2812 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4206 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | TWIN_OAK N__5 - GIBN_CREK_5 & JKCREEK1 - GIBN_CREK_5 (CAT_C)(DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.003 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | TWIN_OAK__5-LIMEST__345A & TWIN_OAK__5-LIMEST__345A (CAT_C)(DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0081 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | TWIN_OAK_BKR_8995_345_OAK_GROVE_SINGLE_B_T0_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2181 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | TWIN_OAK_BKR_9000_345_OAK_GROVE_SINGLE_B_T0_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2179 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | U2GSU56_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.084 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | U2GSU78_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0829 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | U3CT1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1143 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | U3GSU1_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2938 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | U3GSU2_B | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1454 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | V3X2A1C2_B_1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.069 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | VALLEY S-ANNA SW 345 KV & VALLEY S-FARMERSVILLE 345 KV | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.003 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | VALLEY S-VALLEY SW 345 KV & VALLEY S-PARIS SW 345 KV | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0049 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | VALLEY SW-COMMERCE SW 138 KV BONHAM SW 138-69KV AUTO #1 A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0089 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0768 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0393 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1407 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0951 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3235 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2878 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.8913 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | VIKING_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1034 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | Voss Lake - Temple 138 kV (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0138 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | WAP - HOUDINI & STP - SHAULA | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4318 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0676 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | WATERMILL-LOOP NINE 345 KV DCKT (DOUBLE B TO B) A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0094 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0327 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0342 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0644 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | WHITERIVER-COTTONWOOD (DOUBLE B TO B)-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0036 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | WHITERIVER-COTTONWOOD (DOUBLE B TO B)-3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1352 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.5 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | WINDMILL - AJSWOPE (SINGLE B TO B) SUM 2028 - FUTURE | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2444 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3021 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C2_345 KV (SINGLE B TO B) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.114 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | WSHACK_LATIMER_P7 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2154 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-CALFRESTN_5-4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0278 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-CALFRESTN_5-5 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0277 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-CALFRESTN_5-6 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0379 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-CALPFREST_5-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0169 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-CALPFREST_5-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0169 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-CALPFREST_5-3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0152 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-DECORDOVA2_8-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0089 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-DECORDOVA2_8-3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0088 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-DECORDOVA2_8-4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0082 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-DECORDOVA2_8-5 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0089 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-ENNSTRAC_8-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.095 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-ENNSTRAC_8-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0397 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-FSCOGEN_8-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0259 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-FSCOGEN_8-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0259 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-GRHAMSES1_8-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.136 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-HANDLEYC_8-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2194 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-HANDLEYC_8-3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2582 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-HANDLEYD_8-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2641 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-LKHB_1T8-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.2265 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-LKHB_2T8-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3087 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-MARTINLK_5-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3463 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-MARTINLK_5-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3473 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-MARTINLK_5-3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3505 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-MDLTHELP_5-5 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1176 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-MDLTHELP_5-6 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1187 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-MDLTHELP_N5-3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1239 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-MDLTHELP_N5-4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1238 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-MDLTHELP_S5-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1107 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-MDLTHELP_S5-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1199 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-MTCK_6T8-6 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0506 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-MTCK_7T8-7 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0512 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-MTCK_8T8-8 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3524 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-MTENTRPR_5G-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0347 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-MTENTRPR_5G-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0251 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-MTENTRPR_5G-3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0333 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-MTENTRPR_5G-4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.149 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-PBGENBUS_B-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0197 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-PBGENBUS_B-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0206 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-PBGENBUS_B-3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0188 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-PBGENBUS_B-4 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0197 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-PBGENBUS_B-5 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0197 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-SANDYCRK_5-01 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4194 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-STRYKER_8-2 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1943 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-STRYKERND_8-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0387 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-TENASKA_8-1_REVA (UNIT1) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.005 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-TENASKA_8-1_REVA (UNIT2) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.005 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-TENASKA_8-1_REVA (UNIT3) | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0066 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-WHCCS2_4-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.1842 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-WHCCS2_5-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.4819 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-WLFHMDPT_5-1 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.3021 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | XFMR-WLFHOSTR-3 | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.114 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD ( 9216) CKT 1 | YELLOW_WOLF_CON | 13.8 | 138 | Branch MVA | 107 | - | - | - | - | - | 100.0882 | -
RAEN | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SANDHSYD_SH3 (170213) -> SANDHSYD (9216) CKT 1 | Pre-contingency | 13.8 | 138 | MVA | 107 | - | - | - | 100.564 | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLAKE_5 (11098) -> SANDLSTR (500209) CKT 1 | Pre-contingency | 345 | 1 | MVA | 700 | 107.4075 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLAKE_5 (11098) -> SANDLSTR (500210) CKT 2 | Pre-contingency | 345 | 1 | MVA | 700 | 107.9054 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLAKE_8 (11097) -> BARSTOWNW_8 ( 1086) CKT 1 | L_011086MCHALAM_8-011612ONC900009_TAPC1 | 138 | 138 | Branch Amp | 2568.79 | - | - | - | - | 100.0276 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLAKE_8 (11097) -> BARSTOWNW_8 ( 1086) CKT 1 | L_011097SANDLAKE_8-011612ONC900009_TAPC1 | 138 | 138 | Branch Amp | 2568.79 | - | - | - | - | 108.9654 | 101.272 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLAKE_8 (11097) -> ONC900009_TAP (11612) CKT 1 | L_001086BARSTOWNW_8-011097SANDLAKE_8C1 | 138 | 138 | Branch Amp | 2401.4421 | - | - | - | 101.4628 | 116.2113 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLAKE_8 (11097) -> ONC900009_TAP (11612) CKT 1 | L_001086BARSTOWNW_8-011105PECONE_P8C1 | 138 | 138 | Branch Amp | 2401.4421 | - | - | - | - | 113.5849 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLAKE_8 (11097) -> ONC900009_TAP (11612) CKT 1 | L_011105PECONE_P8-011377AQUIFER_8C1 | 138 | 138 | Branch Amp | 2401.4421 | - | - | - | - | 104.603 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLAKE_8 (11097) -> ONC900009_TAP (11612) CKT 1 | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | 138 | Branch Amp | 2401.4421 | - | - | - | - | 109.777 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLAKE_8 (11097) -> SANDLSTR (500209) CKT 1 | Pre-contingency | 138 | 1 | MVA | 700 | 102.7384 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLAKE_8 (11097) -> SANDLSTR (500210) CKT 2 | Pre-contingency | 138 | 1 | MVA | 700 | 103.2147 | - | - | - | - | - | -
TTNMP,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLAKE_8 (11097) -> TNCEDRVALE1 (38145) CKT 1 | L_011097SANDLAKE_8-038145TNCEDRVALE1C2 | 138 | 138 | Branch Amp | 2568.79 | 163.4425 | - | - | - | - | - | -
TTNMP,TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLAKE_8 (11097) -> TNCEDRVALE1 (38145) CKT 2 | L_011097SANDLAKE_8-038145TNCEDRVALE1C1 | 138 | 138 | Branch Amp | 2539.5042 | 165.7965 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500209) -> SANDLAKE_8 (11097) CKT 1 | 3WT_011098SANDLAKE_5_011097SANDLAKE_8_011109SANDLAKE2_3 C 2 | 138 | 1 | Branch MVA | 750 | 150.9207 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500209) -> SANDLAKE_8 (11097) CKT 1 | L_001009YUCCADR_8-001080WHITOIL_8C1 | 138 | 1 | Branch MVA | 750 | 101.1984 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500209) -> SANDLAKE_8 (11097) CKT 1 | L_001012PIRCOVE_8-001080WHITOIL_8C1 | 138 | 1 | Branch MVA | 750 | 101.1825 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500209) -> SANDLAKE_8 (11097) CKT 1 | L_001012PIRCOVE_8-011104BARKETT_P8C1 | 138 | 1 | Branch MVA | 750 | 100.9301 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500209) -> SANDLAKE_8 (11097) CKT 1 | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 138 | 1 | Branch MVA | 750 | 100.5149 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500209) -> SANDLAKE_8 (11097) CKT 1 | L_038045TNIH20____1-038055TNSALTDRWT1C1 | 138 | 1 | Branch MVA | 750 | 100.425 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500209) -> SANDLAKE_8 (11097) CKT 1 | L_038055TNSALTDRWT1-038058TNSADDLEBK1C1 | 138 | 1 | Branch MVA | 750 | 101.439 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500209) -> SANDLAKE_8 (11097) CKT 1 | L_038058TNSADDLEBK1-038065TNBRDRFLD_1C1 | 138 | 1 | Branch MVA | 750 | 101.6796 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500209) -> SANDLAKE_8 (11097) CKT 1 | L_038065TNBRDRFLD_1-038069TNFLATTOP_1C1 | 138 | 1 | Branch MVA | 750 | 102.0858 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500209) -> SANDLAKE_8 (11097) CKT 1 | L_038069TNFLATTOP_1-038294TNFOXTAIL_1C1 | 138 | 1 | Branch MVA | 750 | 102.1633 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500209) -> SANDLAKE_8 (11097) CKT 1 | P1.2_M138I-1_19SPG-2026 | 138 | 1 | Branch MVA | 750 | 100.4972 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500209) -> SANDLAKE_8 (11097) CKT 1 | RIVERTON - THREE MILE DRAW/HORSESHOE SPRINGS DCKT 138 KV SUM 2022 - FUTURE (DOUBLE B TO B) C | 138 | 1 | Branch MVA | 750 | 100.7217 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500209) -> SANDLAKE_8 (11097) CKT 1 | WOLF - METEOR/ODESSA EHV 345 KV 2025 WIN - 2026 SUM (DOUBLE B TO B) | 138 | 1 | Branch MVA | 750 | 100.2142 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500210) -> SANDLAKE_8 (11097) CKT 2 | 3WT_011098SANDLAKE_5_011097SANDLAKE_8_011099SANDLAKE1_3 C 1 | 138 | 1 | Branch MVA | 750 | 151.2258 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500210) -> SANDLAKE_8 (11097) CKT 2 | L_001009YUCCADR_8-001080WHITOIL_8C1 | 138 | 1 | Branch MVA | 750 | 101.6675 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500210) -> SANDLAKE_8 (11097) CKT 2 | L_001012PIRCOVE_8-001080WHITOIL_8C1 | 138 | 1 | Branch MVA | 750 | 101.6515 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500210) -> SANDLAKE_8 (11097) CKT 2 | L_001012PIRCOVE_8-011104BARKETT_P8C1 | 138 | 1 | Branch MVA | 750 | 101.3979 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500210) -> SANDLAKE_8 (11097) CKT 2 | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 138 | 1 | Branch MVA | 750 | 100.9808 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500210) -> SANDLAKE_8 (11097) CKT 2 | L_037981TNWICKETT_1-037990TNSTAGHORN1C1 | 138 | 1 | Branch MVA | 750 | 100.3357 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500210) -> SANDLAKE_8 (11097) CKT 2 | L_037990TNSTAGHORN1-038001TNPYOTE___1C1 | 138 | 1 | Branch MVA | 750 | 100.0502 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500210) -> SANDLAKE_8 (11097) CKT 2 | L_038045TNIH20____1-038055TNSALTDRWT1C1 | 138 | 1 | Branch MVA | 750 | 100.8905 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500210) -> SANDLAKE_8 (11097) CKT 2 | L_038055TNSALTDRWT1-038058TNSADDLEBK1C1 | 138 | 1 | Branch MVA | 750 | 101.9092 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500210) -> SANDLAKE_8 (11097) CKT 2 | L_038058TNSADDLEBK1-038065TNBRDRFLD_1C1 | 138 | 1 | Branch MVA | 750 | 102.1509 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500210) -> SANDLAKE_8 (11097) CKT 2 | L_038065TNBRDRFLD_1-038069TNFLATTOP_1C1 | 138 | 1 | Branch MVA | 750 | 102.559 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500210) -> SANDLAKE_8 (11097) CKT 2 | L_038069TNFLATTOP_1-038294TNFOXTAIL_1C1 | 138 | 1 | Branch MVA | 750 | 102.6368 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500210) -> SANDLAKE_8 (11097) CKT 2 | P1.2_M138I-1_19SPG-2026 | 138 | 1 | Branch MVA | 750 | 100.963 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500210) -> SANDLAKE_8 (11097) CKT 2 | RIVERTON - THREE MILE DRAW/HORSESHOE SPRINGS DCKT 138 KV SUM 2022 - FUTURE (DOUBLE B TO B) C | 138 | 1 | Branch MVA | 750 | 101.1886 | - | - | - | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SANDLSTR (500210) -> SANDLAKE_8 (11097) CKT 2 | WOLF - METEOR/ODESSA EHV 345 KV 2025 WIN - 2026 SUM (DOUBLE B TO B) | 138 | 1 | Branch MVA | 750 | 100.6787 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SANW2A ( 6527) -> SAMATHIS2A ( 6477) CKT 1 | L_006036YUCCA4A-006525ESMERALD4AC1 | 69 | 69 | Branch Amp | 317.961 | 130.7642 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SANW2A ( 6527) -> SAMATHIS2A ( 6477) CKT 1 | L_006036YUCCA4A-060360CASSAVA4AC1 | 69 | 69 | Branch Amp | 317.961 | 114.3126 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SANW2A ( 6527) -> SAMATHIS2A ( 6477) CKT 1 | L_006525ESMERALD4A-006562FDRAN4AC1 | 69 | 69 | Branch Amp | 317.961 | 102.0172 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SANW2A ( 6527) -> SAMATHIS2A ( 6477) CKT 1 | L_006559JERRY4A-060374PUMPJACK4AC1 | 69 | 69 | Branch Amp | 317.961 | 100.6603 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SANW2A ( 6527) -> SAMATHIS2A ( 6477) CKT 1 | L_006648HARGROVE4A-060374PUMPJACK4AC1 | 69 | 69 | Branch Amp | 317.961 | 102.8298 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SANW2A ( 6527) -> SAMATHIS2A ( 6477) CKT 1 | L_006648HARGROVE4A-076011L_TWINBU8_1YC1 | 69 | 69 | Branch Amp | 317.961 | 104.2353 | - | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | SANW2A ( 6527) -> SAMATHIS2A ( 6477) CKT 1 | LCRA TSC_T429_T9426 | 69 | 69 | Branch Amp | 317.961 | 102.2852 | - | - | - | - | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | 3WT_002431DESSW1_5_002424DESSW1_8_012431DESSW1_3 C 1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 105.2282 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 109.2108 | - | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 101.9318 | - | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 103.5121 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | CEDAR HILL - DESOTO/LOOP NINE 345 KV DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 108.7145 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 106.5917 | 127.0067 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 107.6191 | 127.5915 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | CLEBURNE-KEMP RANCH 138 KV WITH RAILPORT (SINGLE B TO B) A | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.2875 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | E_ETCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 117.4365 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 102.275 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 112.7357 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | ENNIS WEST - STERRETT 138 KV (SINGLE B TO B) A REAGOR SPRINGS | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 109.7977 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | GLASGOW_CON | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 102.4168 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | KEMP RANCH - CLEBURNE 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.2875 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | KEMP RANCH-ALVARADO-CLEBURNE 138 KV (SINGLE B TO B) A ALVARDO 138/69 TRANSFORMER | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.2875 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 115.2055 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 115.4839 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_000217GLNHEIGHTS-002237STERTRD_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 104.5953 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_000217GLNHEIGHTS-002424DESSW1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 112.7872 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.2789 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 101.257 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 101.7772 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 105.0218 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 104.0992 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 106.4145 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 103.5121 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 102.275 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 108.1768 | 128.9894 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_002286PADERA_8-002310MDLTHTXI2_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 104.4246 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_002286PADERA_8-002311MDLTH_N_T8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 101.81 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_002289SOAPCRK_8-002303KEMPRNCH_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.8465 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_002289SOAPCRK_8-002310MDLTHTXI2_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 104.6158 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_002313MDLTH_N_8-002314MDLTHBOX_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.1856 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_002315WAX_PMP2_8-002319WAX_PMP1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 113.1297 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_002315WAX_PMP2_8-002320WAX_N_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 113.5269 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_002316MG_IND_T8-002319WAX_PMP1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 111.8238 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_002320WAX_N_8-002321WAX_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 100.9085 | 122.3461 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 106.9236 | 127.6878 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 113.3187 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 112.7599 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 102.2525 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 101.3902 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.2357 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 107.5088 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 109.0275 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 108.7753 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 103.6439 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 115.3264 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | SOAP CREEK - CEDAR HILL 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 101.5427 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | STERRETT 5400 - DESOTO (SINGLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 104.3171 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 104.3917 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 106.1886 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 107.0601 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 106.844 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 115.5726 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | Venus Switch- Cleburne 138 kV Line (SINGLE B TO B) new load | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.2875 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.7273 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 105.6172 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 895.3112 | - | - | - | 101.3428 | - | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | WAXAHACHI-WAXAHACHI OFC 69KV/ENNIS-STERRETT 138KV (DOUBLE B TO B) A REAGOR | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 116.9466 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 105.001 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 106.3695 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> STERRETTL_8 (12317) CKT 1 | XFMR-ENNSTRAC_8-1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 106.5203 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SARDIS8 ( 203) -> WAX_NW_8 ( 2309) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 103.1088 | 102.451 | 100.685 | -
TSTEC | COAST | COAST | COAST, COAST | SARGENTSUB9 ( 5564) -> BAYCITYSUB9 ( 5560) CKT 1 | L_005557CAYCESW9-005558VANVLECKSUB9C1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 109.4701 | - | -
TSTEC | COAST | COAST | COAST, COAST | SARGENTSUB9 ( 5564) -> BAYCITYSUB9 ( 5560) CKT 1 | L_005915SO_TEX__345A-008123BLESSING7AC1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 108.3713 | - | -
TSTEC | COAST | COAST | COAST, COAST | SARGENTSUB9 ( 5564) -> BAYCITYSUB9 ( 5560) CKT 1 | L_008127LAN_CTY4A-008130LAN_CTY4BCS1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.8437 | - | -
TSTEC | COAST | COAST | COAST, COAST | SARGENTSUB9 ( 5564) -> BAYCITYSUB9 ( 5560) CKT 1 | L10012900 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.8437 | - | -
TSTEC | COAST | COAST | COAST, COAST | SARGENTSUB9 ( 5564) -> BAYCITYSUB9 ( 5560) CKT 1 | P1-2_(8130-43190-1) | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.8437 | - | -
TSTEC | COAST | COAST | COAST, COAST | SARGENTSUB9 ( 5564) -> BAYCITYSUB9 ( 5560) CKT 1 | P7-1_E1>>T1827D | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 100.0688 | - | -
TSTEC | COAST | COAST | COAST, COAST | SARGENTSUB9 ( 5564) -> BAYCITYSUB9 ( 5560) CKT 1 | STECL_10301 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 108.9572 | - | -
TSTEC | COAST | COAST | COAST, COAST | SARGENTSUB9 ( 5564) -> BAYCITYSUB9 ( 5560) CKT 1 | T_008121BLESSING4A-008123BLESSING7AC1 | 69 | 69 | Branch Amp | 376.5327 | - | - | - | - | 108.3485 | - | -
TSTEC | COAST | COAST | COAST, COAST | SARGENTSUB9 (5564) -> FRNKLNCMPSB9 (5566) CKT 1 | Pre-contingency | 69 | 69 | Amps | 334.6958 | - | - | - | - | 102.0192 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.7891 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | AUSTROP - BEULAH/TORTOISE_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 104.7316 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | BELL CNTY - SALADOSOUTH_GABRIEL(LCRA)_8 (SINGLE B TO B ) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 114.4963 | 127.2688 | 114.4875 | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | E_FERGCC_CC1_TRAIN | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.2088 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | G_170126CALAVER_JKS2UL2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.5001 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | G_RIO_TRAIN | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.7561 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | GABRIEL - BELL COUNTY - HUTTO/ROUND ROCK (DOUBLE B TO B ) E | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 104.2762 | 116.325 | 103.8517 | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | GABRIEL - BELL COUNTY/GEORGETOWN E_8 (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 108.3588 | 120.9731 | 108.0511 | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | HUTTO - ROUND ROCK/GEORGETOWN SOUTH (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 105.0505 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 138.2901 | - | 126.0328 | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | J5LCA1C1_B | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.771 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 778.1677 | - | - | 104.6536 | 152.068 | - | 143.6253 | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_000121SONTERRA-003688JARRELL_E_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 111.9126 | 124.7743 | 112.0075 | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_000121SONTERRA-013640SALADO_S1_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 113.5895 | 126.4372 | 113.6466 | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_000132BELLCNTY8-003640SALADO1_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 119.0649 | 131.9025 | 119.0342 | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003413KNOBCRKSS_5-003414TEMP_SS__5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 106.1153 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 111.444 | 148.9593 | 105.2775 | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003415TEMP_SS__8-003485TINROOF_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.3047 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003640SALADO1_8-013640SALADO_S1_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 115.7797 | 128.6218 | 115.8005 | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003664RNDRCKWH_T_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 105.3536 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003664RNDRCKWH_T_8-003669RNDRCKWH1_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 105.3519 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 108.7182 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003668RNDROCK1_8-007366L_CHIEBR8_1YC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.1563 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003669RNDRCKWH1_8-007532L_GEORSO8_1YC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.094 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003688JARRELL_E_8-007346L_GABRIE8_1YC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 107.6279 | 120.449 | 107.7318 | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 105.7314 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003696HUTTOSS__5-003699SALADOSS_5C2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 105.7314 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_003717TORTOISE_5-013429SAND_TXU_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 103.1246 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 107.1042 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.5151 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.3531 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | LCRA TSC_T255_TAE3121_1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.2873 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | LCRA TSC_T378_T642 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 102.8614 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | LCRATSC_6_EUCLID_JOHNDU | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.7032 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | N5GSU2_B | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.5001 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 100.1584 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | TORTOISE - BEULAH/AUSTROP_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 104.5945 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | TORTOISE - SANDOW_8_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 103.2535 | - | -
TBREC,TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER ( 122) -> L_GABRIE8_1Y ( 7346) CKT 1 | Voss Lake - Temple 138 kV (SINGLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | 101.4875 | - | -
TBREC , TLCRA | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SCHWERTNER (122) -> L_GABRIE8_1Y (7346) CKT 1 | Pre-contingency | 138 | 138 | Amps | 594.085 | - | - | - | 109.5227 | 121.8512 | 109.5374 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SCOTWHIT_T_8 ( 3602) -> TEMPLE_S1_8 ( 3611) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1380.62 | - | - | - | - | 108.3392 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SCOTWHIT_T_8 ( 3602) -> TEMPLE_S1_8 ( 3611) CKT 1 | TEMPLE ELM CREEK SWITCH - PASCA RISE (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1380.62 | - | - | - | - | 111.4428 | - | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | 3WT_001302WILLOWVAL_5_001301WILLOWVAL_8_018537WILLOWVAL_3 C 3 | 138 | 138 | Branch Amp | 778.1677 | 106.3901 | - | 111.2366 | 113.2386 | - | 117.7168 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | BLUFF CREEK SW - WILLOW VALLEY SW 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | 101.3591 | - | 109.2142 | 111.7613 | - | 117.3652 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | C5-WETT-2_A | 138 | 138 | Branch Amp | 778.1677 | - | - | 100.9305 | - | - | - | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | ENNIS CREEK - GOLDEN SW 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 100.0023 | - | 106.5334 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | HOLLY_CON | 138 | 138 | Branch Amp | 778.1677 | - | - | 100.3962 | 104.533 | - | 104.9203 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | L_001064SUN_8-001067GOLDENSW_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 101.8737 | - | 108.373 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | L_001064SUN_8-001311SACROC_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | 107.6855 | 109.4407 | - | 107.7501 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | L_001067GOLDENSW_8-001315BRAND_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | - | 105.6305 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | L_001300EXSHARNR_8-001309BLUFCKTA_8C1 | 138 | 138 | Branch Amp | 778.1677 | 101.4073 | - | 109.2588 | 111.8022 | - | 117.3031 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | L_001300EXSHARNR_8-901303ONC900119_TAPC1 | 138 | 138 | Branch Amp | 778.1677 | 105.9136 | 101.0978 | 113.6484 | 115.8733 | - | 121.3742 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | L_001301WILLOWVAL_8-901303ONC900119_TAPC1 | 138 | 138 | Branch Amp | 778.1677 | 108.0207 | 102.3554 | 115.8589 | 118.2886 | - | 123.8967 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | L_001304DEEPCRK_8-001305SNYDER_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | 105.2759 | 107.2011 | - | 105.551 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | L_001304DEEPCRK_8-001311SACROC_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | 105.808 | 107.7007 | - | 106.0455 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | L_001313ENISCKTA_8-001314ENNISCK_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 100.4833 | - | 106.9791 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | L_001313ENISCKTA_8-001315BRAND_8C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 100.041 | - | 106.5409 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | L_001314ENNISCK_8-011306DERMOTT_8C1 | 138 | 138 | Branch Amp | 778.1677 | 100.9897 | - | 110.4139 | 112.3536 | - | 121.3851 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | L_011305DERMOTT_5-011318SCURCNTYS_5C1 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | - | 101.6967 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | L_011305DERMOTT_5-011318SCURCNTYS_5C2 | 138 | 138 | Branch Amp | 778.1677 | - | - | - | - | - | 101.6967 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | L_888856HOLLY_POI-059900LONG_DRAWC1 | 138 | 138 | Branch Amp | 778.1677 | - | - | 102.7475 | 108.2055 | - | 109.2856 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 778.1677 | 100.1427 | - | 104.9222 | 105.6388 | - | 106.2647 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 778.1677 | - | - | - | 103.3062 | - | 103.3802 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 1 & SCURRY COUNTY SOUTH SW - DERMOTT SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | 110.8228 | 103.2064 | 123.7043 | 136.1115 | - | 144.7821 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | - | - | 104.7379 | 115.8894 | - | 119.2609 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | WILLOW VALLEY TRANSFORMER 1 (SINGLE B TO B) | 138 | 138 | Branch Amp | 778.1677 | 106.3902 | - | 111.2366 | 113.2387 | - | 117.7169 | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 ( 1312) -> KNDRSACRC_8 (11130) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 778.1677 | - | 106.5521 | - | - | - | - | -
TONCOR | WEST | WEST | WEST, WEST | SCURYCHV_8 (1312) -> KNDRSACRC_8 (11130) CKT 1 | Pre-contingency | 138 | 138 | Amps | 778.1677 | - | - | - | - | 103.874 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SCYENE1T_8 ( 2743) -> PARKDB2_8 ( 2445) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1199.8844 | - | - | - | - | - | 108.273 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SCYENE1T_8 ( 2743) -> PARKDB2_8 ( 2445) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1199.8844 | - | - | - | 114.182 | - | - | -
TAEPTC | COAST | SOUTHERN | COAST, SOUTHERN | SEADRFTC4A (8144) -> MELNCRK4A (80065) CKT 1 | Pre-contingency | 138 | 138 | Amps | 656.8405 | - | - | - | 119.1095 | 161.7561 | 113.2814 | -
TAEPTC | COAST | COAST | COAST, COAST | SEADRFTC4A (8144) -> TUNGSTEN4A (8189) CKT 1 | Pre-contingency | 138 | 138 | Amps | 652.6567 | - | - | - | 120.0054 | 162.9047 | 114.1419 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEATON8 ( 130) -> SEATON9 ( 131) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 69 | 138 | Branch MVA | 100 | - | - | - | 106.22 | - | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEATON8 ( 130) -> SEATON9 ( 131) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 69 | 138 | Branch MVA | 100 | - | - | - | - | 100.9088 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEATON9 ( 131) -> POAGE ( 126) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 69 | 69 | Branch Amp | 861.8416 | - | - | - | 114.7657 | - | 108.4078 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEATON9 ( 131) -> POAGE ( 126) CKT 1 | L_000132BELLCNTY8-003415TEMP_SS__8C1 | 69 | 69 | Branch Amp | 861.8416 | - | - | - | - | 103.9041 | - | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEATON9 ( 131) -> POAGE ( 126) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 69 | 69 | Branch Amp | 861.8416 | - | - | - | - | 115.1619 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | 3WT_002433SGVLSW1_5_002434SGVLSW1_8_012434SGVLSW1_3 C 2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.4998 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1277 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.3913 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 108.4598 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | E_FRNYPP_CC1_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.0317 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | E_FRNYPP_CC2_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.1034 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.5824 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 109.8548 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | G_151371LILY_S1US1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 106.5166 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | GLASGOW_CON | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.8432 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 110.0523 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 110.2172 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.5997 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.3913 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.5824 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 108.8721 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 108.5168 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.9366 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 110.2081 | 135.7994 | 111.0331 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.0853 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.0435 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.5935 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.9275 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 106.2291 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_006903BOZE-151372LILY_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 107.1138 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.4455 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.3615 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 107.1709 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 107.6867 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.1629 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 107.7881 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 113.8618 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.053 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.2988 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.0918 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | SEAGOVILLE SW - FORNEY/TRICORNER DCKT 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.0621 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 109.8484 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 105.3166 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.8017 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 107.0247 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 110.6323 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 123.7367 | - | 121.3507 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1904 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.8181 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.0493 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SEVENPTS_8 ( 3264) -> KEMP_S_8 ( 2726) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.7809 | - | -
TONCOR,TBREC | NORTH | NORTH | NORTH, NORTH | SEYMOUR_T9 ( 1534) -> SEYMOUR ( 779) CKT 1 | L_000779SEYMOUR-033728MABELLEC1 | 69 | 69 | Branch Amp | 225.9196 | 108.6707 | - | 109.2256 | 110.4194 | 110.8445 | 109.8733 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SGVL1_8 ( 3076) -> KLEBRG1T_8 ( 3077) CKT 1 | L_002429WATMLL_8-003083WILMER1_8C1 | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | 135.101 | 138.0457 | 128.9441 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SGVL1_8 ( 3076) -> KLEBRG1T_8 ( 3077) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | - | - | 115.9366 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SGVL1_8 ( 3076) -> KLEBRG1T_8 ( 3077) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | 128.9861 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SGVLSSTR (500085) -> SGVLSW1_8 ( 2434) CKT 2 | L_002429WATMLL_8-003083WILMER1_8C1 | 138 | 1 | Branch MVA | 750 | - | - | - | 104.8587 | 103.4245 | 116.1959 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SGVLSSTR (500085) -> SGVLSW1_8 ( 2434) CKT 2 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 129.1752 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SGVLSSTR (500085) -> SGVLSW1_8 ( 2434) CKT 2 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 1 | Branch MVA | 750 | - | - | 100.9153 | 137.7774 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SGVLSW1_5 ( 2433) -> SGVLSSTR (500085) CKT 2 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | 100.1052 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SGVLSW1_5 ( 2433) -> SGVLSSTR (500085) CKT 2 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | 100.1052 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SGVLSW1_5 ( 2433) -> SGVLSSTR (500085) CKT 2 | L_002429WATMLL_8-003083WILMER1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | 115.054 | 113.5228 | 129.0837 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SGVLSW1_5 ( 2433) -> SGVLSSTR (500085) CKT 2 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 135.5306 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SGVLSW1_5 ( 2433) -> SGVLSSTR (500085) CKT 2 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 1 | Branch MVA | 750 | - | - | 105.2382 | 148.1835 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SGVLSW1_8 ( 2434) -> SGVL1_8 ( 3076) CKT 1 | L_002429WATMLL_8-003083WILMER1_8C1 | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | 138.0685 | 140.9938 | 131.793 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SGVLSW1_8 ( 2434) -> SGVL1_8 ( 3076) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | - | - | 118.8766 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SGVLSW1_8 ( 2434) -> SGVL1_8 ( 3076) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | 132.0114 | - | - | -
TONCOR | EAST | EAST | EAST, EAST | SHAMBRGR_5 ( 3103) -> SHAMBRGR_8 ( 3104) CKT 1 | DRY_CREEK_CON | 345 | 138 | Branch MVA | 750 | - | - | - | - | 105.1903 | - | -
TONCOR | EAST | EAST | EAST, EAST | SHAMBRGR_5 ( 3103) -> SHAMBRGR_8 ( 3104) CKT 1 | L_003100MARTINLK_5-003102TYLERGND_5C1 | 345 | 138 | Branch MVA | 750 | - | - | - | - | 111.5265 | 100.3472 | -
TONCOR | EAST | EAST | EAST, EAST | SHAMBRGR_5 ( 3103) -> SHAMBRGR_8 ( 3104) CKT 1 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 345 | 138 | Branch MVA | 750 | - | - | - | - | 101.9917 | - | -
TONCOR | EAST | EAST | EAST, EAST | SHAMBRGR_5 ( 3103) -> SHAMBRGR_8 ( 3104) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | 138 | Branch MVA | 750 | - | - | - | - | 106.4705 | - | -
TONCOR | EAST | EAST | EAST, EAST | SHAMBRGR_5 ( 3103) -> SHAMBRGR_8 ( 3104) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 138 | Branch MVA | 750 | - | - | - | 141.2614 | 179.1857 | 150.8583 | -
TONCOR | EAST | EAST | EAST, EAST | SHAMBRGR_5 ( 3103) -> SHAMBRGR_8 ( 3104) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 345 | 138 | Branch MVA | 750 | - | - | 105.909 | 149.6998 | - | 156.1379 | -
TONCOR | EAST | EAST | EAST, EAST | SHAMBRGR_5 ( 3103) -> SHAMBRGR_8 ( 3104) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 138 | Branch MVA | 750 | - | - | - | - | 101.3796 | - | -
TONCOR | EAST | EAST | EAST, EAST | SHAMBRGR_8 ( 3104) -> TYLERNE_8 ( 3210) CKT 1 | L_003100MARTINLK_5-003102TYLERGND_5C1 | 138 | 138 | Branch Amp | 1416.1815 | - | - | - | 105.6258 | 128.9121 | 116.5367 | -
TONCOR | EAST | EAST | EAST, EAST | SHAMBRGR_8 ( 3104) -> TYLERNE_8 ( 3210) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1416.1815 | - | - | 105.409 | 147.081 | 182.0763 | 159.3937 | -
TONCOR | EAST | EAST | EAST, EAST | SHAMBRGR_8 ( 3104) -> TYLERNE_8 ( 3210) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1416.1815 | 103.5955 | - | 110.1174 | 152.7637 | - | 164.0755 | -
TONCOR | EAST | EAST | EAST, EAST | SHAMBRGR_8 ( 3104) -> TYLERNW_8 ( 3141) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1631.642 | - | - | - | 101.24 | 125.4525 | 110.7184 | -
TONCOR | EAST | EAST | EAST, EAST | SHAMBRGR_8 ( 3104) -> TYLERNW_8 ( 3141) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1631.642 | - | - | - | 106.3807 | - | 116.2418 | -
TONCOR | EAST | EAST | EAST, EAST | SHAMBRGR_8 ( 3104) -> TYLERNW_8 ( 3141) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 108.5495 | - | -
TONCOR | EAST | EAST | EAST, EAST | SHAMBRGR_8 ( 3104) -> TYLERNW_8 ( 3141) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 106.953 | - | -
TONCOR | EAST | EAST | EAST, EAST | SHAMBRGR_8 ( 3104) -> TYLERNW_8 ( 3141) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 112.4174 | 101.9709 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHANKLSW_8 (12329) -> GAMMA_8 (12344) CKT 1 | ENNIS WEST - STERRETT 138 KV (SINGLE B TO B) A REAGOR SPRINGS | 138 | 138 | Branch Amp | 1004.0873 | - | - | 114.5493 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHANKLSW_8 (12329) -> GAMMA_8 (12344) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 1004.0873 | - | - | 115.8878 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHANKLSW_8 (12329) -> GAMMA_8 (12344) CKT 1 | L_002320WAX_N_8-002321WAX_8C1 | 138 | 138 | Branch Amp | 1004.0873 | - | - | 102.5387 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHANKLSW_8 (12329) -> GAMMA_8 (12344) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 1004.0873 | - | - | 113.7348 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHANKLSW_8 (12329) -> GAMMA_8 (12344) CKT 1 | Pre-contingency | 138 | 138 | Amps | 1004.0874 | - | - | - | 118.426 | 133.0499 | 110.1273 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHANKLSW_8 (12329) -> GAMMA_8 (12344) CKT 1 | WAXAHACHI-WAXAHACHI OFC 69KV/ENNIS-STERRETT 138KV (DOUBLE B TO B) A REAGOR | 138 | 138 | Branch Amp | 1004.0873 | - | - | 114.5229 | - | - | - | -
TCPSE,RBECR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SHAULA ( 5380) -> ELMCREEK ( 5133) CKT 1 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 345 | 345 | Branch Amp | 1715.3158 | - | - | - | 100.9994 | - | - | -
TCPSE,RBECR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SHAULA ( 5380) -> ELMCREEK ( 5133) CKT 1 | DVCPA1C21B_2 | 345 | 345 | Branch Amp | 1715.3158 | - | - | - | 100.5278 | - | - | -
TCPSE,RBECR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SHAULA ( 5380) -> ELMCREEK ( 5133) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 345 | 345 | Branch Amp | 1715.3158 | - | - | - | 114.8212 | - | - | -
TCPSE,RBECR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SHAULA ( 5380) -> ELMCREEK ( 5133) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | 345 | Branch Amp | 1715.3158 | - | - | - | 105.0603 | - | - | -
TCPSE,RBECR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SHAULA ( 5380) -> ELMCREEK ( 5133) CKT 1 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 345 | 345 | Branch Amp | 1715.3158 | - | - | - | 101.3621 | - | - | -
TCPSE,RBECR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SHAULA ( 5380) -> ELMCREEK ( 5133) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 1715.3158 | - | - | - | 107.3979 | - | - | -
TCPSE,RBECR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SHAULA ( 5380) -> ELMCREEK ( 5133) CKT 1 | L_008715RADIANT7A-008728COBRA7AC1 | 345 | 345 | Branch Amp | 1715.3158 | - | - | - | 107.4873 | - | - | -
TCPSE,RBECR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SHAULA ( 5380) -> ELMCREEK ( 5133) CKT 1 | L_008728COBRA7A-081003HABER7AC1 | 345 | 345 | Branch Amp | 1715.3158 | - | - | - | 110.1937 | - | - | -
TCPSE,RBECR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SHAULA ( 5380) -> ELMCREEK ( 5133) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 345 | 345 | Branch Amp | 1715.3158 | - | - | - | 102.5212 | - | - | -
TCPSE,RBECR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SHAULA ( 5380) -> ELMCREEK ( 5133) CKT 1 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 345 | 345 | Branch Amp | 1715.3158 | - | - | - | 100.3933 | - | - | -
TCPSE,RBECR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | SHAULA ( 5380) -> ELMCREEK ( 5133) CKT 1 | P7-1_E1>>T2764Y_ERCa | 345 | 345 | Branch Amp | 1715.3158 | - | - | - | 103.8583 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 1316.191 | - | - | - | - | 100.5386 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | 3WT_001918SHRYAUTO1_5_001920SHRY_B8_011920SHRY_B_3 C 1 | 138 | 138 | Branch Amp | 1316.191 | - | - | - | - | 100.9128 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | 3WT_002420CHILSW1_5_016421CHILSW_1T8_012419CHILSW1_3 C 1 | 138 | 138 | Branch Amp | 1316.191 | - | - | - | - | 102.759 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1316.191 | - | - | - | 109.9165 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1316.191 | - | - | - | 103.7562 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 1316.191 | - | - | - | 126.5828 | 137.0845 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1316.191 | - | - | - | 128.3529 | 138.6435 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | G_150023MCSES_UNIT8UN8 | 138 | 138 | Branch Amp | 1316.191 | - | - | - | - | 101.0995 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 138 | 138 | Branch Amp | 1316.191 | - | - | - | - | 100.3433 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 138 | 138 | Branch Amp | 1316.191 | - | - | - | - | 101.4336 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 138 | 138 | Branch Amp | 1316.191 | - | - | - | - | 102.0139 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 138 | 138 | Branch Amp | 1316.191 | - | - | - | - | 100.6764 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | L_001920SHRY_B8-002258PARKROW2_8C1 | 138 | 138 | Branch Amp | 1316.191 | - | - | - | - | 103.5205 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 138 | 138 | Branch Amp | 1316.191 | - | - | - | 102.0881 | 108.2006 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 138 | 138 | Branch Amp | 1316.191 | - | - | - | 104.8676 | 111.242 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | L_002258PARKROW2_8-002259LTV1_8C1 | 138 | 138 | Branch Amp | 1316.191 | - | - | - | - | 102.4388 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | L_002259LTV1_8-002262GRANDPR1_8C1 | 138 | 138 | Branch Amp | 1316.191 | - | - | - | - | 101.5328 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 1316.191 | - | - | - | - | 104.3177 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1316.191 | - | - | - | 100.8791 | 106.8637 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1316.191 | - | - | - | 100.7445 | 106.6629 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1316.191 | - | - | - | 103.2145 | 109.1904 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 1316.191 | - | - | - | 103.532 | 110.9943 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1316.191 | - | - | - | - | 100.9267 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1316.191 | - | - | - | 101.4496 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_A8 ( 1919) -> PARKROW1_8 ( 2257) CKT 1 | XFMR-MTCK_8T8-8 | 138 | 138 | Branch Amp | 1316.191 | - | - | - | - | 101.0995 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | 3WT_002420CHILSW1_5_016421CHILSW_1T8_012419CHILSW1_3 C 1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | - | 106.7482 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | 104.2212 | - | 104.1858 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | - | 103.2646 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | 119.4662 | - | 112.9172 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | CEDAR HILL SW 345-138 KV AUTO #1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | 104.9536 | - | 118.7671 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | 120.8774 | - | 114.3749 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | DIVISION-SHERRY/GENERAL MOTORS 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | 102.3186 | - | 106.0409 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | G_150023MCSES_UNIT8UN8 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | - | 101.4732 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | GENERAL MOTORS-SHERRY/ EXECUTIVE PKWY-CEDAR HILL(DOUBLE B TO B) | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | - | 101.6878 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | L_001919SHRY_A8-002257PARKROW1_8C1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | - | 100.0152 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | L_001920SHRY_B8-002140GEN_MOT2_8C1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | 102.8485 | - | 106.5515 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | 101.1771 | - | 100.6881 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | L_002140GEN_MOT2_8-012265GPWEST_T8C1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | - | 102.7747 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | L_002274DALWRTH1_8-012265GPWEST_T8C1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | - | 102.7774 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | L_002421CHILSW_S8-012491FSHCRK2_8C1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | - | 121.1478 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | LIGGETT - GENERAL MOTORS 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | - | 102.2222 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | 100.9731 | - | 103.2424 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-2 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | 101.2359 | - | 103.3733 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | - | 100.5597 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | 100.971 | - | 103.6604 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | - | 101.3551 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | 101.3072 | - | 103.0306 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-2 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | 101.2598 | - | 103.386 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | 101.0038 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | - | 101.0399 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 ( 1920) -> PARKROW2_8 ( 2258) CKT 1 | XFMR-MTCK_8T8-8 | 138 | 138 | Branch Amp | 1317.8646 | - | - | - | - | - | 101.4732 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRY_B8 (1920) -> PARKROW2_8 (2258) CKT 1 | Pre-contingency | 138 | 138 | Amps | 1317.8646 | - | - | - | - | 107.5021 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRYASTR (500059) -> SHRY_B8 ( 1920) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 1 | Branch MVA | 625 | - | - | - | - | 106.3188 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRYASTR (500059) -> SHRY_B8 ( 1920) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 1 | Branch MVA | 625 | - | - | - | - | 107.937 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRYASTR (500059) -> SHRY_B8 ( 1920) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 138 | 1 | Branch MVA | 625 | - | - | - | - | 106.6922 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRYASTR (500059) -> SHRY_B8 ( 1920) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 138 | 1 | Branch MVA | 625 | - | - | - | 100.2789 | 109.923 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRYASTR (500059) -> SHRY_B8 ( 1920) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 138 | 1 | Branch MVA | 625 | - | - | - | 100.3434 | 109.9456 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRYASTR (500059) -> SHRY_B8 ( 1920) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 1 | Branch MVA | 625 | - | - | - | 102.0554 | 112.1903 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRYAUTO1_5 ( 1918) -> SHRYASTR (500059) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 1 | Branch MVA | 625 | - | - | - | - | 107.7325 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRYAUTO1_5 ( 1918) -> SHRYASTR (500059) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 625 | - | - | - | - | 109.5654 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRYAUTO1_5 ( 1918) -> SHRYASTR (500059) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 345 | 1 | Branch MVA | 625 | - | - | - | - | 100.0256 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRYAUTO1_5 ( 1918) -> SHRYASTR (500059) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 345 | 1 | Branch MVA | 625 | - | - | - | - | 107.9798 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRYAUTO1_5 ( 1918) -> SHRYASTR (500059) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 345 | 1 | Branch MVA | 625 | - | - | - | 100.484 | 111.1879 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRYAUTO1_5 ( 1918) -> SHRYASTR (500059) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 345 | 1 | Branch MVA | 625 | - | - | - | 100.5538 | 111.246 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SHRYAUTO1_5 ( 1918) -> SHRYASTR (500059) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | 1 | Branch MVA | 625 | - | - | - | 102.2837 | 113.4237 | - | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | CLUTCH_CITY_CON | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | 103.9286 | 106.9484 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_042050CLUTE___B138-042190BIPORT_X82B8C&1-MS | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | 125.6314 | 131.8942 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_042100HUDSON_POI_8-042940MONSAN_POI_8C04 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 102.7815 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_042100HUDSON_POI_8-888849CLUTCH_CITY_POIC04 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | 103.1984 | 107.0654 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_042150BASF___POI_8-042210BRZPRT_S02_8C02 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 104.003 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_042150BASF___POI_8-042810HOFMAN_X02B8C02 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 107.3929 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_042190BIPORT_X82B8-043335OYSCRK_POI_8C&1-MS | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | 117.4856 | 123.6694 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_042210BRZPRT_S02_8-042215COPPER_X02B8C02 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 101.5563 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_042215COPPER_X02B8-042540JONCRK__B138C&1-MS | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 102.8375 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_042570ARCHER_POI_8-044430MANVEL_S26_8C26 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | 101.7774 | 105.7453 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_042810HOFMAN_X02B8-042880LKJACK_S02_8C02 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 107.6108 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_042880LKJACK_S02_8-043170RETREV__B138C&1-MS | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | 102.6724 | 110.692 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_042940MONSAN_POI_8-043070PETSON_X04B8C04 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | 100.2271 | 104.1128 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_042960MUSTNG_S04_8-043500WEBSTR_B138AC&1-MS | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | 113.4955 | 117.2178 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_043070PETSON_X04B8-044890SNUG___POI_8C04 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | 100.8841 | 104.7614 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_043335OYSCRK_POI_8-043345GLOBAL_X82B8C&1-MS | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | 104.4282 | 110.4432 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_043345GLOBAL_X82B8-043360VLASCO__B138C&1-MS | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 102.652 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_044410KARSTN_C26_8-048173ALVIN_26TP_8C26 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 102.1528 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_044430MANVEL_S26_8-048173ALVIN_26TP_8C26 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 102.6438 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | L_888849CLUTCH_CITY_POI-042960MUSTNG_S04_8C04 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | 114.5371 | 118.2579 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | P1-2_ALVIN_CKT05 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 102.6352 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | P7-1_E1>>T0202C | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 107.5524 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | P7-1_E1>>T0202E | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 103.346 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | P7-1_E1>>T0202H | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 102.8299 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | P7-1_E1>>T0405 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | 113.519 | 117.3683 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | P7-1_E1>>T0463 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | 113.5504 | 117.2691 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | P7-1_E1>>T0493 | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | 113.3272 | 117.0301 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | P7-1_E1>>T1827FX | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 100.5928 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | P7-1_E1>>T1827K | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 103.631 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | P7-1_E1>>T2626D | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | 101.8714 | 105.9416 | -
TCNPE | COAST | COAST | COAST, COAST | SINTEK_X26B8 (43240) -> CAMDEN_X26B8 (43365) CKT 26 | P7-1_E1>T0202GX | 138 | 138 | Branch Amp | 1727.8669 | - | - | - | - | - | 106.1051 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SMPST2T_8 ( 2986) -> WITTRD1_8 ( 3067) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1199.8844 | - | - | - | - | 107.9121 | - | -
TONCOR | EAST | EAST | EAST, EAST | SMRFLDMT_8 ( 3112) -> JAXVLSW_8 ( 3253) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 100.1453 | 107.3362 | - | -
TONCOR | EAST | EAST | EAST, EAST | SMRFLDMT_8 ( 3112) -> JAXVLSW_8 ( 3253) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 103.212 | - | 103.3815 | -
1 | WEST | WEST | WEST, WEST | SNYDER_8 ( 1305) -> ONC900014_TAP ( 1298) CKT 1 | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 773.984 | 100.5697 | 101.2868 | 101.8208 | 101.7737 | - | - | -
1 | WEST | WEST | WEST, WEST | SNYDER_8 ( 1305) -> ONC900014_TAP ( 1298) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 773.984 | - | 103.0939 | - | - | - | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | AEN_LP-AU¦DL_2013 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 100.3103 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | AEN_LY-FPP:CIS-HO | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 103.6229 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | AEN_LY-FPP¦CIS | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 104.9854 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 115.1967 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | BAS_RANCH_CON | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 103.895 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 109.5391 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 108.1659 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 106.3471 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | E_B_DAVIS_CC1_TRAIN | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 102.153 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | E_BRAUNIG_CC1_TRAIN | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 100.7124 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | E_INGLCOSW_CC1_TRAIN | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 100.4739 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | E_NEDIN_CC1_TRAIN | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 102.4966 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | E_NUECES_B_CC1_TRAIN | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 102.5047 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | G_112351OLDHCKRY_S1US1 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 105.0931 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | G_170126CALAVER_JKS2UL2 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 104.0105 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | G_170671CACHENA_S1US1 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 104.5171 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | G_888839BAS_RANCH_POIUC1 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 103.883 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | G_RIO_TRAIN | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 103.0507 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | J5LCA1C1_B | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 103.0468 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 109.0925 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | L_005133ELMCREEK-005380SHAULAC1 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 126.2104 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | L_005380SHAULA-005915SO_TEX__345AC1 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 117.5292 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 112.4115 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 118.0353 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 118.6329 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | L_080071ZORILLO7A-080076AJO7AC1 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 100.673 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 110.9187 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | LCRA TSC_T185_T246 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 104.0686 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | LCRA TSC_T255_TAE3121_1 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 105.8575 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 103.9105 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | M10000271115801 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 102.3067 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | M115851115803 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 100.673 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | MB100002711580 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 102.3067 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | MB1158011585 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 100.673 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | N5GSU2_B | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 104.0105 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 100.5583 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | P7-1_E1>>T1839X1_ERC | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 116.1912 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | P7-1_E1>>T1839X2_ERC | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 114.1754 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | P7-1_E1>>T3944Z_ERC | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 110.8931 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | P7-1_E1>>T9899A | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 100.1915 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | R4U2A5C1_1_B | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 100.6739 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | SAN_PAT_CON | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 100.1017 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | STP - HOUDINI & STP - SHAULA | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 119.6477 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 102.0802 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 100.3268 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 100.0435 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 100.2754 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 100.971 | - | -
TCPSE,RBECR | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> OLD_HCKRY_5 ( 5323) CKT 2 | WAP - HOUDINI & STP - SHAULA | 345 | 345 | Branch Amp | 1551.3149 | - | - | - | - | 115.7906 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | AEN_LP-AU¦DL_2013 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.5198 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | AEN_LY-FPP:CIS-HO | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 103.7754 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | AEN_LY-FPP¦CIS | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 104.9354 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 112.5403 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | AEN_P7 FPP-LP.DC_1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.3695 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | ARGENTA_CON | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 107.3871 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | BAS_RANCH_CON | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 104.8428 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 108.5558 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 107.5026 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 106.1221 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | CACTUS_CON | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.1471 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | DVCPA1C21B_1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 108.206 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | DVCPA1C21B_2 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 110.6195 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E_B_DAVIS_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 110.3256 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E_BASTEN_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.5743 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E_BRAUNIG_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 103.3963 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E_CCEC_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 104.8971 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E_DUKE_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 104.738 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E_FERGCC_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.9437 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E_GUADG_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.4783 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E_GUADG_CC2_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.4453 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E_INGLCOSW_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 107.2541 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E_LGE_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 104.9906 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E_NEDIN_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 108.2576 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E_NUECES_B_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 110.402 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E_VICTORIA_CC1_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.4548 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E_WHCCS2_CC2_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.857 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E5DVA1C1_1_B | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | 107.3984 | - | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E5P4A1C1_B | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.5592 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E5SCA1C1_B | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.2579 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | E5T5A1C1_B | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.7977 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_007044L_MARION5_1YUN1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.2027 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_008249ANGSTRM7AUS1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.3223 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_008573BONILLA7AUW1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.058 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_080039LUCERO7AUS1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.0507 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_080039LUCERO7AUS2 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.1627 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_080219LOBO7AUS1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.2469 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_113051GARCITAS_S1US1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 103.2378 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_113111LUNIS_CK_S1US1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 134.8832 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_150111CPSES_UNIT1UU1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.2547 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_150112CPSES_UNIT2UU2 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.2787 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_160101B_D_B_DAVIG1UN1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.9335 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_160131SAN_SANMIGG1UL1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.0514 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_160151INGLCOS_CTG1UPE | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.0888 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_160152INGLCOS_CTG2UPE | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.0888 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_163521PEREGRN_S1US1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.1362 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_163641CHARGER_S1US1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 105.5762 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_163881TULSITA_S1US1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.209 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_163931OUTPOST_S1US1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.5464 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_170126CALAVER_JKS2UL2 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 107.0841 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_170671CACHENA_S1US1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.7221 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_888839BAS_RANCH_POIUC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 104.8318 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_888858ARGENTA_POIUS1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.0782 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | G_RIO_TRAIN | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 104.098 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | J5LCA1C1_B | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 104.1086 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.9203 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.1577 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 113.1385 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 127.1145 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 115.1348 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_005133ELMCREEK-005380SHAULAC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 118.1475 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 111.7633 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_005380SHAULA-005915SO_TEX__345AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 111.5234 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_005779REDSWTAP8-005784REDGATESW8C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.4967 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_005779REDSWTAP8-161031REDGATE_5C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.4967 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_005915SO_TEX__345A-008123BLESSING7AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.9305 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 119.4886 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.5749 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_008162COLETO4A-008172VICTORIA4AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.1626 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_008162COLETO4A-008172VICTORIA4AC2 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.434 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_008319RIOHONDO4A-160750LV1_AB_8C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.0742 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_008380NEDIN4A-160234NEDIN_1_8C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.3756 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_008380NEDIN4A-160235NEDIN_2_8C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.3756 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 103.5204 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_008455LONHILL7A-008579KATOEN7AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 106.2115 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_008458B_DAVIS4A-160105B_DAVIS_1_8C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.9335 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_008458B_DAVIS4A-160106B_DAVIS_2_8C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 103.4936 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_008579KATOEN7A-008606GODDARD7AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 104.751 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_008606GODDARD7A-888858ARGENTA_POIC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.9945 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_009043CISTERN-009074LYTTON5C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.5969 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 115.2516 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_080071ZORILLO7A-080076AJO7AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 106.31 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_080071ZORILLO7A-080171SARITA7AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 103.2572 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_080171SARITA7A-160299BAFFIN_2_5C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 103.257 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_888858ARGENTA_POI-008689TANGO7AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.6922 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 109.4157 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | L10011585 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 103.2572 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | LCRA TSC_T185_T246 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.6871 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | LCRA TSC_T255_TAE3121_1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 105.7272 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 104.3335 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | M10000271115801 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 108.5539 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | M100052100072 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.1618 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | M105311105321 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 104.9904 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | M115851115803 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 106.31 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | M128103100534 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.6 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | M128104100523 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.3148 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | M128152129153 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.4167 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | MB100002711580 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 108.5539 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | MB1000710005-2 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.3553 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | MB1005312810 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.5177 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | MB1101411110-1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.7598 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | MB1158011585 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 106.31 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | MB1281010052 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.2327 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | MB1291512815a | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.3842 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | N5GSU2_B | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 107.0841 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.3137 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | P7-1_E1>>T1839X1_ERC | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 110.516 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | P7-1_E1>>T1839X2_ERC | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 108.1199 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | P7-1_E1>>T2764Y_ERCa | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 113.419 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | P7-1_E1>>T4848K | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.622 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | P7-1_E1>>T7475A | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.3753 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | P7-1_E1>>T9899A | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.8094 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.7763 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | R4U2A5C1_1_B | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 103.3486 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | SAN_PAT_CON | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 105.5968 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | STECL_10262 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.0514 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | STP - HOUDINI & STP - SHAULA | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 113.2955 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | T_008121BLESSING4A-008123BLESSING7AC1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.9358 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 100.6117 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.9938 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.6203 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.4174 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.5873 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | U3GSU1_B | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 101.0183 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 102.194 | - | -
TAEPTC | COAST | COAST | COAST, COAST | SO_TEX__345A ( 5915) -> RADIANT7A ( 8715) CKT 1 | WAP - HOUDINI & STP - SHAULA | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | 110.2001 | - | -
TCPSE,RBECR | SOUTH_CE | COAST | SOUTH_CE, COAST | SO_TEX__345A ( 5915) -> SHAULA ( 5380) CKT 1 | DVCPA1C21B_2 | 345 | 345 | Branch Amp | 1783.9285 | - | - | - | - | 100.8796 | - | -
TCPSE,RBECR | SOUTH_CE | COAST | SOUTH_CE, COAST | SO_TEX__345A ( 5915) -> SHAULA ( 5380) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 345 | 345 | Branch Amp | 1783.9285 | - | - | - | - | 118.7645 | - | -
TCPSE,RBECR | SOUTH_CE | COAST | SOUTH_CE, COAST | SO_TEX__345A ( 5915) -> SHAULA ( 5380) CKT 1 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 345 | 345 | Branch Amp | 1783.9285 | - | - | - | - | 106.1948 | - | -
TCPSE,RBECR | SOUTH_CE | COAST | SOUTH_CE, COAST | SO_TEX__345A ( 5915) -> SHAULA ( 5380) CKT 1 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 345 | 345 | Branch Amp | 1783.9285 | - | - | - | - | 101.9622 | - | -
TCPSE,RBECR | SOUTH_CE | COAST | SOUTH_CE, COAST | SO_TEX__345A ( 5915) -> SHAULA ( 5380) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 345 | Branch Amp | 1783.9285 | - | - | - | - | 102.4203 | - | -
TCPSE,RBECR | SOUTH_CE | COAST | SOUTH_CE, COAST | SO_TEX__345A ( 5915) -> SHAULA ( 5380) CKT 1 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 345 | 345 | Branch Amp | 1783.9285 | - | - | - | - | 102.8266 | - | -
TCPSE,RBECR | SOUTH_CE | COAST | SOUTH_CE, COAST | SO_TEX__345A ( 5915) -> SHAULA ( 5380) CKT 1 | P7-1_E1>>T2764Y_ERCa | 345 | 345 | Branch Amp | 1783.9285 | - | - | - | - | 103.876 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SOAPCRK_8 ( 2289) -> MDLTHTXI2_8 ( 2310) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.1821 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SOAPCRK_8 ( 2289) -> MDLTHTXI2_8 ( 2310) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 100.6742 | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SOLSTICE7A (60404) -> SOLSTICE4A (60385) CKT T1 | T_060404SOLSTICE7A-060385SOLSTICE4ACT2 | 345 | 138 | Branch MVA | 675 | - | - | 104.2575 | 100.4008 | 111.1964 | 111.9008 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | SOLSTICE7A (60404) -> SOLSTICE4A (60385) CKT T2 | T_060404SOLSTICE7A-060385SOLSTICE4ACT1 | 345 | 138 | Branch MVA | 675 | - | - | 104.3092 | 100.4562 | 111.2572 | 111.9554 | -
TAEPTN | FAR_WEST | WEST | FAR_WEST, WEST | SONR2A ( 6513) -> ATSO2A (6511) CKT 1 | L_006562FDRAN4A-060412CARVER4AC1 | 69 | 69 | Branch Amp | 317.961 | 103.3491 | 131.7646 | 138.3369 | 105.691 | 131.9175 | 105.9213 | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SONTERRA ( 121) -> JARRELL_E_8 ( 3688) CKT 1 | BELLCNTY8-BARTLETTSW (SINGLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 111.2051 | 100.1251 | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SONTERRA ( 121) -> JARRELL_E_8 ( 3688) CKT 1 | BEPC_215_2 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 110.3419 | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SONTERRA ( 121) -> JARRELL_E_8 ( 3688) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 117.874 | - | 107.5956 | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SONTERRA ( 121) -> JARRELL_E_8 ( 3688) CKT 1 | L_000114BARTLETTSW-000122SCHWERTNERC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 110.7544 | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SONTERRA ( 121) -> JARRELL_E_8 ( 3688) CKT 1 | L_000114BARTLETTSW-000132BELLCNTY8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 100.3001 | 111.5284 | 100.4344 | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SONTERRA ( 121) -> JARRELL_E_8 ( 3688) CKT 1 | L_000122SCHWERTNER-007346L_GABRIE8_1YC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 108.6573 | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SONTERRA ( 121) -> JARRELL_E_8 ( 3688) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 127.1507 | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SONTERRA ( 121) -> JARRELL_E_8 ( 3688) CKT 1 | LCRA TSC_T359_T21422_1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 105.2932 | - | -
TBREC | NORTH_CE | NORTH | NORTH_CE, NORTH | SPRING ( 684) -> BLUHORSE ( 612) CKT 1 | KRUM TAP - ARGYLE SW 138 KV (SINGLE B TO B) ARGYLE N | 138 | 138 | Branch Amp | 1146.333 | - | - | - | - | 104.2923 | - | -
TBREC | NORTH_CE | NORTH | NORTH_CE, NORTH | SPRING ( 684) -> BLUHORSE ( 612) CKT 1 | L_001984ARGYLE1_8-011986ARGYLEN_8C1 | 138 | 138 | Branch Amp | 1146.333 | - | - | - | - | 104.2944 | - | -
TBREC | NORTH_CE | NORTH | NORTH_CE, NORTH | SPRING ( 684) -> BLUHORSE ( 612) CKT 1 | L_001986KRUM_T8-011986ARGYLEN_8C1 | 138 | 138 | Branch Amp | 1146.333 | - | - | - | - | 104.2888 | - | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | SPUR2A ( 6148) -> GIRA_TAP2A ( 6151) CKT 1 | L_006195ROBY2A-006196ROTN2AC1 | 69 | 69 | Branch Amp | 267.7566 | 117.6887 | - | 114.44 | 105.7815 | 107.4777 | 107.7428 | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | SPUR4A ( 6150) -> SPUR2A ( 6148) CKT 1 | L_006195ROBY2A-006196ROTN2AC1 | 69 | 138 | Branch MVA | 56 | 107.3043 | - | 105.9417 | 103.097 | - | 102.3457 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SSWWT2T_8 ( 3079) -> GELLER_8 ( 2263) CKT 1 | L_002429WATMLL_8-003083WILMER1_8C1 | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | 130.7843 | 133.7437 | 124.8761 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SSWWT2T_8 ( 3079) -> GELLER_8 ( 2263) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | - | - | 111.5804 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SSWWT2T_8 ( 3079) -> GELLER_8 ( 2263) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | 124.5363 | - | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | STANTON_E_8 ( 1326) -> STANTON_E_9 ( 1230) CKT 1 | T_001330SPRABERY_9-001329SPRABERY_8C1 | 69 | 138 | Branch MVA | 63 | - | - | - | 108.5415 | 157.5077 | 156.7538 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | STANTON_E_9 ( 1230) -> MARTINCAP_9 ( 1231) CKT 1 | T_001330SPRABERY_9-001329SPRABERY_8C1 | 69 | 69 | Branch Amp | 334.6958 | 109.2385 | - | 110.6731 | 167.0194 | 241.373 | 240.8065 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STATIC7A ( 8676) -> HABER7A (81003) CKT 1 | Haber - Coleto Creek | 345 | 345 | Branch Amp | 1780.5815 | - | - | - | - | - | 124.7961 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | STEKLY_DAM_5 ( 3306) -> BELFALLS_8 ( 3404) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 108.4441 | 113.4092 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | STEKLY_DAM_5 ( 3306) -> BELFALLS_8 ( 3404) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.9918 | 109.0042 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | STEKLY_DAM_5 ( 3306) -> BELFALLS_8 ( 3404) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | - | 104.2095 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | STEKLY_DAM_5 ( 3306) -> BELFALLS_8 ( 3404) CKT 1 | LAKE CREEK - LAKE HALL/TRADINGHOUSE_5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | - | 108.4967 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | STEKLY_DAM_5 ( 3306) -> BELFALLS_8 ( 3404) CKT 1 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | - | 110.547 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | STEKLY_DAM_5 ( 3306) -> BELFALLS_8 ( 3404) CKT 1 | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | - | 119.3999 | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | L_001351BSPGGULF_9-001353SIGNALMTN_9C1 | 69 | 69 | Branch Amp | 317.961 | 102.2825 | - | 109.2574 | 123.6128 | 122.2666 | 120.4401 | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | L_010050RANGER_8-011332BRELYN_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 100.2774 | - | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | LCRA TSC_BAKERS_CEDACA_DC | 69 | 69 | Branch Amp | 317.961 | - | 108.9185 | - | - | 101.6504 | - | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-1 | 69 | 69 | Branch Amp | 317.961 | - | 105.4336 | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-2 | 69 | 69 | Branch Amp | 317.961 | - | 103.9154 | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-1 | 69 | 69 | Branch Amp | 317.961 | - | 105.4335 | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-2 | 69 | 69 | Branch Amp | 317.961 | - | 103.9153 | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | LCRA TSC_NOELK_SNGTR_NOELK_SNGTR2 | 69 | 69 | Branch Amp | 317.961 | - | 102.5412 | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | LCRA TSC_SNGTR_SCHDR_SNGTR_SCHDR2 | 69 | 69 | Branch Amp | 317.961 | - | 101.2615 | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | LCRA TSC_T422_T550 | 69 | 69 | Branch Amp | 317.961 | - | 102.4796 | - | - | 100.1125 | - | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | New Meinan - Sweeteast and BitterCreek 345kV Double | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 100.0248 | - | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 101.49 | - | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | STECL_4720 | 69 | 69 | Branch Amp | 317.961 | - | 102.1226 | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | STECL_4721-1 | 69 | 69 | Branch Amp | 317.961 | - | 105.4336 | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | STECL_4721-2 | 69 | 69 | Branch Amp | 317.961 | - | 103.9154 | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | T_001322BIGSPRIG_8-001323BIGSPRIG_9C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 114.0362 | 108.453 | -
TAEPTN | WEST | WEST | WEST, WEST | STER2A ( 6435) -> CAMPELIZ2A ( 6641) CKT 1 | XFMR-RANGER_5 | 69 | 69 | Branch Amp | 317.961 | - | 115.1439 | - | - | - | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STERRETT1_8 ( 2317) -> STERTRD_8 ( 2237) CKT 1 | 3WT_002431DESSW1_5_002424DESSW1_8_012431DESSW1_3 C 1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 104.4088 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STERRETT1_8 ( 2317) -> STERTRD_8 ( 2237) CKT 1 | CEDAR HILL - DESOTO/LOOP NINE 345 KV DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 100.0505 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STERRETT1_8 ( 2317) -> STERTRD_8 ( 2237) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 117.2032 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STERRETT1_8 ( 2317) -> STERTRD_8 ( 2237) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 116.741 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STERRETT1_8 ( 2317) -> STERTRD_8 ( 2237) CKT 1 | ENNIS - PEBBLE CREEK 138 KV SWITCH (SINGLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 138.7666 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STERRETT1_8 ( 2317) -> STERTRD_8 ( 2237) CKT 1 | L_000217GLNHEIGHTS-002237STERTRD_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 108.4013 | 106.3854 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STERRETT1_8 ( 2317) -> STERTRD_8 ( 2237) CKT 1 | L_000217GLNHEIGHTS-002424DESSW1_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 121.9478 | 119.5588 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STERRETT1_8 ( 2317) -> STERTRD_8 ( 2237) CKT 1 | L_000221TRUMBULL8-002229PEBBLCRK_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 133.8456 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STERRETT1_8 ( 2317) -> STERTRD_8 ( 2237) CKT 1 | L_000221TRUMBULL8-012344GAMMA_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 135.5792 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STERRETT1_8 ( 2317) -> STERTRD_8 ( 2237) CKT 1 | L_012329SHANKLSW_8-012344GAMMA_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 135.5458 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STERRETT1_8 ( 2317) -> STERTRD_8 ( 2237) CKT 1 | STERRETT 5400 - DESOTO (SINGLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 108.2947 | 106.3326 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STERRETT1_8 ( 2317) -> STERTRD_8 ( 2237) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 895.3112 | - | - | - | - | 104.2265 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | E_NEDIN_CC1_TRAIN | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 102.7742 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | E5DVA1C1_1_B | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 101.0789 | - | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L_005756LAURELESSUB8-008266MARCONI4AC1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 103.5194 | 103.4435 | 103.6555 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L_005756LAURELESSUB8-008314LA_PALMA4AC1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 104.4063 | 104.3308 | 104.5455 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L_005761PAREDESSW8-005764ERIOHONDOSB8C1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 101.2171 | 101.0915 | 101.1724 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L_005761PAREDESSW8-005766CNTRLAVESUB8C1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 113.2383 | 113.2701 | 113.4899 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L_005766CNTRLAVESUB8-008914COFFPORT4AC1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 110.5614 | 110.5491 | 110.7596 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L_005767HIWAY511SUB8-008735CHALYBE4AC1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 109.095 | 109.1023 | 109.3026 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L_005767HIWAY511SUB8-008914COFFPORT4AC1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 110.8713 | 110.8892 | 111.0961 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L_005963TITAN-005965PALOALTOC1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 104.407 | 104.7296 | 104.858 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L_005963TITAN-008735CHALYBE4AC1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 102.5089 | 102.8891 | 102.8153 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L_005965PALOALTO-008950OLMITO4AC1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 109.883 | 110.1051 | 110.1074 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L_008047OCELOTAP4A-008275MILITARY4DC1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 112.3625 | 112.6473 | 112.6067 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L_008047OCELOTAP4A-008950OLMITO4AC1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 112.3824 | 112.6689 | 112.6265 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L_008266MARCONI4A-008338P_ISABEL4AC1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 112.4552 | 112.4858 | 112.5741 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L_008317LA_PALMA7A-079501KINGFISHERC1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 101.3292 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L_008338P_ISABEL4A-008735CHALYBE4AC1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 104.7596 | 104.8821 | 105.0094 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L_008535POMPANO4A-008735CHALYBE4AC1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 171.8174 | 172.5287 | 173.162 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L10010434_MODIFIED_BY_MZ | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 109.2928 | 109.3274 | 109.5226 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | L10011660_MODIFIED_BY_MZ | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 110.0469 | 110.2508 | 110.2914 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | STILLMAN (79601) -> POMPANO4A ( 8535) CKT 1 | T100001 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | - | 100.7544 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 117.7464 | 144.9745 | 131.1678 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 111.4245 | 140.3626 | 126.1728 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | 104.5594 | 133.7163 | 120.7246 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | G_150741SCES_UNIT1UL1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.3174 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | LAKE CREEK - RATTLE SNAKE 345 KV WITH SANDY UNIT (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.3158 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 124.4199 | 114.3761 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 113.8738 | 102.2078 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 111.3048 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | RAT_SNAKE-SNDY_CREEK_5 (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.3173 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 105.5903 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 117.1808 | 109.2414 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 103.768 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 109.4258 | 103.5062 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 108.6649 | 103.2212 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 109.6423 | 103.9186 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.1985 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | STJOHNS_5 ( 3384) -> LAKE_CRK1_5 ( 3409) CKT 1 | XFMR-SANDYCRK_5-01 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 104.3174 | - | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | STRS2A ( 6547) -> BISON2A (60395) CKT 1 | L_060361SANTARIT4A-060414OWLS4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 119.1397 | 115.1683 | 115.3403 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | STRS2A ( 6547) -> BISON2A (60395) CKT 1 | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 119.1458 | 115.0239 | 115.1299 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | STRS2A ( 6547) -> BISON2A (60395) CKT 1 | L_060723CROSSOVE4A-060728PALOUSE4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 128.7983 | 126.4587 | 129.6599 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | STRS2A ( 6547) -> BISON2A (60395) CKT 1 | L_060723CROSSOVE4A-076032L_NORTMC8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 128.8469 | 126.5133 | 129.7203 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | STRS2A ( 6547) -> BISON2A (60395) CKT 1 | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 117.6694 | 114.3381 | 114.4066 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | STRS2A ( 6547) -> BISON2A (60395) CKT 1 | L2020944-A | 69 | 69 | Branch Amp | 317.961 | - | - | - | 119.1486 | 115.0334 | 115.1303 | -
TAEPTN | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | STRS2A ( 6547) -> BISON2A (60395) CKT 1 | L2020944-B | 69 | 69 | Branch Amp | 317.961 | - | - | - | 128.7979 | 126.4584 | 129.6593 | -
TONCOR | EAST | EAST | EAST, EAST | STRYKER_5 ( 3109) -> TRINDAD1_5 ( 3123) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.0447 | 114.9882 | 108.1655 | -
TONCOR | EAST | EAST | EAST, EAST | STRYKER_5 ( 3109) -> TRINDAD1_5 ( 3123) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 106.0044 | - | 111.879 | -
TONCOR | EAST | EAST | EAST, EAST | STRYKER_5 ( 3109) -> TRINDAD1_5 ( 3123) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 101.7496 | 114.6358 | 107.7895 | -
TONCOR | EAST | EAST | EAST, EAST | STRYKER_5 ( 3109) -> TRINDAD1_5 ( 3123) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.1479 | - | -
TONCOR | EAST | EAST | EAST, EAST | STRYKER_5 ( 3109) -> TRINDAD1_5 ( 3123) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.9667 | - | -
TONCOR | EAST | EAST | EAST, EAST | STRYKER_5 ( 3109) -> TRINDAD1_5 ( 3123) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.7298 | 115.3505 | 108.806 | -
TONCOR | EAST | EAST | EAST, EAST | STRYKER_5 ( 3109) -> TRINDAD1_5 ( 3123) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 106.2102 | 120.3317 | 112.1784 | -
TONCOR | EAST | EAST | EAST, EAST | STRYKER_8 ( 3110) -> SMRFLDMT_8 ( 3112) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 103.0144 | 110.3095 | 102.7849 | -
TONCOR | EAST | EAST | EAST, EAST | STRYKER_8 ( 3110) -> SMRFLDMT_8 ( 3112) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 106.0973 | - | 106.2871 | -
TONCOR | EAST | EAST | EAST, EAST | STRYKER_8 ( 3110) -> STRYKERTA_8 ( 3111) CKT 1 | TRIN-SK*ME (DOUBLE B TO B) | 138 | 138 | Branch Amp | 886.9437 | - | - | - | 107.098 | 111.0851 | 107.3957 | -
TONCOR | EAST | EAST | EAST, EAST | STRYKERTA_8 ( 3111) -> DIALVILL_8 ( 3160) CKT 1 | TRIN-SK*ME (DOUBLE B TO B) | 138 | 138 | Branch Amp | 886.9437 | - | - | - | 107.098 | 111.0851 | 107.3957 | -
TONCOR | EAST | EAST | EAST, EAST | SULBLF1_8 ( 1796) -> WHITEOAK_T (11796) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 119.4481 | 136.6965 | 120.109 | -
TONCOR | EAST | EAST | EAST, EAST | SULBLF1_8 ( 1796) -> WHITEOAK_T (11796) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 138 | 138 | Branch Amp | 748.8818 | - | - | 102.9073 | 128.8742 | 146.6577 | 128.5736 | -
TONCOR | EAST | EAST | EAST, EAST | SULBLF1_8 ( 1796) -> WHITEOAK_T (11796) CKT 1 | L_001695MOSES_5-001697SULSP_SS1_5C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 110.2475 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_E_T8 ( 1797) -> MRTNSPG1_8 ( 1800) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 116.4349 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_E_T8 ( 1797) -> MRTNSPG1_8 ( 1800) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 108.8166 | 126.444 | 107.8189 | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | ALLEN SW - MONTICELLO 345 KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.33 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 111.1886 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.1098 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.2808 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | ALLEN-MOSES 345-138 AUTO-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.185 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | ALLEN-MOSES 345-138 AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 110.8778 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 110.8311 | 126.5359 | 110.36 | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | L_001685FARMVLSW_5-011689CYCLONE_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 106.2307 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | L_001685FARMVLSW_5-011700SALTILLO_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.8134 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.33 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 111.042 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | L_001696MOSES1_T5-888854PINEFOREST_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.33 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | L_011684BRIGHTR_5-011689CYCLONE_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.0569 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 111.042 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | PARIS SW-PACIFIC SW/VALLEY S SW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.2729 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | PINEFOREST_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 103.901 | - | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 118.6154 | 140.6379 | 120.1358 | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 112.1157 | 133.8124 | 113.8061 | -
TONCOR | EAST | EAST | EAST, EAST | SULSP_SS1_5 ( 1697) -> CARTWHEEL_POI (888847) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 117.4687 | 102.8426 | -
TONCOR | WEST | WEST | WEST, WEST | SUN_8 ( 1064) -> ONC900084_TAP ( 1289) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 778.1677 | - | 134.6238 | - | - | - | - | -
TLCRA,TONCOR | WEST | WEST | WEST, WEST | SWEETEAST_5 (11420) -> L_BITTCR5_1Y (71050) CKT 1 | New SweetEAST - Meinan 138kV | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.113 | - | -
TLCRA,TONCOR | WEST | WEST | WEST, WEST | SWEETEAST_5 (11420) -> L_BITTCR5_1Y (71050) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 111.7044 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SWIMMER ( 543) -> ZIONHILL ( 516) CKT 1 | BEPC_242 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 116.6947 | 110.4591 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SWIMMER ( 543) -> ZIONHILL ( 516) CKT 1 | BEPC_283_1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.4014 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SWIMMER ( 543) -> ZIONHILL ( 516) CKT 1 | L_000541RENO-000595KEETERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 115.0443 | 108.7354 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SWIMMER ( 543) -> ZIONHILL ( 516) CKT 1 | L_000571HIDEOUT-000579JCKCNTY8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 100.3892 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SWIMMER ( 543) -> ZIONHILL ( 516) CKT 1 | L_000579JCKCNTY8-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.1376 | 110.7659 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SWIMMER ( 543) -> ZIONHILL ( 516) CKT 1 | L_000595KEETER-000596COTTONDALEC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 115.8011 | 109.471 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | SWIMMER ( 543) -> ZIONHILL ( 516) CKT 1 | L_000596COTTONDALE-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.1288 | 110.757 | -
TONCOR | WEST | WEST | WEST, WEST | SWTRDTAP_8 ( 1341) -> LORAINES_8 (11342) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 748.8818 | - | 164.9314 | - | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | 3WT_076000L_NORTMC5_1Y_076595L_NORTMC8_2Y_076998L_NORTMC2_2Y C 2 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 103.5421 | - | 103.7738 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | 3WT_076000L_NORTMC5_1Y_076595L_NORTMC8_2Y_076999L_NORTMC2_1Y C 1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 103.5421 | - | 103.7738 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | BAS_RANCH_CON | 69 | 69 | Branch Amp | 317.961 | - | - | - | 107.4754 | - | 101.6458 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | Cattleman-Longshore 2 345 kV ONCOR WTIP RPG Submittal | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.7738 | - | 100.2011 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | Cattleman-Longshore Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 69 | 69 | Branch Amp | 317.961 | - | - | - | 105.9334 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | E_OECCS_CC1_TRAIN | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.1467 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | E_OECCS_CC2_TRAIN | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.1624 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | E5DVA1C1_1_B | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5271 | - | 100.0004 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | E5DVA1C1_1_B_1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0658 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | FALCON SOUTH - RANGER CAMP 345 KV SUM 2027 - FUTURE(DOUBLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6077 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | G_010012METEOR_5US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.8872 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | G_060716SGSA4AUS1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5324 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | G_132431SIRIUS_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5625 | - | 100.2828 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | G_132481RIGGINS_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0372 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | G_132781CASLGP_UNIT1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6799 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | G_132941SPTX12B_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4258 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | G_134751FOWLR_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.3921 | - | 100.0383 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | G_135731APPALOSA_W1UW1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6046 | - | 100.5775 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | G_136101BLUESKY_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 108.3398 | - | 108.2316 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | G_136341TRBNT_PV_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.3437 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | G_182151EGROVESL_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0432 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | G_183621ZIER_S1US1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.5026 | - | 101.4214 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | G_888839BAS_RANCH_POIUC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 107.2899 | - | 101.6708 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | G_888851TRIFECTA_POIUN1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1007 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.6701 | - | 101.2593 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | IRON_BELT_CON | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.969 | - | 100.1341 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_000842GPL_KINGMTSW-000843GPL_KINGMTTPC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.0471 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_000842GPL_KINGMTSW-076000L_NORTMC5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.7024 | - | 100.0461 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.7254 | - | 100.3257 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_000844GPL_NEVILLSW-076000L_NORTMC5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 104.768 | - | 104.7477 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_000844GPL_NEVILLSW-076002L_BAKERS5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.816 | - | 102.3967 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_000860GPL_GIRVINSW-136341TRBNT_PV_S1C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.3439 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_001009YUCCADR_8-011245RIVERVIEW_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.892 | - | 100.524 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_001058LONGSHORE_5-010053CATTLEMEN_5C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.7738 | - | 100.2011 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_001058LONGSHORE_5-010053CATTLEMEN_5C2 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.7738 | - | 100.2011 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.8922 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006015MADDUX4A-006490SANTIAGO4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.8584 | - | 102.6179 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006036YUCCA4A-006525ESMERALD4AC1 | 69 | 69 | Branch Amp | 317.961 | 116.8438 | - | 146.39 | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006036YUCCA4A-060360CASSAVA4AC1 | 69 | 69 | Branch Amp | 317.961 | 100.5815 | - | 122.9006 | 140.8699 | - | 151.1245 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006365YELWJCKT4B-060423TREADWEL4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6316 | - | 100.6768 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006435STER2A-006641CAMPELIZ2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0225 | - | 100.0705 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006444REDCREEK7A-076009L_TWINBU5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.7102 | - | 100.3531 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006490SANTIAGO4A-006500LVOK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 106.2253 | - | 106.1743 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006500LVOK4A-060412CARVER4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 110.0294 | - | 109.6375 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006511ATSO2A-006513SONR2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0962 | - | 100.0985 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006517RUSSEKST4A-006535BIGLAKE4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.1777 | 115.4319 | - | 114.0391 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006517RUSSEKST4A-006559JERRY4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 102.6108 | 117.5061 | - | 116.3013 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006525ESMERALD4A-006562FDRAN4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 111.9156 | 127.5271 | - | 131.4748 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006530BARNHRT2A-006534BIGLAKE2BC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 109.9036 | - | 110.4757 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006535BIGLAKE4A-060375WOLFBERR2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 105.394 | - | 105.8627 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006536BIGLAKE4B-060414OWLS4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 110.0066 | - | 110.2786 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006559JERRY4A-060374PUMPJACK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 106.5088 | 123.0487 | - | 122.0024 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006562FDRAN4A-060412CARVER4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.0182 | 108.2083 | - | 108.6978 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006562FDRAN4A-136103BLUESKY_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 108.4048 | - | 108.2987 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006564ILLN4A-060389CORRAL4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5668 | - | 100.551 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006586MCCAMY4-076001L_TIPPET8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.7178 | - | 100.8207 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006586MCCAMY4-076032L_NORTMC8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.719 | - | 100.8237 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006601RIOPECOS4A-076601L_HORSCR8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0417 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006630FTST4A-132482RIGGINS_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0379 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006648HARGROVE4A-060374PUMPJACK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 109.9606 | 127.9634 | - | 126.9235 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_006648HARGROVE4A-076011L_TWINBU8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 111.5777 | 130.2346 | - | 129.1837 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_007389L_PINNAC8_1Y-135019TI_SOLAR_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0232 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_008255HAMILTON4A-008680ROUGHCAN4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.8357 | - | 100.8502 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_008255HAMILTON4A-078255L_PINTCR8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.5641 | - | 101.6186 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_008261WHITING4A-008998MAXWELL4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5977 | - | 100.7326 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_008680ROUGHCAN4A-008683COMSTOCK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6788 | - | 100.6941 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_008683COMSTOCK4A-060389CORRAL4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5551 | - | 100.5452 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_008728COBRA7A-081003HABER7AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0001 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_010053CATTLEMEN_5-076030L_GASCCR5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.3177 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_011245RIVERVIEW_8-900064Other_134C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.8055 | - | 100.4418 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_011270DOGHOUSE_5-023876CLEARFRK_5C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.2218 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_038340TNAIRPORT41-038355TNLEONCRK_1C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5369 | - | 100.7129 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_059900LONG_DRAW-888842IRON_BELT_POIC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6436 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_059902SAND_BLUFF-059907BERNOULLIC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.9029 | - | 101.5969 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_059902SAND_BLUFF-076090L_DIVIDE5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6019 | - | 100.0081 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_059903BEARKAT-059907BERNOULLIC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.6269 | - | 101.9834 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_060361SANTARIT4A-060414OWLS4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.3084 | 120.6985 | - | 122.7479 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_060361SANTARIT4A-060799WOLFCAMP4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 102.3652 | 122.0555 | - | 124.239 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_060392LOTEBUSH4A-060415BASIN4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1722 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_060393PIGCREEK4A-134245TAYGETE_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4952 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_060393PIGCREEK4A-134705TYGTEII_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1729 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_060397GASPADTA4A-060415BASIN4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.2182 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_060397GASPADTA4A-900064Other_134C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.7508 | - | 100.3951 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_060411BURMA2A-061017GOLOID2AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0378 | - | 100.0517 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_060723CROSSOVE4A-060728PALOUSE4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 113.0696 | - | 114.8785 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_060723CROSSOVE4A-076032L_NORTMC8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 113.1454 | - | 114.9813 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_060728PALOUSE4A-060799WOLFCAMP4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | 103.593 | 123.6769 | - | 126.0304 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_060728PALOUSE4A-135734APPALOSA_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.8257 | - | 100.7511 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_076001L_TIPPET8_1Y-076013L_WESTYA8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.064 | - | 100.1585 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_076002L_BAKERS5_1Y-135327REDBARN_5C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0007 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_076003L_BIGHIL5_1Y-076009L_TWINBU5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.7735 | - | 100.6373 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_076011L_TWINBU8_1Y-900117Other_90_SOC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 109.2482 | - | 109.1764 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_076030L_GASCCR5_1Y-076090L_DIVIDE5_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1611 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_076032L_NORTMC8_1Y-900113Other_81_SOC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 105.2004 | - | 105.6754 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_076040L_CASTIL8_1Y-132783CASL_GAP_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.7093 | - | 100.0074 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_076040L_CASTIL8_1Y-132943SPTX12B_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4995 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_076601L_HORSCR8_1Y-182154EGROVESL_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0432 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_078255L_PINTCR8_1Y-183623ZIER_8C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.6971 | - | 101.6089 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_078280L_BEVO__8_1Y-078281L_DIMMIT8_1YC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.3447 | - | 100.4372 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_888839BAS_RANCH_POI-011098SANDLAKE_5C1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4423 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_888842IRON_BELT_POI-059910VOLTAC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.9497 | - | 100.1956 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_888856HOLLY_POI-059900LONG_DRAWC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.3571 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_900052Other_115-900110Other_86_MOC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.722 | - | 100.3532 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_900062Other_118-900113Other_81_SOC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.5959 | - | 103.6567 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L_900110Other_86_MO-900117Other_90_SOC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 107.6595 | - | 107.601 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L10010095 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4341 | - | 100.4124 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L10010116 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 103.0757 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L2020500-1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.0641 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L2020510-A-1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1054 | - | 100.1207 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L2020900 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6315 | - | 100.6768 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L2020925 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.5948 | 115.8393 | - | 114.5023 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L2020933-B | 69 | 69 | Branch Amp | 317.961 | - | - | - | 105.0361 | - | 105.0024 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L2020944-A | 69 | 69 | Branch Amp | 317.961 | - | - | 102.2926 | 121.9859 | - | 124.1778 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L2020944-B | 69 | 69 | Branch Amp | 317.961 | - | - | - | 113.0652 | - | 114.8736 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | L2021632 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1535 | - | 100.3759 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LCRA TSC_BAKERS_CEDACA_DC | 69 | 69 | Branch Amp | 317.961 | - | - | - | 105.9883 | - | 101.7192 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-1 | 69 | 69 | Branch Amp | 317.961 | - | - | 102.2467 | 104.0593 | - | 100.8026 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1A-2 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.2135 | 103.2607 | - | 100.4299 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-1 | 69 | 69 | Branch Amp | 317.961 | - | - | 102.2466 | 104.0592 | - | 100.8025 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LCRA TSC_CEDACA_NOELKE_DC_1B-2 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.2134 | 103.2606 | - | 100.4298 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LCRA TSC_NOELK_SNGTR_NOELK_SNGTR2 | 69 | 69 | Branch Amp | 317.961 | - | - | 100.8117 | 102.992 | - | 100.3206 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LCRA TSC_SNGTR_SCHDR_SNGTR_SCHDR2 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 102.806 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LCRA TSC_T422_T550 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.922 | - | 100.5744 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LCRA TSC_T423_T551_A | 69 | 69 | Branch Amp | 317.961 | - | - | - | 104.5517 | - | 103.3878 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LCRA TSC_T429_T9426 | 69 | 69 | Branch Amp | 317.961 | - | - | 110.7725 | 128.3888 | - | 127.325 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LCRA TSC_T443_T554 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5436 | - | 100.6753 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LCRA TSC_T451_T682 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.9149 | - | 100.5471 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LCRA TSC_T454_T484 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.1072 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LCRA TSC_T464_1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 103.0339 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LCRA TSC_T552_T554 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.5423 | - | 100.6722 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE (DOUBLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 104.32 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | LONGSHORE - CATTLEMEN SUM 2027 - FUTURE CKT 1 (SINGLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.7738 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | M2100120997-2 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6445 | - | 100.6906 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | MB2090020948 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6549 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | MB2092520930 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 116.2245 | - | 115.055 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | MB2093020925 | 69 | 69 | Branch Amp | 317.961 | - | - | 102.2466 | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | MB2094820900 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.7004 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | MB2095120950 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.8986 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | MB2552825529 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | - | 100.4153 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | MB2726627277 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.8421 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | MOSS - HOLT/YUCCA 138 KV/MIDLAND COUNTY NW SW 345 KV (DOUBLE B TO B) SUM 2025- FUTURE | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.1015 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | New Meinan - Sweeteast and BitterCreek 345kV Double | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.5431 | - | 100.8801 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | New Sweeteast - Meinan and BitterCreek 345kV Double | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.9898 | - | 100.4903 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | ODESSA EHV - NORTH MCCAMEY 345 KV (SINGLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.8326 | - | 100.2007 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | P7-WETT-7 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.2758 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.8289 | - | 100.7045 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | Rockhound-Prong Moss Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.326 | - | 100.0794 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | STECL_10592 | 69 | 69 | Branch Amp | 317.961 | - | - | 104.7785 | - | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | STECL_4720 | 69 | 69 | Branch Amp | 317.961 | - | - | 100.6543 | 102.7729 | - | 100.2491 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | STECL_4721-1 | 69 | 69 | Branch Amp | 317.961 | - | - | 102.2468 | 104.0594 | - | 100.8027 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | STECL_4721-2 | 69 | 69 | Branch Amp | 317.961 | - | - | 101.2136 | 103.2608 | - | 100.43 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | SWEETWATER EAST - CENTRAL BLUFF CKT 1 & SWEETWATER EAST - CENTRAL BLUFF CKT 2 345 KV (DOUBLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.4812 | - | 100.2553 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | T_006364YELWJCKT4A-006365YELWJCKT4BC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6314 | - | 100.6765 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | T_006533BIGLAKE2A-006535BIGLAKE4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.8995 | - | 100.5045 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | T_006534BIGLAKE2B-006535BIGLAKE4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.762 | - | 100.3896 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | T_006535BIGLAKE4A-006536BIGLAKE4BC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 108.5126 | - | 108.8588 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | T_060359CASSAVA2A-060360CASSAVA4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 108.8686 | - | 112.0801 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | TRIFECTA_CON | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.0907 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | WETT LONG DRAW - WETT VOLTA 345 KV LINE (SINGLE B TO B)-1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.6435 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | WETT LONG DRAW - WETT VOLTA 345 KV LINE (SINGLE B TO B)-2 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 100.9497 | - | 100.1956 | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A ( 6528) -> MERT2A ( 6529) CKT 1 | WOLF - METEOR/REITER 345 KV 2026 SUM - FUTURE (DOUBLE B TO B) | 69 | 69 | Branch Amp | 317.961 | - | - | - | 101.1262 | - | - | -
TAEPTN | WEST | WEST | WEST, WEST | TANK2A (6528) -> MERT2A (6529) CKT 1 | Pre-contingency | 69 | 69 | Amps | 317.961 | - | - | - | - | 112.0788 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMP_PEC__5 ( 3412) -> TEMP_STR (500118) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | 104.9343 | 112.7629 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMP_SE1_8 ( 3612) -> SCOTWHIT_T_8 ( 3602) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1380.62 | - | - | - | 101.4107 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMP_SE1_8 ( 3612) -> SCOTWHIT_T_8 ( 3602) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1380.62 | - | - | - | - | 112.1786 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMP_SE1_8 ( 3612) -> SCOTWHIT_T_8 ( 3602) CKT 1 | TEMPLE ELM CREEK SWITCH - PASCA RISE (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1380.62 | - | - | - | - | 115.0787 | 101.236 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMP_SS__5 ( 3414) -> TEMP_STR (500120) CKT 1 | 3WT_003412TEMP_PEC__5_003420TEMP_PEC__8_013420TEMP_PEC__3 C 1 | 345 | 1 | Branch MVA | 741 | - | - | - | - | 100.2586 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMP_SS__5 ( 3414) -> TEMP_STR (500120) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 345 | 1 | Branch MVA | 741 | - | - | - | 104.5915 | 150.1728 | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMP_SS__8 ( 3415) -> BELLCNTY8 ( 132) CKT 1 | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1317.8646 | - | - | 113.0495 | - | - | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMP_SS__8 ( 3415) -> BELLCNTY8 ( 132) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | 103.671 | - | - | - | -
TONCOR,TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMP_SS__8 ( 3415) -> BELLCNTY8 ( 132) CKT 1 | L_003666HUTTOSS1_8-003667RNDRCKNE2_8C1 | 138 | 138 | Branch Amp | 1317.8646 | - | - | 101.3023 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMP_SS__8 ( 3415) -> TEMP_SE1_8 ( 3612) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1380.62 | - | - | - | 101.1544 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMP_SS__8 ( 3415) -> TEMP_SE1_8 ( 3612) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1380.62 | - | - | - | 110.2962 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMP_SS__8 ( 3415) -> TEMP_SE1_8 ( 3612) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1380.62 | - | - | - | - | 121.5225 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMP_SS__8 ( 3415) -> TEMP_SE1_8 ( 3612) CKT 1 | TEMPLE ELM CREEK SWITCH - PASCA RISE (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1380.62 | - | - | - | 108.5832 | 124.0182 | 110.2013 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMP_STR (500118) -> TEMP_PEC__8 ( 3420) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 1 | Branch MVA | 750 | - | - | - | 104.5408 | 112.7629 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMP_STR (500120) -> TEMP_SS_R_8 (13415) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 1 | Branch MVA | 741 | - | - | - | 100.6543 | 135.6176 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPELMC__8 (13662) -> TEMPLE_N1_8 ( 3608) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 112.5432 | - | 108.4305 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPELMC__8 (13662) -> TEMPLE_N1_8 ( 3608) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 115.9407 | - | 111.4469 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPELMC__8 (13662) -> TEMPLE_N1_8 ( 3608) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 110.5493 | 136.4417 | 106.7047 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPELMC__8 (13662) -> TEMPLE_N1_8 ( 3608) CKT 1 | L_003484PEPPERCRK_8-013608TEMPLE_N2_8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 113.0935 | 128.6096 | 118.8437 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPELMC__8 (13662) -> TEMPLE_N1_8 ( 3608) CKT 1 | L_013608TEMPLE_N2_8-013662TEMPELMC__8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 115.7707 | 131.3353 | 121.5676 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPELMC__8 (13662) -> TEMPLE_N1_8 ( 3608) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 101.8109 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPELMC__8 (13662) -> TEMPLE_N1_8 ( 3608) CKT 1 | TEMPLE ELM CREEK SWITCH - PASCA RISE CKT 2 (SINGLE B TO B ) | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 113.7464 | 129.2677 | 119.4968 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPELMC__8 (13662) -> TEMPLE_N2_8 (13608) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 105.5808 | - | 101.4023 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPELMC__8 (13662) -> TEMPLE_N2_8 (13608) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 108.9702 | - | 104.4107 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPELMC__8 (13662) -> TEMPLE_N2_8 (13608) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 103.5859 | 129.1406 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPELMC__8 (13662) -> TEMPLE_N2_8 (13608) CKT 1 | L_003484PEPPERCRK_8-003608TEMPLE_N1_8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 105.144 | 120.4788 | 110.7061 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPELMC__8 (13662) -> TEMPLE_N2_8 (13608) CKT 1 | L_003608TEMPLE_N1_8-013662TEMPELMC__8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 114.4364 | 129.9731 | 120.2156 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPELMC__8 (13662) -> TEMPLE_N2_8 (13608) CKT 1 | TEMPLE ELM CREEK SWITCH - PASCA RISE CKT1 (SINGLE B TO B) | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 107.4003 | 122.7757 | 112.9758 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPLE_N1_8 ( 3608) -> PEPPERCRK_8 ( 3484) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1363.8853 | - | - | - | 100.1488 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPLE_N1_8 ( 3608) -> PEPPERCRK_8 ( 3484) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1363.8853 | - | - | - | - | 119.3568 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPLE_N1_8 ( 3608) -> PEPPERCRK_8 ( 3484) CKT 1 | L_003484PEPPERCRK_8-013608TEMPLE_N2_8C1 | 138 | 138 | Branch Amp | 1363.8853 | - | - | - | - | 112.5115 | 103.0998 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPLE_N1_8 ( 3608) -> PEPPERCRK_8 ( 3484) CKT 1 | L_013608TEMPLE_N2_8-013662TEMPELMC__8C1 | 138 | 138 | Branch Amp | 1363.8853 | - | - | - | 100.3651 | 115.1176 | 105.7066 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPLE_N1_8 ( 3608) -> PEPPERCRK_8 ( 3484) CKT 1 | TEMPLE ELM CREEK SWITCH - PASCA RISE CKT 2 (SINGLE B TO B ) | 138 | 138 | Branch Amp | 1363.8853 | - | - | - | - | 113.1442 | 103.7283 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPLE_N2_8 (13608) -> PEPPERCRK_8 ( 3484) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1363.8853 | - | - | - | 101.6721 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPLE_N2_8 (13608) -> PEPPERCRK_8 ( 3484) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1363.8853 | - | - | - | - | 120.9533 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPLE_N2_8 (13608) -> PEPPERCRK_8 ( 3484) CKT 1 | L_003484PEPPERCRK_8-003608TEMPLE_N1_8C1 | 138 | 138 | Branch Amp | 1363.8853 | - | - | - | - | 112.7982 | 103.3878 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPLE_N2_8 (13608) -> PEPPERCRK_8 ( 3484) CKT 1 | L_003608TEMPLE_N1_8-013662TEMPELMC__8C1 | 138 | 138 | Branch Amp | 1363.8853 | - | - | - | 107.0166 | 121.9231 | 112.5297 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPLE_N2_8 (13608) -> PEPPERCRK_8 ( 3484) CKT 1 | TEMPLE ELM CREEK SWITCH - PASCA RISE CKT1 (SINGLE B TO B) | 138 | 138 | Branch Amp | 1363.8853 | - | - | - | 100.2616 | 115.0097 | 105.5738 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPTAYV1_9 ( 3636) -> BELLCNTY9 ( 133) CKT 1 | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 69 | 69 | Branch Amp | 861.8416 | - | - | - | 108.1581 | - | 103.0786 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TEMPTAYV1_9 ( 3636) -> BELLCNTY9 ( 133) CKT 1 | TEMP_SS__5-KNOBCRK_SS_5 & TEMP_SS__8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | 69 | 69 | Branch Amp | 861.8416 | - | - | - | - | 105.2729 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TENMIL2_8 ( 2144) -> GREENRD_8 ( 3069) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1648.3767 | - | - | - | 105.5232 | 127.5776 | 132.5853 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TENMIL2_8 ( 2144) -> GREENRD_8 ( 3069) CKT 1 | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1648.3767 | - | - | - | - | - | 106.7092 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TENMILE_8 ( 2126) -> GREENRD_8 ( 3069) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1280.2113 | - | - | - | 141.4372 | 170.9944 | 177.73 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TENMILE_8 ( 2126) -> GREENRD_8 ( 3069) CKT 1 | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1280.2113 | - | - | - | 113.1038 | 131.901 | 143.106 | -
TONCOR | EAST | EAST | EAST, EAST | THORNTRE_5 (11688) -> SALTILLO_5 (11700) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 106.7917 | - | -
TONCOR | EAST | EAST | EAST, EAST | THORNTRE_5 (11688) -> SALTILLO_5 (11700) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.4822 | - | -
TONCOR | EAST | EAST | EAST, EAST | THORNTRE_5 (11688) -> SALTILLO_5 (11700) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 106.0207 | - | -
TONCOR | EAST | EAST | EAST, EAST | THORNTRE_5 (11688) -> SALTILLO_5 (11700) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 115.3664 | - | -
TONCOR | EAST | EAST | EAST, EAST | THORNTRE_5 (11688) -> SALTILLO_5 (11700) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 106.9018 | - | -
TONCOR | EAST | EAST | EAST, EAST | THORNTRE_5 (11688) -> SALTILLO_5 (11700) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 116.2631 | - | -
TONCOR | EAST | EAST | EAST, EAST | THORNTRE_5 (11688) -> SALTILLO_5 (11700) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.8028 | - | -
TONCOR | EAST | EAST | EAST, EAST | THORNTRE_5 (11688) -> SALTILLO_5 (11700) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 113.9644 | - | -
TONCOR | EAST | EAST | EAST, EAST | THORNTRE_5 (11688) -> SALTILLO_5 (11700) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.6902 | - | -
TONCOR | EAST | EAST | EAST, EAST | THORNTRE_5 (11688) -> SALTILLO_5 (11700) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 114.8514 | - | -
TONCOR | EAST | EAST | EAST, EAST | THORNTRE_5 (11688) -> SALTILLO_5 (11700) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 116.3835 | - | -
TONCOR | EAST | EAST | EAST, EAST | THORNTRE_5 (11688) -> SALTILLO_5 (11700) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 105.9714 | 127.0232 | 106.5708 | -
TONCOR | EAST | EAST | EAST, EAST | THORNTRE_5 (11688) -> SALTILLO_5 (11700) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 110.7882 | - | -
TONCOR | EAST | EAST | EAST, EAST | THORNTRE_5 (11688) -> SALTILLO_5 (11700) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 100.9442 | 120.6142 | 101.5584 | -
TONCOR | EAST | EAST | EAST, EAST | THORNTRE_5 (11688) -> SALTILLO_5 (11700) CKT 1 | L_001685FARMVLSW_5-011689CYCLONE_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 101.1447 | - | -
TONCOR,TLSTR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THOUSE__5 ( 3405) -> FOURBTHRS_5 ( 3388) CKT 1 | L_013401TIGERCK_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.2074 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 100.4135 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | 3WT_003522HILLBORO1_8_003523HILLBORO1_9_003519HILLBORO1_3 C 1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 106.8861 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | CARMICHAEL BEND-TIMBERVIEW 345 KV*DECORDOVA-CLEBURNE 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 102.4516 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | CLEBURNE-DECORDOVA 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 101.0438 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | G_154011MIDPOINT_S1US1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 109.2106 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | L_002279CLEBRNSW_8-002280CLEBRN_N_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 101.2358 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | L_002280CLEBRN_N_8-002283AIRLIQD_P8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 105.2255 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | L_002281GODLEY_8-002283AIRLIQD_P8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.3196 | - | 106.5402 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | L_002281GODLEY_8-002888CARMICHL_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.3872 | - | 106.6077 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 101.1267 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 101.1199 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 100.9798 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 116.2657 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 112.9919 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | - | 102.7636 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 108.5704 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 100.6402 | - | 104.7239 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | THRESLR_POI (888875) -> BLANTON ( 237) CKT 1 | VENUS-JOHNSON 345KV/DECORDOVA-CLEBURNE 138KV (DOUBLE B TO B) new load | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 105.4017 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIGERCK_5 (13401) -> SAMSW (68090) CKT 1 | L_003388FOURBTHRS_5-003405THOUSE__5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 106.9276 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIGERCK_5 (13401) -> SAMSW (68090) CKT 1 | L_003388FOURBTHRS_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 115.0557 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIGERCK_5 (13401) -> SAMSW (68090) CKT 1 | LAKE CREEK - LAKE HALL_5 (SINGLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.6759 | - | -
TLSTR,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIGERCK_5 (13401) -> SAMSW (68090) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | 101.4934 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 118.9459 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 113.5002 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | BEPC_015_2 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 101.3576 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 104.4246 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 101.7646 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 103.3426 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | GLASGOW_CON | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 103.5562 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 115.2547 | 121.2643 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 117.3966 | 123.5657 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 118.5955 | 124.755 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 101.0457 | 105.8618 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | L_001921LIGGETTA1_5-002632MILLERRD_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 100.5688 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | L_001928LIGGETT_3T5-002406NORWD1_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 101.8321 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 104.4246 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 103.3426 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 103.3448 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 103.0918 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 102.1215 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 106.3711 | 109.9138 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | LIGGETT-NORWOOD 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 101.5947 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 107.4673 | 112.2262 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 107.3018 | 112.0174 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | NORWOOD-LIGGETT 345 & MOUNTAIN CREEK - LIGGETT 138 KV DCKT A BLUBONT | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 101.5011 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV DCKT & EAGLE MOUNTAIN - WEATHERFORD 138 KV LINE | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 100.0601 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | SHERRY-TIMBERVIEW*VENUS 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 101.2707 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 102.2147 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 101.127 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 116.2735 | 122.5553 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 110.5372 | 115.7805 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | Venus SW - MillerRoad 345 KV (SINGLE B TO B) New Load | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 101.0457 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 115.552 | 122.0128 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 114.6269 | 120.8463 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 115.9496 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 113.4714 | 119.9709 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TIMBERVW_5 (11886) -> COURTLND1_5 ( 1931) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 115.4531 | 121.4139 | - | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TN16TH_ST_0 (38320) -> TN16TH_ST_1 (38310) CKT 1 | Pre-contingency | 69 | 138 | MVA | 62.5 | - | - | 104.0329 | 130.3443 | 142.6115 | 146.8177 | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TN16TH_ST_0 (38320) -> TNFTSTCKTN0 (38360) CKT 1 | Pre-contingency | 69 | 69 | Amps | 242.6544 | 179.2689 | 127.9949 | 215.7047 | 255.8433 | 278.6146 | 312.7601 | -
TTNMP | NORTH | NORTH | NORTH, NORTH | TNBELLS___0 (37140) -> TNWHITEWRT0 (37160) CKT 1 | L_037245BRDG_RC-037280TNCLIMAX__0C1 | 69 | 69 | Branch Amp | 357.2877 | 121.9116 | - | 145.9055 | - | - | - | -
TTNMP | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TNBLUERDGE0 (37240) -> BRDG_RC (37245) CKT 1 | L_037245BRDG_RC-037280TNCLIMAX__0C1 | 69 | 69 | Branch Amp | 301.2262 | - | - | 117.343 | - | - | - | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNCEDRVALE1 (38145) -> TNBCTRESTL1 (38146) CKT 1 | BAS_RANCH_CON | 138 | 138 | Branch Amp | 2999.7109 | - | - | - | - | 100.4292 | - | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNCEDRVALE1 (38145) -> TNBCTRESTL1 (38146) CKT 1 | G_888839BAS_RANCH_POIUC1 | 138 | 138 | Branch Amp | 2999.7109 | - | - | - | - | 100.4403 | - | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNCEDRVALE1 (38145) -> TNBCTRESTL1 (38146) CKT 1 | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 138 | 138 | Branch Amp | 2999.7109 | - | - | - | - | 100.0069 | - | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNCEDRVALE1 (38145) -> TNBCTRESTL1 (38146) CKT 1 | L_011080THRMIDRW_8-011083RIVERTON_8C1 | 138 | 138 | Branch Amp | 2999.7109 | - | - | - | - | 100.0141 | - | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNCEDRVALE1 (38145) -> TNBCTRESTL1 (38146) CKT 1 | L_011182MCLLVAIN_8-011377AQUIFER_8C1 | 138 | 138 | Branch Amp | 2999.7109 | - | - | - | - | 100.0676 | - | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNCEDRVALE1 (38145) -> TNBCTRESTL1 (38146) CKT 1 | P1.2_M138H-A4 | 138 | 138 | Branch Amp | 2999.7109 | - | - | - | - | 100.1902 | - | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNCEDRVALE1 (38145) -> TNBCTRESTL1 (38146) CKT 1 | P7.1_T-WT-138J-138K | 138 | 138 | Branch Amp | 2999.7109 | - | - | - | - | 100.1235 | - | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNCEDRVALE1 (38145) -> TNBCTRESTL1 (38146) CKT 1 | Pre-contingency | 138 | 138 | Amps | 2999.7109 | - | - | 101.2505 | - | - | - | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNCEDRVALE1 (38145) -> TNBCTRESTL1 (38146) CKT 1 | RIVERTON - THREE MILE DRAW/HORSESHOE SPRINGS DCKT 138 KV SUM 2022 - FUTURE (DOUBLE B TO B) C | 138 | 138 | Branch Amp | 2999.7109 | - | - | - | - | 100.1719 | - | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNCEDRVALE1 (38145) -> TNBCTRESTL1 (38146) CKT 1 | S_038145TNCEDRVALE11 | 138 | 138 | Branch Amp | 2999.7109 | - | - | - | 101.7089 | 100.1768 | 101.5693 | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNCEDRVALE1 (38145) -> TNBCTRESTL1 (38146) CKT 1 | S_038190TNLONESTAR11 | 138 | 138 | Branch Amp | 2999.7109 | - | - | - | - | 100.0755 | - | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNCEDRVALE1 (38145) -> TNBCTRESTL1 (38146) CKT 1 | SAND LAKE - SOLSTICE 345 KV DCKT LINE (DOUBLE B TO B) WIN 2027 - FUTURE | 138 | 138 | Branch Amp | 2999.7109 | - | - | - | 100.2594 | 100.822 | - | -
TTNMP | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TNCLIMAX__0 (37280) -> BRDG_RC (37245) CKT 1 | L_037140TNBELLS___0-037160TNWHITEWRT0C1 | 69 | 69 | Branch Amp | 301.2262 | 103.4066 | - | 109.1045 | 120.0458 | 125.9364 | 126.5398 | -
TTNMP | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TNCLIMAX__0 (37280) -> BRDG_RC (37245) CKT 1 | L_037160TNWHITEWRT0-037180TNFRNTRTAP0C1 | 69 | 69 | Branch Amp | 301.2262 | 100.829 | - | 106.3098 | 117.1536 | 122.8394 | 123.5527 | -
TTNMP | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TNCLIMAX__0 (37280) -> BRDG_RC (37245) CKT 1 | L_037180TNFRNTRTAP0-037200TNTRENTON_0C1 | 69 | 69 | Branch Amp | 301.2262 | - | - | - | 110.4118 | 116.0454 | 116.6656 | -
TTNMP | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TNCLIMAX__0 (37280) -> BRDG_RC (37245) CKT 1 | L_037200TNTRENTON_0-037220TNLEONARD_0C1 | 69 | 69 | Branch Amp | 301.2262 | - | - | - | 103.9038 | 109.5361 | 110.0423 | -
TTNMP | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TNCLIMAX__0 (37280) -> BRDG_RC (37245) CKT 1 | STONE CREEK SW-BONHAM SW 69 KV | 69 | 69 | Branch Amp | 301.2262 | 111.8724 | - | 117.717 | 127.4726 | 133.4463 | 134.0968 | -
TTNMP | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TNCLIMAX__0 (37280) -> BRDG_RC (37245) CKT 1 | STONE CREEK SW-BONHAM SW 69 KV & VALLEY -COMMERCE 138 KV LINE A | 69 | 69 | Branch Amp | 301.2262 | 111.8835 | - | 117.722 | 127.4976 | 133.5037 | 134.1041 | -
TTNMP | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TNCLIMAX__0 (37280) -> BRDG_RC (37245) CKT 1 | STONE CREEK SW-BONHAM SW 69 KV (SINGLE B TO B) | 69 | 69 | Branch Amp | 301.2262 | 103.2418 | - | 108.9354 | 119.867 | 125.7569 | 126.357 | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNCOLIYDT_1 (38036) -> TNCOLIET__1 (38037) CKT 1 | Pre-contingency | 138 | 138 | Amps | 1012.4547 | - | - | - | - | 105.4757 | 105.6058 | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNCOWPEN__1 (38043) -> TNBIRDOPT_1 (38027) CKT 1 | P1.2_M138I-1_2026-FUTURE | 138 | 138 | Branch Amp | 1711.1322 | - | - | - | - | 101.2552 | - | -
TTNMP | NORTH | NORTH | NORTH, NORTH | TNFRNTRTAP0 (37180) -> TNTRENTON_0 (37200) CKT 1 | L_037245BRDG_RC-037280TNCLIMAX__0C1 | 69 | 69 | Branch Amp | 359.798 | 113.6941 | - | 137.2158 | - | - | - | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNFTSTCKTN0 (38360) -> TNPINON___0 (38365) CKT 1 | Pre-contingency | 69 | 69 | Amps | 200.8175 | - | - | - | 126.5624 | 139.8924 | 162.2874 | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNGEMSBOKM1 (38107) -> TNGMSBKACC1 (38109) CKT 1 | L_001012PIRCOVE_8-011104BARKETT_P8C1 | 138 | 138 | Branch Amp | 732.147 | - | - | - | 101.4099 | 102.9319 | 101.4349 | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNJACKRBT1 (38095) -> TNREEVSCOT1 (38114) CKT 1 | New Shunt 900021 | 138 | 138 | Branch Amp | 1711.1322 | - | - | - | - | 108.6329 | 107.8514 | -
TTNMP | NORTH | NORTH_CE | NORTH, NORTH_CE | TNLEONARD_0 (37220) -> TNBLUERDGE0 (37240) CKT 1 | L_037245BRDG_RC-037280TNCLIMAX__0C1 | 69 | 69 | Branch Amp | 359.798 | - | - | 108.6414 | - | - | - | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNPECOS___1 (38091) -> TNJACKRBT1 (38095) CKT 1 | New Shunt 900021 | 138 | 138 | Branch Amp | 1711.1322 | - | - | - | - | 108.5632 | 107.7817 | -
TTNMP | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNREEVSCOT1 (38114) -> TNETOYAHT_1 (38117) CKT 1 | New Shunt 900021 | 138 | 138 | Branch Amp | 1711.1322 | - | - | - | - | 103.3552 | 102.5972 | -
TTNMP | NORTH | NORTH | NORTH, NORTH | TNTRENTON_0 (37200) -> TNLEONARD_0 (37220) CKT 1 | L_037245BRDG_RC-037280TNCLIMAX__0C1 | 69 | 69 | Branch Amp | 359.798 | 107.968 | - | 131.0918 | - | - | - | -
RSHER2 | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | TNWHITEBKR1 (38430) -> KEO_2_8 (131453) CKT 1 | L_131453KEO_2_8-131454KEO_3_8CS2 | 138 | 138 | Branch Amp | 2133.6855 | 101.4896 | - | 103.2176 | 102.9389 | 102.8455 | 102.4691 | -
TTNMP | NORTH | NORTH | NORTH, NORTH | TNWHITEWRT0 (37160) -> TNFRNTRTAP0 (37180) CKT 1 | L_037245BRDG_RC-037280TNCLIMAX__0C1 | 69 | 69 | Branch Amp | 359.798 | 119.324 | - | 143.195 | - | - | - | -
TONCOR | WEST | WEST | WEST, WEST | TONKAWAW_5 (11048) -> RANGER_5 (10049) CKT 1 | CATTLEMAN - CHAMPION CREEK & MORGAN CREEK SW - BITTER CREEK SW (LCRA) 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | 109.0963 | - | - | - | -
TONCOR | WEST | WEST | WEST, WEST | TONKAWAW_5 (11048) -> RANGER_5 (10049) CKT 1 | CATTLEMEN - RANGER CAMP 345 KV SUM 2026 - FUTURE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | 109.666 | - | - | - | - | -
TONCOR | WEST | WEST | WEST, WEST | TONKAWAW_5 (11048) -> RANGER_5 (10049) CKT 1 | New Cattleman - Meinan and Champion 345kV Double | 345 | 345 | Branch Amp | 1793.9694 | - | - | 108.4933 | - | - | - | -
TONCOR | WEST | WEST | WEST, WEST | TONKAWAW_5 (11048) -> RANGER_5 (10049) CKT 1 | New Meinan - Champion and Cattleman 345kV Double | 345 | 345 | Branch Amp | 1793.9694 | - | - | 106.9581 | - | - | - | -
TONCOR | WEST | WEST | WEST, WEST | TONKAWAW_5 (11048) -> RANGER_5 (10049) CKT 1 | New Meinan - Sweeteast and BitterCreek 345kV Double | 345 | 345 | Branch Amp | 1793.9694 | 119.3218 | 121.8373 | 136.0048 | - | - | - | -
TONCOR | WEST | WEST | WEST, WEST | TONKAWAW_5 (11048) -> RANGER_5 (10049) CKT 1 | New Sweeteast - Meinan and BitterCreek 345kV Double | 345 | 345 | Branch Amp | 1793.9694 | 110.8754 | 106.2154 | 127.6381 | - | - | - | -
TONCOR | WEST | WEST | WEST, WEST | TONKAWAW_5 (11048) -> RANGER_5 (10049) CKT 1 | SWEETWATER EAST - TONKAWA SW CKT 1 & SWEETWATER EAST - TONKAWA SW CKT 2 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | 110.0797 | - | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | TORTOISE_5 ( 3717) -> TORTOSTR (500128) CKT 1 | 3WT_003717TORTOISE_5_003713TOR_SR2_8_003715TORTOISE2_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | 103.3935 | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | TORTOISE_5 ( 3717) -> TORTOSTR (500128) CKT 1 | L_003712TORTOISE_8-003713TOR_SR2_8C2 | 345 | 1 | Branch MVA | 750 | - | - | - | 103.3935 | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | TORTOISE_5 ( 3717) -> TORTOSTR (500129) CKT 1 | 3WT_003717TORTOISE_5_003714TOR_SR1_8_003716TORTOISE_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | 103.3935 | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | TORTOISE_5 ( 3717) -> TORTOSTR (500129) CKT 1 | L_003712TORTOISE_8-003714TOR_SR1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | 103.3935 | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | TORTOISE_8 ( 3712) -> SAND_TXU_8 (13430) CKT 1 | L_003712TORTOISE_8-013430SAND_TXU_8C2 | 138 | 138 | Branch Amp | 3200.5283 | 104.253 | - | - | 110.4536 | - | - | -
TONCOR | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | TORTOISE_8 ( 3712) -> SAND_TXU_8 (13430) CKT 2 | L_003712TORTOISE_8-013430SAND_TXU_8C1 | 138 | 138 | Branch Amp | 3200.5283 | 104.253 | - | - | 110.4536 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TRICRN1_5 ( 2432) -> FRNY1_5 ( 2437) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1599.8458 | - | - | - | - | - | 131.933 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TRICRN1_5 ( 2432) -> FRNY1_5 ( 2437) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 1599.8458 | - | - | - | 128.6043 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TRICRN1_5 ( 2432) -> SGVLSW1_5 ( 2433) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2632.3821 | - | - | - | 100.3855 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TRICRN1_5 ( 2432) -> WATMLL_W5 ( 2427) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 345 | 345 | Branch Amp | 3199.6917 | - | - | 119.1666 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TRICRN1_5 ( 2432) -> WATMLL_W5 ( 2427) CKT 2 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 345 | 345 | Branch Amp | 3199.6917 | - | - | 119.1666 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRICRN1_5 (2432) -> TRINDAD1_5 (3123) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1725.3568 | - | - | - | 121.7116 | 142.0348 | 119.5439 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRICRN1_5 (2432) -> TRINDAD2_5 (3124) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1725.3568 | - | - | - | 131.1848 | 165.758 | 134.3578 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD1_5 ( 3123) -> TRICRN1_5 ( 2432) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | 114.2941 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD1_5 ( 3123) -> TRICRN1_5 ( 2432) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | 110.2765 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD1_5 ( 3123) -> TRICRN1_5 ( 2432) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | 106.2318 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD1_5 ( 3123) -> TRICRN1_5 ( 2432) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | 108.9374 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD1_5 ( 3123) -> TRICRN1_5 ( 2432) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | 105.5546 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD1_5 ( 3123) -> TRICRN1_5 ( 2432) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | 104.2215 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD1_5 ( 3123) -> TRICRN1_5 ( 2432) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | 106.9639 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD2_5 ( 3124) -> TRICRN1_5 ( 2432) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | 115.449 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD2_5 ( 3124) -> TRICRN1_5 ( 2432) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 1725.3568 | - | - | 111.5914 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD2_5 ( 3124) -> TRICRN1_5 ( 2432) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 345 | 345 | Branch Amp | 1725.3568 | - | - | 101.3294 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD2_5 ( 3124) -> TRICRN1_5 ( 2432) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | 101.1014 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD2_5 ( 3124) -> TRICRN1_5 ( 2432) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | 100.3008 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD2_5 ( 3124) -> TRICRN1_5 ( 2432) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | 106.5539 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD2_5 ( 3124) -> TRICRN1_5 ( 2432) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | 109.1291 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD2_5 ( 3124) -> TRICRN1_5 ( 2432) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | 107.847 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD2_5 ( 3124) -> TRICRN1_5 ( 2432) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | 345 | Branch Amp | 1725.3568 | - | - | 100.9222 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD2_5 ( 3124) -> TRICRN1_5 ( 2432) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | 103.7631 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD2_5 ( 3124) -> TRICRN1_5 ( 2432) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | 101.5441 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD2_5 ( 3124) -> TRICRN1_5 ( 2432) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | 106.2521 | - | - | - | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | TRINDAD2_5 ( 3124) -> TRICRN1_5 ( 2432) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 1725.3568 | - | - | 109.0962 | - | - | - | -
TONCOR | EAST | EAST | EAST, EAST | TRINDAD2_5 (3124) -> RICHLND1_5 (3134) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1725.3568 | - | - | - | - | 134.8296 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | 3WT_002433SGVLSW1_5_002434SGVLSW1_8_012434SGVLSW1_3 C 2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 101.7765 | - | 103.1091 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 110.561 | - | 105.6709 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 106.5729 | - | 104.1089 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 100.8098 | - | 102.9755 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 105.4141 | - | 106.7058 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | G_151371LILY_S1US1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 104.8722 | - | 106.0902 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 105.4143 | - | 106.5787 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 105.57 | - | 106.7245 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 104.3455 | - | 105.6728 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 104.0502 | - | 105.3978 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 122.7369 | - | 123.6392 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | - | 101.7835 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | L_006903BOZE-151372LILY_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 105.7159 | - | 106.9514 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 100.7921 | - | 100.8811 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 101.7321 | - | 101.741 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 102.5315 | - | 102.9289 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 103.4973 | - | 104.9736 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 109.2577 | - | 110.3612 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | SEAGOVILLE SW - FORNEY/TRICORNER DCKT 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 101.4555 | - | 103.1927 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 101.7862 | - | 101.9964 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 100.8746 | - | 101.7396 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | - | 100.8268 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 102.242 | - | 102.9056 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 103.4711 | - | 103.8371 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 ( 3127) -> NIPAKTAP_8 ( 3260) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 138 | 138 | Branch Amp | 1008.2711 | - | - | 102.3366 | 136.3421 | - | 134.0068 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TRINIDAD_8 (3127) -> NIPAKTAP_8 (3260) CKT 1 | Pre-contingency | 138 | 138 | Amps | 1008.271 | - | - | - | - | 105.1847 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TRUMBULL8 ( 221) -> PEBBLCRK_8 ( 2229) CKT 1 | ENNIS WEST - STERRETT 138 KV (SINGLE B TO B) A REAGOR SPRINGS | 138 | 138 | Branch Amp | 1004.0873 | - | - | 110.053 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TRUMBULL8 ( 221) -> PEBBLCRK_8 ( 2229) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 1004.0873 | - | - | 111.2206 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TRUMBULL8 ( 221) -> PEBBLCRK_8 ( 2229) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 1004.0873 | - | - | 109.054 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TRUMBULL8 ( 221) -> PEBBLCRK_8 ( 2229) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 1004.0873 | - | - | 101.5847 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TRUMBULL8 ( 221) -> PEBBLCRK_8 ( 2229) CKT 1 | WAXAHACHI-WAXAHACHI OFC 69KV/ENNIS-STERRETT 138KV (DOUBLE B TO B) A REAGOR | 138 | 138 | Branch Amp | 1004.0873 | - | - | 111.9581 | - | - | - | -
TONCOR , TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TRUMBULL8 (221) -> GAMMA_8 (12344) CKT 1 | Pre-contingency | 138 | 138 | Amps | 1004.0874 | - | - | - | 118.4487 | 133.0525 | 110.1207 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | TRUMBULL8 (221) -> PEBBLCRK_8 (2229) CKT 1 | Pre-contingency | 138 | 138 | Amps | 1004.0874 | - | - | - | 118.7615 | 135.708 | 109.5407 | -
TAEPTC | COAST | COAST | COAST, COAST | TUNGSTEN2A ( 8161) -> GREENLK2A ( 8159) CKT 1 | L_008144SEADRFTC4A-008189TUNGSTEN4AC1 | 69 | 69 | Branch Amp | 343.0632 | - | - | - | - | 103.4858 | - | -
TAEPTC | COAST | COAST | COAST, COAST | TUNGSTEN2A ( 8161) -> GREENLK2A ( 8159) CKT 1 | L_008144SEADRFTC4A-080065MELNCRK4AC1 | 69 | 69 | Branch Amp | 343.0632 | - | - | - | - | 103.4494 | - | -
TAEPTC | COAST | COAST | COAST, COAST | TUNGSTEN2A ( 8161) -> GREENLK2A ( 8159) CKT 1 | M100101100271-1A | 69 | 69 | Branch Amp | 343.0632 | - | - | - | - | 107.1416 | - | -
TAEPTC | COAST | COAST | COAST, COAST | TUNGSTEN2A ( 8161) -> GREENLK2A ( 8159) CKT 1 | M100101100271-1B | 69 | 69 | Branch Amp | 343.0632 | - | - | - | - | 104.0747 | - | -
TAEPTC | COAST | COAST | COAST, COAST | TUNGSTEN2A ( 8161) -> GREENLK2A ( 8159) CKT 1 | MB1002710010-1 | 69 | 69 | Branch Amp | 343.0632 | - | - | - | - | 106.5336 | - | -
TAEPTC | COAST | COAST | COAST, COAST | TUNGSTEN2A ( 8161) -> GREENLK2A ( 8159) CKT 1 | MB1291012930 | 69 | 69 | Branch Amp | 343.0632 | - | - | - | - | 103.3114 | - | -
TONCOR | EAST | EAST | EAST, EAST | TYLERE_8 ( 3211) -> DELEKTAP2_8 ( 3214) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | - | 109.7819 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | BAS_RANCH_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5403 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | DRY_CREEK_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 112.9355 | 100.886 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.4613 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | ERIKA_CON | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 105.7065 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | G_888839BAS_RANCH_POIUC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.5414 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 107.9192 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 110.4218 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | L_002432TRICRN1_5-888878ERIKA_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 106.9691 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 112.6679 | 101.3982 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | L_003109STRYKER_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 108.4648 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | L_003116MTENTRPR_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.45 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 115.6308 | 103.9504 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | L_888878ERIKA_POI-003105ELKTON_5C1 | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 104.2884 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | ML-SK*ME-TR (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 109.2534 | - | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | TRIN-SK*ME (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 113.8153 | 132.6538 | 118.0398 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 107.5872 | - | 109.1858 | -
TONCOR | EAST | NORTH_CE | EAST, NORTH_CE | TYLERGND_5 ( 3102) -> KNGSCRK2_5 (15203) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 102.1055 | - | -
TONCOR | EAST | EAST | EAST, EAST | TYLERGND_8 ( 3143) -> PRKCENTRAL_8 ( 3164) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 2062.5625 | - | - | - | 140.8816 | 158.2062 | 147.4067 | -
TONCOR | EAST | EAST | EAST, EAST | TYLERGND_8 ( 3143) -> PRKCENTRAL_8 ( 3164) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 2062.5625 | - | - | - | 138.7899 | 155.8909 | 144.675 | -
TONCOR | EAST | EAST | EAST, EAST | TYLERGND_8 ( 3143) -> PRKCENTRAL_8 ( 3164) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 2062.5625 | - | - | 104.2283 | 145.9717 | 164.7875 | 152.4911 | -
TONCOR | EAST | EAST | EAST, EAST | TYLERLOP_8 ( 3220) -> TYLRBUL_8 ( 3219) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1999.8074 | - | - | 102.525 | 143.8011 | 161.6245 | 150.5366 | -
TONCOR | EAST | EAST | EAST, EAST | TYLERLOP_8 ( 3220) -> TYLRBUL_8 ( 3219) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 141.6403 | 159.2429 | 147.7042 | -
TONCOR | EAST | EAST | EAST, EAST | TYLERLOP_8 ( 3220) -> TYLRBUL_8 ( 3219) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1999.8074 | 100.1294 | - | 107.488 | 149.0489 | 168.4005 | 155.7761 | -
TONCOR | EAST | EAST | EAST, EAST | TYLERNE_8 ( 3210) -> DELELKTAP1_8 ( 3208) CKT 1 | L_003100MARTINLK_5-003102TYLERGND_5C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 106.2939 | 131.3066 | 118.0426 | -
TONCOR | EAST | EAST | EAST, EAST | TYLERNE_8 ( 3210) -> DELELKTAP1_8 ( 3208) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | 106.2311 | 150.9315 | 188.4667 | 164.1318 | -
TONCOR | EAST | EAST | EAST, EAST | TYLERNE_8 ( 3210) -> DELELKTAP1_8 ( 3208) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1313.6809 | 104.4232 | - | 111.3232 | 157.0647 | - | 169.1763 | -
TONCOR | EAST | EAST | EAST, EAST | TYLERNW_8 ( 3141) -> BLACKFORK ( 3137) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1648.3767 | - | - | - | - | 120.3042 | 105.6347 | -
TONCOR | EAST | EAST | EAST, EAST | TYLERNW_8 ( 3141) -> BLACKFORK ( 3137) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1648.3767 | - | - | - | 101.5157 | - | 111.0877 | -
TONCOR | EAST | EAST | EAST, EAST | TYLERNW_8 ( 3141) -> BLACKFORK ( 3137) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1648.3767 | - | - | - | - | 103.6287 | - | -
TONCOR | EAST | EAST | EAST, EAST | TYLERNW_8 ( 3141) -> BLACKFORK ( 3137) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1648.3767 | - | - | - | - | 101.9913 | - | -
TONCOR | EAST | EAST | EAST, EAST | TYLERNW_8 ( 3141) -> BLACKFORK ( 3137) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1648.3767 | - | - | - | - | 107.4526 | - | -
TONCOR | EAST | EAST | EAST, EAST | TYLRBUL_8 ( 3219) -> ELKTON_8 ( 3106) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 132.7349 | 149.9619 | 139.6319 | -
TONCOR | EAST | EAST | EAST, EAST | TYLRBUL_8 ( 3219) -> ELKTON_8 ( 3106) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 130.6007 | 147.7666 | 136.6224 | -
TONCOR | EAST | EAST | EAST, EAST | TYLRBUL_8 ( 3219) -> ELKTON_8 ( 3106) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1999.8074 | - | - | - | 137.9642 | 156.6045 | 144.8095 | -
TONCOR | EAST | EAST | EAST, EAST | UMBRA_POI (888843) -> MOSES_5 ( 1695) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 104.4873 | 108.7705 | 107.6981 | -
TONCOR | NORTH_CE | NORTH | NORTH_CE, NORTH | VAL_STH_5 ( 1729) -> FARMVLSW_5 ( 1685) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | - | 100.3573 | - | -
TONCOR | NORTH | NORTH_CE | NORTH, NORTH_CE | VALLYSES1_5 ( 1690) -> ANNASW_5 ( 2373) CKT 1 | VALLEY S-ANNA SW 345 KV & VALLEY S-FARMERSVILLE 345 KV | 345 | 345 | Branch Amp | 3199.6917 | - | - | - | - | 106.7401 | 100.1625 | -
TONCOR | NORTH | NORTH | NORTH, NORTH | VALLYSES1_5 ( 1690) -> VAL_STH_5 ( 1729) CKT 1 | L_001690VALLYSES1_5-002373ANNASW_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 100.7223 | - | -
TONCOR | NORTH | NORTH | NORTH, NORTH | VALLYSES1_8 ( 1691) -> BELLSN_T8 ( 1699) CKT 2 | L_001839STONCRK_8-012677HAGGRTY_8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 124.1827 | 133.1903 | 129.7288 | -
TSTEC | COAST | COAST | COAST, COAST | VANDERBLTSW8 ( 5584) -> VANDERBLTSW9 ( 5582) CKT 1 | L_005502RAYBURN8-005506FURHMANSW8C1 | 69 | 138 | Branch MVA | 112 | - | - | - | - | 115.433 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VEALJNCTN ( 534) -> AGNESSWTCH ( 511) CKT 1 | BEPC_006 | 138 | 138 | Branch Amp | 836.7394 | - | - | 102.3072 | 109.4939 | 137.2532 | 123.9071 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VEALJNCTN ( 534) -> AGNESSWTCH ( 511) CKT 1 | BEPC_283_1 | 138 | 138 | Branch Amp | 836.7394 | - | - | - | - | 111.2755 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VEALJNCTN ( 534) -> AGNESSWTCH ( 511) CKT 1 | BEPC_432 | 138 | 138 | Branch Amp | 836.7394 | - | - | - | - | 102.2393 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VEALJNCTN ( 534) -> AGNESSWTCH ( 511) CKT 1 | L_000570WISECNTY-000571HIDEOUTC1 | 138 | 138 | Branch Amp | 836.7394 | - | - | - | - | 110.2757 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VEALJNCTN ( 534) -> AGNESSWTCH ( 511) CKT 1 | L_000571HIDEOUT-000579JCKCNTY8C1 | 138 | 138 | Branch Amp | 836.7394 | - | - | - | - | 111.2846 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VEALJNCTN ( 534) -> AGNESSWTCH ( 511) CKT 1 | L_000576RHOME-000585CHISOLMC1 | 138 | 138 | Branch Amp | 836.7394 | - | - | - | - | 102.9514 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VEALJNCTN ( 534) -> AGNESSWTCH ( 511) CKT 1 | ROANOKE - RHOME 138 KV & ROANOKE - GRAPEVINE SW 138 KV (DOUBLE B TO B) F FLOWERMOUND WEST | 138 | 138 | Branch Amp | 836.7394 | - | - | - | - | 101.0739 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS ( 1908) -> RAILPORT ( 442) CKT 1 | CARMICHAEL BEND-TIMBERVIEW 345 KV*DECORDOVA-CLEBURNE 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | 102.08 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS ( 1908) -> RAILPORT ( 442) CKT 1 | CLEBURNE-DECORDOVA 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | 101.8274 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS ( 1908) -> RAILPORT ( 442) CKT 1 | CLEBURNE-DECORDOVA/BURLESON 138 KV (DOUBLE B TO B) B WILSHIRE | 138 | 138 | Branch Amp | 895.3112 | - | 106.1684 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS ( 1908) -> RAILPORT ( 442) CKT 1 | L_001303FORBESRD_8-001905GRIFFTH_P8C1 | 138 | 138 | Branch Amp | 895.3112 | 103.2834 | 141.2342 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS ( 1908) -> RAILPORT ( 442) CKT 1 | L_001905GRIFFTH_P8-002297ALVARADO1_8C1 | 138 | 138 | Branch Amp | 895.3112 | 111.3628 | 145.2776 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS ( 1908) -> RAILPORT ( 442) CKT 1 | L_002279CLEBRNSW_8-002280CLEBRN_N_8C1 | 138 | 138 | Branch Amp | 895.3112 | - | 101.8365 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS ( 1908) -> RAILPORT ( 442) CKT 1 | L_002279CLEBRNSW_8-002294KEENE_8C1 | 138 | 138 | Branch Amp | 895.3112 | 119.029 | 136.3584 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS ( 1908) -> RAILPORT ( 442) CKT 1 | L_002280CLEBRN_N_8-002283AIRLIQD_P8C1 | 138 | 138 | Branch Amp | 895.3112 | 101.764 | 103.6096 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS ( 1908) -> RAILPORT ( 442) CKT 1 | L_002281GODLEY_8-002283AIRLIQD_P8C1 | 138 | 138 | Branch Amp | 895.3112 | 104.6009 | 106.6458 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS ( 1908) -> RAILPORT ( 442) CKT 1 | L_002281GODLEY_8-002888CARMICHL_8C1 | 138 | 138 | Branch Amp | 895.3112 | 104.6573 | 106.6081 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS ( 1908) -> RAILPORT ( 442) CKT 1 | L_002294KEENE_8-002297ALVARADO1_8C1 | 138 | 138 | Branch Amp | 895.3112 | 112.1197 | 134.9428 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS ( 1908) -> RAILPORT ( 442) CKT 1 | L_003522HILLBORO1_8-003546WHITNEY__8C1 | 138 | 138 | Branch Amp | 895.3112 | - | 103.04 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS ( 1908) -> RAILPORT ( 442) CKT 1 | SOAP CREEK - CEDAR HILL / SARDIS 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 895.3112 | - | 100.3274 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS ( 1908) -> RAILPORT ( 442) CKT 1 | VENUS-JOHNSON 345KV/DECORDOVA-CLEBURNE 138KV (DOUBLE B TO B) new load | 138 | 138 | Branch Amp | 895.3112 | - | 102.4842 | - | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 104.6551 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 104.3007 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | DES_WILL_CON | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 108.7531 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | L_001906VENUS_S5-888880DES_WILL_POIC1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 107.5359 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | L_888880DES_WILL_POI-001916LIGGETTA2_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 108.6724 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 107.274 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 108.1299 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 108.7654 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | 100.396 | 109.456 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 108.6622 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 108.5816 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 108.0603 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 107.9494 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 109.2049 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | 100.6763 | 110.3972 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | 100.539 | 109.9274 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> MILLERRD_5 ( 2632) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | 100.3076 | 109.3645 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | 3WT_001882EVRMAN_W5_011887EVERMAN3_T8_011884EVRMAN1_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.4556 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | 3WT_001886EVRMAN_E5_011882EVERMAN1_T8_024997EVRMAN4_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.4547 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | 3WT_001907VENUS_N5_001909VENUS1_8_011910VENUS2_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0951 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | 3WT_001918SHRYAUTO1_5_001920SHRY_B8_011920SHRY_B_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.5422 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | 3WT_001934SHRYAUTO2_5_001919SHRY_A8_011921SHRY_A_3 C 2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.5351 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | 3WT_002420CHILSW1_5_016421CHILSW_1T8_012419CHILSW1_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.1385 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | 3WT_002431DESSW1_5_002424DESSW1_8_012431DESSW1_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 105.384 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | 3WT_002847LOOP9_5_002848LOOP9_8_012847LOOP9_2_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.4572 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | 3WT_002847LOOP9_5_002848LOOP9_8_012848LOOP9_1_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.4572 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | 3WT_003124TRINDAD2_5_003127TRINIDAD_8_024140TRINIDAD2_3 C 3 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.013 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | 3WT_003522HILLBORO1_8_003523HILLBORO1_9_003519HILLBORO1_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.9346 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | 3WT_013125TDADTMOD_5_003127TRINIDAD_8_120151TRSES_UNIT6 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.1718 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 1 | Branch MVA | 750 | - | - | 100.8925 | - | - | 106.2307 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 105.3982 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | BEPC_008 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.248 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | BEPC_108 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.3412 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | BEPC_210_1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.3179 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | BEPC_211 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.6896 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | BEPC_225 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | BEPC_227-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.0937 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | BEPC_227-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.0937 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | BEPC_229 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.4315 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | BEPC_459 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.2577 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.6165 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | CARMICHAEL BEND-TIMBERVIEW 345 KV*DECORDOVA-CLEBURNE 138 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.6352 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | CEDAR HILL - DESOTO/LOOP NINE 345 KV DCKT (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.2023 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | CEDAR HILL - SHERRY / FISH CREEK DCKT (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.0223 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 1 | Branch MVA | 750 | - | - | 103.5993 | - | - | 107.671 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | CEDAR HILL SW - FISH CREEK 138 KV (SINGLE B TO B) FISH CREEK 138/69 TRANSFORMER | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.4565 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | CEDAR HILL SW 045 - SHERRY (SINGLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.1201 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | CEDAR HILL SW 345-138 KV AUTO #1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.456 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | 104.6549 | - | - | 108.545 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | CLEBURNE-DECORDOVA 138 KV (SINGLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.3854 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | CLEBURNE-DECORDOVA/BURLESON 138 KV (DOUBLE B TO B) B WILSHIRE | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.2489 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | DIVISION-SHERRY/GENERAL MOTORS 138 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0821 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | E_BOSQUESW_CC1_TRAIN | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2039 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | E_BOSQUESW_CC2_TRAIN | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.1964 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | E_ETCCS_CC1_TRAIN | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.1888 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | E_TGCCS_CC1_TRAIN | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2771 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.8892 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.1533 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | ENNIS WEST - STERRETT 138 KV (SINGLE B TO B) A REAGOR SPRINGS | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.283 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | EVERMAN - MARRS (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0154 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | G_000099BENHURUS1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0251 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | G_003321REDLAND_5UN1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0944 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | G_003478NAVARRO1_8US1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2132 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | G_120041MLSES_UNIT1UL1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2455 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | G_120042MLSES_UNIT2UL2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.25 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | G_120043MLSES_UNIT3UL3 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2557 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | G_120142SCSES_UNIT2UN2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0302 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | G_120151TRSES_UNIT6UN6 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.1718 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | G_152281ELLISSLR_S1US1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.3641 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | G_153961GAIA_SOL_S1US1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.096 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | G_154011MIDPOINT_S1US1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.8228 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | G_888859HIGHNOON_POIUS1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.4219 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | G_888875THRESLR_POIUS1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.5822 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | G_888876P_BTTLECRK_POIUS1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0509 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | GLASGOW_CON | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.7319 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | HIGHNOON_CON | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.3059 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | HILLS-ALVARADO_9 (SINGLE B TO B ) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.3362 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | HILLSBORO-ASH CREEK 138 KV (SINGLE B TO B) B | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.1384 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000099BENHUR-000107PRAIRIEHILC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.4837 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000107PRAIRIEHIL-000186NAVAROMILSC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.384 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000186NAVAROMILS-000190DAWSONC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.394 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000190DAWSON-000194PURDONC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.3517 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.3696 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.4173 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000193BARRY-000194PURDONC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.36 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000193BARRY-000210REAGORSPRGC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.3137 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000200CHATFIELD-003454MONTFTSS__8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.095 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000200CHATFIELD-003455CORS1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.1567 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000202SARDIS9-000210REAGORSPRGC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2204 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000203SARDIS8-000280LONGBRANCHC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.9165 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000217GLNHEIGHTS-002237STERTRD_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 104.1244 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000217GLNHEIGHTS-002424DESSW1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 105.2594 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000220CEDARHILL-000223SAINTPAULC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 104.5968 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000220CEDARHILL-000280LONGBRANCHC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.2897 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000223SAINTPAUL-000404JESSICAC1 | 345 | 1 | Branch MVA | 750 | - | - | 100.1282 | - | - | 105.3032 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000224ITASCA-000225FORRESTONC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.1409 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000224ITASCA-000228PEORIAC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.237 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000228PEORIA-000243WHITNEYSWC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.3391 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000232LAMPOSTSW-000241WHITNEY8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2612 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000232LAMPOSTSW-000445YATESC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.1885 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000234CHATT-003352PECANST_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2054 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000234CHATT-003522HILLBORO1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.1542 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000237BLANTON-888875THRESLR_POIC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.8028 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000237BLANTON-888889MIDPOINT_POIC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.6903 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000240WHITNEY5-000246BOSQUESW5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.6044 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000370JNSNCNTY8-000415KEENEC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.1146 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000394CONCORD8-000398JOSHUAC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.8426 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000398JOSHUA-000399CROWLEYC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.217 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000399CROWLEY-000405EGANC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.8131 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000404JESSICA-000419LILLIAN8C1 | 345 | 1 | Branch MVA | 750 | - | - | 101.1243 | - | - | 106.3234 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000405EGAN-000412BURLESONC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.6251 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000412BURLESON-000430TIMBERGRENC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.186 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000419LILLIAN8-000428VALLYBRNCHC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.3869 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000419LILLIAN8-000439HIGHPOINTC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.2718 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000428VALLYBRNCH-000429RETTAC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.5486 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000429RETTA-000430TIMBERGRENC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.6362 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000432CONLEY-000436GRANDVIEWC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.7151 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000432CONLEY-000439HIGHPOINTC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.434 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000436GRANDVIEW-000443SANDFLATSWC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.9445 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000443SANDFLATSW-000444COVINGTONC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0298 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_000444COVINGTON-888859HIGHNOON_POIC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.1184 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001303FORBESRD_8-001905GRIFFTH_P8C1 | 345 | 1 | Branch MVA | 750 | - | - | 102.6701 | - | - | 110.9731 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001883EVRMAN_A8-001933KENNEDALE_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.7945 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.6501 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.9204 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001905GRIFFTH_P8-002297ALVARADO1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | 104.3169 | - | - | 112.7558 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.0516 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 345 | 1 | Branch MVA | 750 | - | - | 103.5275 | - | - | 109.6177 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001907VENUS_N5-011902BRITTNRD2_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.5205 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001909VENUS1_8-002302COTTONWD2_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0952 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001911WEBB1_5-001929CENTURY1_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.8514 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001911WEBB1_5-011902BRITTNRD2_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.3939 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001918SHRYAUTO1_5-001929CENTURY1_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.194 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001919SHRY_A8-002257PARKROW1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.132 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001920SHRY_B8-002258PARKROW2_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2637 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001921LIGGETTA1_5-002632MILLERRD_5C1 | 345 | 1 | Branch MVA | 750 | - | - | 101.1909 | - | - | 105.0891 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001928LIGGETT_3T5-002406NORWD1_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.9958 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.8031 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.4754 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001933KENNEDALE_8-002208MANSFLD_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.4583 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_001969MARRS_8-002198GARDNACR_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.6694 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002198GARDNACR_8-002209BURLESON_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.4765 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.6165 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.8892 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 104.358 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002258PARKROW2_8-002259LTV1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.1306 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002259LTV1_8-002262GRANDPR1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0186 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002260POLY_AM1_8-012492LAKECRST_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.6991 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002279CLEBRNSW_8-002280CLEBRN_N_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.3466 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002279CLEBRNSW_8-002290CLEBRN_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.1998 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002279CLEBRNSW_8-002294KEENE_8C1 | 345 | 1 | Branch MVA | 750 | - | - | 105.0249 | - | - | 112.6605 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002280CLEBRN_N_8-002283AIRLIQD_P8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.7289 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002281GODLEY_8-002283AIRLIQD_P8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 104.272 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002281GODLEY_8-002888CARMICHL_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 104.2864 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002290CLEBRN_8-002291CLEBRN_W_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.9573 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002291CLEBRN_W_8-037810TNHILL_CO_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.5261 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002294KEENE_8-002297ALVARADO1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | 104.0278 | - | - | 111.4309 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002298ALVARADO1_9-003537GRANDVEW1_9C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.5063 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002315WAX_PMP2_8-002319WAX_PMP1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.017 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002315WAX_PMP2_8-002320WAX_N_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.0786 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002316MG_IND_T8-002319WAX_PMP1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.808 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002320WAX_N_8-002321WAX_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.4684 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 104.1561 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.2706 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.1805 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002406NORWD1_5-012398TOPEKA1_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.3196 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002422CHILSW_N8-002491FSHCRK1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2894 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002422CHILSW_N8-003049EGLFD2_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.0793 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002424DESSW1_8-002425DESPKV1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0887 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002424DESSW1_8-012425DESPKV2_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0664 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002429WATMLL_8-003065REINDEER_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.3906 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.9327 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_002491FSHCRK1_8-012492LAKECRST_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.6994 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_003049EGLFD2_8-003050SORCEY1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.5963 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_003051SORCEY2_8-003052DVILS1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.312 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_003052DVILS1_8-003055CHCLRKRD_T8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.4935 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.4215 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_003127TRINIDAD_8-003723OLYMPUS_SWC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2068 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_003134RICHLND1_5-003380BIGBRNE_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.4299 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.69 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_003352PECANST_8-003473ASHCREEK_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2129 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_003483GOODLOE_P_8-003490LNGPRAIRIE_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_003490LNGPRAIRIE_8-152736FENCESLR_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.1833 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_003518BLUMPUMP1_8-037810TNHILL_CO_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.6646 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_003522HILLBORO1_8-003546WHITNEY__8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.5645 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_003523HILLBORO1_9-003532ITASCA_9C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.4381 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_003532ITASCA_9-003533FILE_SIN1_T9C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.2592 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_003533FILE_SIN1_T9-003537GRANDVEW1_9C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.9134 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_003723OLYMPUS_SW-003454MONTFTSS__8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.6501 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_060017HODLRAN27A-060515CLEARCRO7AC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.1274 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_888859HIGHNOON_POI-000445YATESC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.1692 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_888875THRESLR_POI-003522HILLBORO1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.6374 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_888876P_BTTLECRK_POI-003515HUBBARD_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0131 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.6732 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | L_888889MIDPOINT_POI-003518BLUMPUMP1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.7025 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 345 | 1 | Branch MVA | 750 | - | - | 103.7206 | - | - | 106.7505 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | LIGGETT-DFW-EULESS(DFW MID) 138 KV (DOUBLE B TO B) ESTELLE | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0686 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | LIGGETT-HANDLEY/EXECUTIVE PKWY 138 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0773 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | LIGGETT-NORWOOD 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.8341 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 345 | 1 | Branch MVA | 750 | - | - | 105.7539 | - | - | 111.2354 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 345 | 1 | Branch MVA | 750 | - | - | 106.0474 | - | - | 111.9467 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | MARRS - BURLESON 138 KV (SINGLE B TO B) GARDEN ACRES | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.3964 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | MB2552825529 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.147 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | NAVARRO-ASH CREEK 138 KV (SINGLE B TO B)-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0929 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | NAVARRO-ASH CREEK 138 KV (SINGLE B TO B)-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0929 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-1-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.2318 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.2318 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.5842 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | NEW-HILLSBORO-CLEBURNE_SW_8 (SINGLE B TO B )-1-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.5842 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.8716 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.3165 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | NORWOOD - LIGGETT/CEDAR HILL DCKT 345 KV (DOUBLE B TO B) NEW_LOAD | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.8032 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | NORWOOD-LIGGETT 345 & MOUNTAIN CREEK - LIGGETT 138 KV DCKT A BLUBONT | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.8261 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | P_BTTLECRK_CON | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.1533 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | S_002303KEMPRNCH_81 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.7921 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | SHERRY - FISH CREEK 138 KV (SINGLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.8771 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | SHERRY-FISH CREEK/CEDAR HILL (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.3933 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | SHERRY-TIMBERVIEW*VENUS 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 104.9406 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | SHERRY-VENUS 345 KV (SINGLE B TO B) BRITTON RD | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.5702 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | STERRETT 5400 - DESOTO (SINGLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.9544 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | T_000202SARDIS9-000203SARDIS8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2192 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | T_002298ALVARADO1_9-002297ALVARADO1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.5058 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | THRESLR_CON | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1506 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.6784 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | TIMBERVIEW-SHERRY 345 KV WITH SHERRY AUTO (SINGLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.3528 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1786 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | TRICORNER - WATERMILL (DOUBLE B TO B) B | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.2178 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.9519 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 345 | 1 | Branch MVA | 750 | - | - | 100.795 | - | - | 106.0712 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | VENUS - WEBB 345KV (SINGLE B TO B) BRITTONRD2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.4559 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | 1 | Branch MVA | 750 | - | - | 106.2558 | - | - | 111.6822 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.8309 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 345 | 1 | Branch MVA | 750 | - | - | 100.6617 | - | - | 106.1833 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | VENUS-JOHNSON 345KV/DECORDOVA-CLEBURNE 138KV (DOUBLE B TO B) new load | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.7312 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | WATERMILL-LOOP NINE 345 KV DCKT (DOUBLE B TO B) A | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.9651 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | WAXAHACHI-WAXAHACHI OFC 69KV/ENNIS-STERRETT 138KV (DOUBLE B TO B) A REAGOR | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.4513 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 105.0607 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 345 | 1 | Branch MVA | 750 | - | - | 100.6102 | - | - | 105.9608 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | WEDGWOOD-ROCKY CREEK 138 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2002 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | XFMR-ENNSTRAC_8-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.425 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | XFMR-ENNSTRAC_8-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.126 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | XFMR-MARTINLK_5-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2455 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | XFMR-MARTINLK_5-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.25 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | XFMR-MARTINLK_5-3 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2557 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 ( 1907) -> VENUSSTR (500057) CKT 1 | XFMR-STRYKER_8-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0302 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_N5 (1907) -> VENUSSTR (500057) CKT 1 | Pre-contingency | 345 | 1 | MVA | 695 | - | - | 100.5342 | 112.9736 | 116.5235 | 107.6417 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | 109.1989 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | 103.9574 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 100.9383 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | DES_WILL_CON | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 107.9933 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | L_001906VENUS_S5-888880DES_WILL_POIC1 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 107.5156 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 107.3756 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | 100.5236 | 110.3972 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 100.9383 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | L_888880DES_WILL_POI-001916LIGGETTA2_5C1 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 108.532 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 106.8222 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 107.5603 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 107.5196 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 108.3115 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 108.0085 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 108.5471 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | 105.8502 | 116.2871 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | 105.7307 | 116.2976 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | 106.2022 | 116.7461 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 107.6869 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | 102.0564 | 111.6265 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | 108.1575 | 119.9891 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 107.0557 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 107.5309 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-1 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 107.0825 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-2 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 107.9364 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 107.8994 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> BRITNRD1_5 (11901) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 3200.0261 | - | - | - | - | 108.3266 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> DES_WILL_POI (888880) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | 104.4496 | 115.4546 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> DES_WILL_POI (888880) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | 107.2501 | 117.8545 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> DES_WILL_POI (888880) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 101.1488 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> DES_WILL_POI (888880) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 102.2357 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> DES_WILL_POI (888880) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 101.0533 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 ( 1906) -> DES_WILL_POI (888880) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2624.0149 | - | - | - | - | 100.7383 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUS_S5 (1906) -> FORBESR2_5 (15201) CKT 1 | Pre-contingency | 345 | 345 | Amps | 1725.3568 | - | - | - | - | 112.1657 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | 3WT_002431DESSW1_5_002424DESSW1_8_012431DESSW1_3 C 1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.6191 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.4941 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.5372 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.5333 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 1 | Branch MVA | 750 | - | - | 100.7233 | - | - | 104.3411 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | L_000217GLNHEIGHTS-002424DESSW1_8C1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2625 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | L_000220CEDARHILL-000223SAINTPAULC1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.3739 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | L_000223SAINTPAUL-000404JESSICAC1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.3536 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | L_000404JESSICA-000419LILLIAN8C1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.2726 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | L_001303FORBESRD_8-001905GRIFFTH_P8C1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 106.7375 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | L_001905GRIFFTH_P8-002297ALVARADO1_8C1 | 138 | 1 | Branch MVA | 750 | - | - | 100.7394 | - | - | 108.3016 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 105.2129 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | L_001921LIGGETTA1_5-002632MILLERRD_5C1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.1036 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2357 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | L_002279CLEBRNSW_8-002294KEENE_8C1 | 138 | 1 | Branch MVA | 750 | - | - | 101.2051 | - | - | 107.9442 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | L_002281GODLEY_8-002283AIRLIQD_P8C1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.259 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | L_002281GODLEY_8-002888CARMICHL_8C1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.2742 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | L_002294KEENE_8-002297ALVARADO1_8C1 | 138 | 1 | Branch MVA | 750 | - | - | 100.2407 | - | - | 106.862 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.0609 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 138 | 1 | Branch MVA | 750 | - | - | 100.0216 | - | - | 102.8463 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 138 | 1 | Branch MVA | 750 | - | - | 101.869 | - | - | 106.8549 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 138 | 1 | Branch MVA | 750 | - | - | 102.0983 | - | - | 107.3971 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | SHERRY-TIMBERVIEW*VENUS 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.9265 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.111 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 1 | Branch MVA | 750 | - | - | 102.3047 | - | - | 107.3114 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1613 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.1627 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | VENUSSTR (500057) -> KEMPRNCH_8 ( 2303) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.9977 | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | VERN4A ( 6060) -> VERN2B ( 6055) CKT 1 | L_006063SANDROAD2A-006064VERS2AC1 | 69 | 138 | Branch MVA | 63 | 107.4975 | - | 107.7706 | 108.5319 | 108.2406 | 108.245 | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | VERN4A ( 6060) -> VERN2B ( 6055) CKT 1 | L_006066VERS4A-006098OKLA4BC1 | 69 | 138 | Branch MVA | 63 | 107.4787 | - | 107.7517 | 108.5125 | 108.2213 | 108.2258 | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | VERN4A ( 6060) -> VERN2B ( 6055) CKT 1 | T_006064VERS2A-006066VERS4AC1 | 69 | 138 | Branch MVA | 63 | 107.4786 | - | 107.7516 | 108.5125 | 108.2212 | 108.2257 | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | VERN4A ( 6060) -> VERN2B ( 6055) CKT 1 | T_006100OKLA7A-006098OKLA4BC1 | 69 | 138 | Branch MVA | 63 | 107.2078 | - | 107.4802 | 108.2564 | 107.9448 | 107.9506 | -
TETRTX | NORTH | NORTH | NORTH, NORTH | VERS2A ( 6064) -> SANDROAD2A ( 6063) CKT 1 | 3WT_006100OKLA7A_006097OKLA4A_060780OK1TERT C 1 | 69 | 69 | Branch Amp | 702.8611 | 131.8108 | - | 128.5628 | 131.1705 | 140.0261 | 132.9958 | -
TETRTX | NORTH | NORTH | NORTH, NORTH | VERS2A ( 6064) -> SANDROAD2A ( 6063) CKT 1 | L_006060VERN4A-006097OKLA4AC1 | 69 | 69 | Branch Amp | 702.8611 | 130.8772 | - | 127.0508 | 130.8017 | 139.0608 | 132.0338 | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | VERS4A ( 6066) -> VERS2A ( 6064) CKT 1 | 3WT_006100OKLA7A_006097OKLA4A_060780OK1TERT C 1 | 69 | 138 | Branch MVA | 77 | 147.1691 | - | 143.3118 | 145.7696 | 155.2712 | 147.9959 | -
TAEPTN | NORTH | NORTH | NORTH, NORTH | VERS4A ( 6066) -> VERS2A ( 6064) CKT 1 | L_006060VERN4A-006097OKLA4AC1 | 69 | 138 | Branch MVA | 77 | 146.1372 | - | 141.7936 | 145.3085 | 154.2194 | 146.9419 | -
TAEPTN | COAST | SOUTHERN | COAST, SOUTHERN | VICTORIA2A ( 8169) -> OCONNER2A ( 8591) CKT 1 | L_008144SEADRFTC4A-008189TUNGSTEN4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 112.1408 | 154.9564 | 103.4988 | -
TAEPTN | COAST | SOUTHERN | COAST, SOUTHERN | VICTORIA2A ( 8169) -> OCONNER2A ( 8591) CKT 1 | L_008144SEADRFTC4A-080065MELNCRK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 111.8733 | 154.6716 | 103.2508 | -
TAEPTN | COAST | SOUTHERN | COAST, SOUTHERN | VICTORIA2A ( 8169) -> OCONNER2A ( 8591) CKT 1 | L_008412REFUGIO4A-008813QUINTANA4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 119.7783 | - | -
TAEPTN | COAST | SOUTHERN | COAST, SOUTHERN | VICTORIA2A ( 8169) -> OCONNER2A ( 8591) CKT 1 | L_008455LONHILL7A-008579KATOEN7AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 101.9573 | - | -
TAEPTN | COAST | SOUTHERN | COAST, SOUTHERN | VICTORIA2A ( 8169) -> OCONNER2A ( 8591) CKT 1 | L_008813QUINTANA4A-080065MELNCRK4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 123.726 | - | -
TAEPTN | COAST | SOUTHERN | COAST, SOUTHERN | VICTORIA2A ( 8169) -> OCONNER2A ( 8591) CKT 1 | L10011206 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 119.7647 | - | -
TAEPTN | COAST | SOUTHERN | COAST, SOUTHERN | VICTORIA2A ( 8169) -> OCONNER2A ( 8591) CKT 1 | M128103100534 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 104.1782 | - | -
TAEPTN | COAST | SOUTHERN | COAST, SOUTHERN | VICTORIA2A ( 8169) -> OCONNER2A ( 8591) CKT 1 | M128104100523 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 102.9621 | - | -
TAEPTN | COAST | SOUTHERN | COAST, SOUTHERN | VICTORIA2A ( 8169) -> OCONNER2A ( 8591) CKT 1 | MB1005312810 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 104.1171 | - | -
TAEPTN | COAST | SOUTHERN | COAST, SOUTHERN | VICTORIA2A ( 8169) -> OCONNER2A ( 8591) CKT 1 | MB1281010052 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 102.9023 | - | -
TAEPTN | COAST | SOUTHERN | COAST, SOUTHERN | VICTORIA2A ( 8169) -> OCONNER2A ( 8591) CKT 1 | MB1291012930 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 147.9574 | 104.0793 | -
TAEPTN | COAST | SOUTHERN | COAST, SOUTHERN | VICTORIA2A ( 8169) -> OCONNER2A ( 8591) CKT 1 | MB1293012910 | 69 | 69 | Branch Amp | 317.961 | - | - | - | 111.7674 | - | - | -
TAEPTN | COAST | SOUTHERN | COAST, SOUTHERN | VICTORIA2A ( 8169) -> OCONNER2A ( 8591) CKT 1 | SAN_PAT_CON | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 104.2091 | - | -
TAEPTN | COAST | SOUTHERN | COAST, SOUTHERN | VICTORIA2A ( 8169) -> OCONNER2A ( 8591) CKT 1 | T_008410REFUGIO2A-008412REFUGIO4AC1 | 69 | 69 | Branch Amp | 317.961 | - | - | - | - | 119.6353 | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 1 | E5DVA1C1_1_B | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 105.8571 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 1 | E5DVA1C1_1_B_1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 101.2586 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 1 | L_005607WRBRTN8-008912MEDIOCR4AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 100.3343 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 1 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 106.2593 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 1 | L_008143V_DUPSW4A-081433SARDINIA4AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 101.617 | - | 101.3498 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 1 | L_008144SEADRFTC4A-008189TUNGSTEN4AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 101.2221 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 1 | L_008144SEADRFTC4A-080065MELNCRK4AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 101.2112 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 1 | L_008162COLETO4A-008172VICTORIA4AC2 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 135.9408 | - | 134.7871 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 1 | L_008715RADIANT7A-008728COBRA7AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 118.0445 | - | 108.3571 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 1 | L_008728COBRA7A-081003HABER7AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 122.12 | - | 111.8243 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 1 | L_008912MEDIOCR4A-008920HAISLEY4AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 100.0805 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 1 | M128103100532 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 141.3125 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 1 | M128103100534 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | - | - | 140.0635 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 1 | MB1005312810 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 141.2761 | - | 140.0487 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 1 | MB1293012910 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 101.1044 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 1 | P7-1_E1>>T3944Z_ERC | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 106.0034 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | E5DVA1C1_1_B | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 111.4142 | - | 101.3033 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | E5DVA1C1_1_B_1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 106.5745 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | E5DVA1C1_1_B_2 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 104.1391 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 101.1874 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L_005502RAYBURN8-005730FORCORNERSB8C1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 102.1378 | - | 101.5848 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L_005607WRBRTN8-008172VICTORIA4AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 104.3564 | - | 102.4794 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L_005607WRBRTN8-008912MEDIOCR4AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 105.6029 | - | 103.3732 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L_005728CHOATESUB8-005730FORCORNERSB8C1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 101.8657 | - | 101.3205 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 111.8392 | - | 103.9448 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L_008143V_DUPSW4A-081433SARDINIA4AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 106.9531 | - | 106.6714 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L_008144SEADRFTC4A-008189TUNGSTEN4AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 106.5374 | - | 104.7283 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L_008144SEADRFTC4A-080065MELNCRK4AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 106.5258 | - | 104.7167 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L_008162COLETO4A-008172VICTORIA4AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 139.487 | - | 138.3301 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L_008437RINCON4B-080065MELNCRK4AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 102.4077 | - | 101.0381 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L_008676STATIC7A-081003HABER7AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | - | - | 101.4868 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L_008715RADIANT7A-008728COBRA7AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 124.2439 | - | 114.0465 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L_008728COBRA7A-081003HABER7AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 128.533 | - | 117.6953 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L_008912MEDIOCR4A-008920HAISLEY4AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 105.3358 | - | 103.1233 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L_008920HAISLEY4A-008924PORTILLA4AC1 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 102.7402 | - | 100.6533 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L10010650-1A | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 104.625 | - | 102.9954 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | L10010650-1B | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 102.1785 | - | 100.4369 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | M128104100523 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 144.9501 | - | 143.6977 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | MB1005212810 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 144.9128 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | MB1281010052 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | - | - | 143.6826 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | MB1291012930 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | - | - | 104.5945 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | MB1293012910 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 106.4135 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | P7-1_E1>>T1827GX_ERC | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 102.7923 | - | - | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | P7-1_E1>>T3944Z_ERC | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 111.5698 | - | 104.387 | -
TAEPTC,TAEPTN | SOUTHERN | COAST | SOUTHERN, COAST | VICTORIA4A ( 8172) -> COLETO4A ( 8162) CKT 2 | STECL_10131 | 138 | 138 | Branch Amp | 1338.7831 | - | - | - | 102.1301 | - | 101.5891 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | VLMOOR_8 (23835) -> KOCHTAP_8 (23829) CKT 1 | IRON_BELT_CON | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 110.8979 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | VLMOOR_8 (23835) -> KOCHTAP_8 (23829) CKT 1 | L_059900LONG_DRAW-888842IRON_BELT_POIC1 | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 108.5042 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | VLMOOR_8 (23835) -> KOCHTAP_8 (23829) CKT 1 | L_888842IRON_BELT_POI-059910VOLTAC1 | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 112.5134 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | VLMOOR_8 (23835) -> KOCHTAP_8 (23829) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 101.5831 | - | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | VLMOOR_8 (23835) -> KOCHTAP_8 (23829) CKT 1 | WETT LONG DRAW - WETT VOLTA 345 KV LINE (SINGLE B TO B)-2 | 138 | 138 | Branch Amp | 1631.642 | - | - | - | - | 112.5134 | - | -
ERCOT | SOUTH_CE | SOUTH_CE | SOUTH_CE, SOUTH_CE | VON_ROSE (5475) -> BRA_AVR1_CT2 (170135) CKT T2 | Pre-contingency | 345 | 18 | MVA | 193 | - | - | 102.5755 | - | 101.4174 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_A_P__POI5A (44000) -> OBRIEN_B345A (44500) CKT 98 | L_044000W_A_P__POI5A-044500OBRIEN_B345AC99 | 345 | 345 | Branch Amp | 2426.5444 | 107.3085 | - | - | - | - | - | -
TCNPE | COAST | COAST | COAST, COAST | W_A_P__POI5A (44000) -> OBRIEN_B345A (44500) CKT 99 | L_044000W_A_P__POI5A-044500OBRIEN_B345AC98 | 345 | 345 | Branch Amp | 2426.5444 | 107.3086 | - | - | - | - | - | -
TCNPE | COAST | COAST | COAST, COAST | W_A_P__POI8A (44010) -> IMPERL05T3_8 (44342) CKT 05 | P1-2_HOC_BUS_REACTOR | 138 | 138 | Branch Amp | 2196.4409 | - | - | - | - | 100.7414 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.113 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | 3WT_013125TDADTMOD_5_003127TRINIDAD_8_120151TRSES_UNIT6 C 1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9284 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | 3WT_044500OBRIEN_B345A_044510OBRIEN_B138A_049031OBRIEN_A1TER CA1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5429 | 100.0025 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | 3WT_044500OBRIEN_B345A_044510OBRIEN_B138A_049063OBRIEN_A3TER CA3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5595 | 100.0179 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | 3WT_044500OBRIEN_B345A_044510OBRIEN_B138A_049064OBRIEN_A2TER CA2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5323 | 100.0058 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | AEN_FPP-HO¦LY | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6547 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | AEN_LY-FPP¦CIS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2187 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | AEN_P1-1_GEN_SH5A+5C | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2261 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | AEN_P2HO345_RB_1201_1203(107OF224):-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.8488 | 101.2132 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1696 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1864 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5895 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1855 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5863 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3092 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7473 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3544 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7714 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3101 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7458 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3555 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7708 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1121 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5005 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1099 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4925 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLEN-MOSES 345-138 AUTO-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1808 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3907 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8459 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.375 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7909 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ARGENTA_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.131 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | B2-COD-1_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3318 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | BARRETT_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1571 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | BAS_RANCH_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.7906 | 100.1088 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.4889 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | BEPC_015_2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0765 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | BEPC_211 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3136 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | BEPC_22 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.491 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | BEPC_227-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2581 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | BEPC_227-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2581 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | BEPC_23_2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2596 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | BEPC_230_4 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0435 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | BEPC_311_2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3077 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5299 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0266 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | BITTER CREEK SW (LCRA) - CATTLEMEN SW & BITTER CREEK SW (LCRA) - SWEETWATER EAST 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6935 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | BLUBIRD_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.4648 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | BRYN_1037 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1859 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | CACTUS_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.47 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | CARLSON - STEGER (LCRA)_8 (SINGLE B TO B ) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1504 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | CARTWHEEL_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.08 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4565 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | CLUTCH_CITY_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.7312 | 106.5518 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | COODY CROSSING - TECUMSEH AND CLEAR CROSSING - THOMAS PRICE 345 KV DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1051 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | D5GSU1_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0123 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | D5GSU2_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0135 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | DERMOTT - COYOTE WIND 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1941 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | DERMOTT - KIRCHHOF CKT 1 & DERMOTT - KIRCHHOF CKT 2 345 KV (DOUBLE B TO B) C | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5286 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | DERMOTT - KIRCHHOF CKT 1 345 KV WIN 2023 - FUTURE (SINGLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5456 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | DES_WILL_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0001 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | DRY_CREEK_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0729 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | DUNE - WINK/YUKON 138 KV 2019 SUM - FUTURE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6365 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | DUNHAM - LEWISVILLE DC 345 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.019 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | DVCPA1C21B_1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.4318 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | DVCPA1C21B_2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.6275 | 100.585 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_AMOCOOIL_CC2_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9809 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_AMOCOOIL_CC2_TRAIN_NSO | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1896 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_B_DAVIS_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9512 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_BASTEN_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.7783 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_BOSQUESW_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8277 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_BOSQUESW_CC2_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3883 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_BRAUNIG_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3339 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_BTE_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.5165 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_BVE_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.6992 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_BYU_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.689 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_CAL_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3587 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_CBECII_CC3_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4556 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_CBY4_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8678 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_CCEC_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.6078 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_CHE_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.89 | 100.1661 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_CVC_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9343 | 100.2163 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_DDPEC_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.7937 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_DIB_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7667 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_DUKE_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9523 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_ETCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.7046 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_FERGCC_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.5604 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_FLCNS_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4933 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_FREC_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.2638 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_FREC_CC2_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3388 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_FRNYPP_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.1148 | 100.0038 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_FRNYPP_CC2_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.1316 | 100.0031 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_FTR_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.7686 | 100.9382 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_GUADG_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.0552 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_GUADG_CC2_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.0343 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_INGLCOSW_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.277 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_JACKCNTY_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.919 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_JCKCNTY2_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.349 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_KMCHI_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.1215 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_KMCHI_CC2_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.1455 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_LGE_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4801 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_LOSTPI_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.484 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_LPCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.7425 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_LPCCS_CC2_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.4811 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_NEDIN_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.983 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_NUECES_B_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.0529 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_OECCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9671 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_OECCS_CC2_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9772 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_PANDA_S_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.7825 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_PANDA_T1_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.8445 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_PANDA_T2_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.875 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_PSA_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8464 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_PSG_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.7007 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_QALSW_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1054 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_QALSW_CC2_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0784 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_RAYBURN_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1558 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_TEN_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2389 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_TGCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.2147 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_THW_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4835 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_THW_CC2_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4833 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_TNSKA_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8759 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_TXCTY_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5421 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_VICTORIA_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6425 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_WCPP_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.3169 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_WHCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.0492 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E_WHCCS2_CC2_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.9743 | 100.1345 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E5DVA1C1_1_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 104.0813 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E5DVA1C1_1_B_2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 102.1294 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | E5P4A1C1_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0383 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ELMAX_POI_Con | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3103 | 100.0109 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ELPATR_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.14 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4418 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ERC1_BZR-SWN_BRZ-CLM | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3097 | 100.0653 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ERC1_RTR-BZR_RTR-ANG | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5684 | 101.716 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ERIKA_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8634 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3151 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_000099BENHURUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3359 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_000575JCKCNTY5UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.6074 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_000579JCKCNTY8UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.2829 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_000971PRUITT_8US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2883 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_001777PARIS_8US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2984 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_001877MITCHBND_5UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4732 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_003134RICHLND1_5UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8649 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_003134RICHLND1_5UN2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8649 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_003306STEKLY_DAM_5US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.718 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_003321REDLAND_5UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.988 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_003377LITTLEPOND_5US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0868 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_003391JEWETT_N5US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2791 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_003420TEMP_PEC__8US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4316 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_003478NAVARRO1_8US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4548 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_003706GIBSON_5US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4265 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_003707CANNON_8US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4547 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_003717TORTOISE_5US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3946 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_003717TORTOISE_5US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1916 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_005660ORANGEGRVSW8US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0502 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_006100OKLA7AUC0 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.65 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_006111RILEY7BUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7138 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_007041L_JOHNDU5_1YUN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5659 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_007044L_MARION5_1YUN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8832 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_007048L_GARFIE5_1YUN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.23 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_008249ANGSTRM7AUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5035 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_008573BONILLA7AUW1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5217 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_008707DRYFRIOUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2332 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_010012METEOR_5US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.5347 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_023906AJSWOPE_5US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5269 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_023908DEAFSMITH_5US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3599 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_023909WALLABY_5US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8052 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_023912OGALLALA_5US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5274 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_023913KRESS_5US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4447 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_040000CEDARP_B345AUC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.7687 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_040700GRNBYU__B345UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9605 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_040710GRNBYU_POI8AUN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8178 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_040890DANEK__POI_8UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0201 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_043990ELMATO_POI_5US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1888 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_045500T_H_W__POI_5UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.2805 | 100.1783 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_045515T_H_W__POI_8UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.2926 | 100.2089 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_047170H_O_C__POI_8UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0115 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_048262SOWYCK26TP_8UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1041 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_059904COTTONWOODUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4752 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_060700GAUSS7AUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.6066 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_060716SGSA4AUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0332 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_068004PHNTMHLUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4659 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_068014OPENSKYUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.417 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_068025WRANGLERUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4836 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_068051REATAUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4882 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_079000GRAYUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.6853 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_079000GRAYUW1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9677 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_079007YELLOWWOLFUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5788 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_080039LUCERO7AUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.79 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_080039LUCERO7AUS2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5541 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_080219LOBO7AUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6803 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_080219LOBO7AUS2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3003 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_080355DELSOL7AUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3284 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_085000N_SHARPE7AUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1196 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110013WAP_WAP_G3UN3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8251 | 100.5675 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110014WAP_WAP_G4UN4 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.6091 | 102.3997 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110015WAP_WAP_G5UL5 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2344 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110016WAP_WAP_G6UL6 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3318 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110017WAP_WAP_G7UL7 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.968 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110018WAP_WAP_G8UL8 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8941 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110071CBY_CBY_G1UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9239 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110072CBY_CBY_G2UN2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.8673 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110351STP_STP_G1UU1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9784 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110352STP_STP_G2UU2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9697 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110521CAL_CALGT1UPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1013 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110577PSA_PSA_G7UPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0796 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110661CHE_CHEGT1UPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1606 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110662CHE_CHEST1UPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3918 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110701LHM_CVC_G4UPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3393 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110731BTE_BTE_G1UPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4472 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110732BTE_BTE_G2UPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2111 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110733BTE_BTE_G3UPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.211 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_110734BTE_BTE_G4UPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.211 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_112091SBE_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0818 | 100.7241 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_112351OLDHCKRY_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0797 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_112431TAV_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.2287 | 101.3627 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_112432TAV_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3413 | 100.6057 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_112491JAY_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.013 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_113051GARCITAS_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2412 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_113111LUNIS_CK_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.583 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_113921PARLIMNT_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8547 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120041MLSES_UNIT1UL1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.9594 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120042MLSES_UNIT2UL2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.995 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120043MLSES_UNIT3UL3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.0062 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120051DAN_DANSBYG1UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1859 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120071TNP__TNP_O_1UL1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4311 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120072TNP__TNP_O_2UL2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4311 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120131OGSES_UNIT1AUL1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.4205 | 100.3822 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120132OGSES_UNIT2UL2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.4206 | 100.3821 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120141SCSES_UNIT1AUN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4723 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120142SCSES_UNIT2UN2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3875 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120151TRSES_UNIT6UN6 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9284 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120391STARRSOL_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0554 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120441BR_ARROW_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1139 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120442BR_ARROW_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3393 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120591STAM_SLR_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.34 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120691GLENPINE_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0813 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120821HOPKINS_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3315 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_120871AZALEA_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3087 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_132311ECEC_G1UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4741 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_132312ECEC_G2UN2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4741 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_132431SIRIUS_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0789 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_132481RIGGINS_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3228 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_132731BOOTLE_UNIT1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1084 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_132781CASLGP_UNIT1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4216 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_132881LMESASLR_G1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0161 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_132941SPTX12B_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.31 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_133341W_PECOS_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0282 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_133841WAYMARK_W1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4132 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134091OBERON_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4206 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134141JUNO_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2973 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134142JUNO_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1974 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134241TAYGETE_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.165 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134243TAYGETE_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1802 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134343LGDRAW_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1303 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134441LAPETUS_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0104 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134591QUEEN_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0255 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134592QUEEN_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0255 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134593QUEEN_S3US3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0012 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134594QUEEN_S4US4 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0498 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134701TYGTEII_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0455 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134702TYGTEII_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0456 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134751FOWLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2882 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134801PROSPERO_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.275 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134802PROSPERO_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2454 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134901GREASEW_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1249 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134902GREASE_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1527 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134951EUNICE_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.454 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_134953EUNICE_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6845 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_135011TI_SOLAR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2149 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_135012TI_SOLAR_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.186 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_135111ARAGORN_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.48 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_135181PRSPERO2_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1327 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_135182PRSPERO2_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1324 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_135321REDBARN_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6059 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_135501RDOSLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5012 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_136101BLUESKY_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0468 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_136341TRBNT_PV_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0138 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_136441SWIFTAIR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2697 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_141607AEEC_5UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7916 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_141609ELK_G3UN6 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6754 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_141662SOLARA_UNIT1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0754 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_142811MISAE_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0863 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_142812MISAE_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0734 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_143111NOVA1SLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1016 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_143112NOVA1SLR_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1016 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_143116SRNOVA2_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4806 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_143261CONGLI_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1004 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_143312AZURE_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2484 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_143571SAMSON_3_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0851 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_143572SAMSON_3_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0851 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_143621SAMSON_1_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0853 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_143622SAMSON_1_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0853 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_143701DELILA_1_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.197 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_143702DELILA_1_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.197 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_143961MISAE2_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9314 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_144011BRSFORK_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9534 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_144064INERTIA_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4733 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_144161NOVA2SLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4545 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_144211HRNTSLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.2537 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_144261EIFSLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5999 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_144311FRYE_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.648 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_144312FRYE_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.648 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_144511TROJAN_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2926 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_144561BAKE_SLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5913 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_144562BAKE_SLR_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5912 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150021MCSES_UNIT6UN6 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3858 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150022MCSES_UNIT7UN7 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3644 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150023MCSES_UNIT8UN8 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.3974 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150041GRSES_UNIT1UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0222 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150042GRSES_UNIT2UN2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9484 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150051HLSES_UNIT3UN3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9908 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150052HLSES_UNIT4UN4 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.4178 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150053HLSES_UNIT5UN5 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.392 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150082OLIN_OLING_2UN2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2393 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150083OLIN_OLING_3UN3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5049 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150084OLIN_OLING_4UN4 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0637 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150091LHSES_UNIT1UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.128 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150092LH2SES_UNIT2UN2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.0479 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150101LEG_LEG_G1UL1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.2872 | 100.3215 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150102LEG_LEG_G2UL2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.3555 | 100.3407 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150111CPSES_UNIT1UU1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.5172 | 100.2247 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150112CPSES_UNIT2UU2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.5032 | 100.2168 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150132MIL_MILLERG2UN2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2333 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150133MIL_MILLERG3UN3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7749 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150134MIL_MILLERG4UN4 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1175 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150135MIL_MILLERG5UN5 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1175 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150151MDANP_CT1UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0318 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150152MDANP_CT2UN2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1331 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150153MDANP_CT3UN3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1422 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150154MDANP_CT4UN4 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1415 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150155MDANP_CT5UN5 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.108 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150156MDANP_CT6UN6 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1201 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_150741SCES_UNIT1UL1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.7157 | 100.0652 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_151371LILY_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2538 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_151421STRATEGC_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2215 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_151551VISION_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1522 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_151751RADN_SLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2619 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_151752RADN_SLR_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2804 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_152081NOBLESLR_R1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2674 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_152082NOBLESLR_R2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1676 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_152181SUNVASLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2453 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_152231MARKUM_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2289 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_152331FILESSLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2249 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_152431MERCURY_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.461 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_152582ESTONIAN_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.031 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_152731FENCESLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1439 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_153141PORT_SLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7564 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_153241ANGUSSLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0117 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_153291BIGELM_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0927 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_153381FIVEWLLS_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3708 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_153382FIVEWLLS_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0895 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_153532ELIZA_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2963 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_153631DORADO_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3999 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_153681HALO_SLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0079 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_153731TNS_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0453 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_153732TNS_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0458 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_153781JAGUARSP_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8759 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_153861TOKIO_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3129 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_153911PNGT1_PV_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.7237 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_153961GAIA_SOL_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2318 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_154011MIDPOINT_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0151 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_154061DIVER_PV_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2161 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_154161LANGER_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6746 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_154221ASHCRKSL_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4596 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_154281CLINGHAM_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0811 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_154331CMPDREPV_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4809 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_160101B_D_B_DAVIG1UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0502 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_160131SAN_SANMIGG1UL1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4894 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_160151INGLCOS_CTG1UPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3681 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_160152INGLCOS_CTG2UPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3681 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_160153INGLCOSW_STGUPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3585 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_160201LGE_LGE_GT1UPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3072 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_160202LGE_LGE_GT2UPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.301 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_160261CCEC_GT1UPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1915 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_160262CCEC_GT2UPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1915 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_160263CCEC_ST1UPE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2562 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_160291PENA_UNIT1UW1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0294 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_160391PAP1_PAP1UW1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0845 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_160392COTTON_PAP2UW1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1805 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_160741LV1_LV1AUW1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1773 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_160742LV1_LV1BUW2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.18 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_160982CAMWIND_G1UW1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0665 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_161451CHAWND_UNIT1UW1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0078 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_161501MIDWIND_UNIUW1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0505 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_161651PATWND_UNIT1UW1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2621 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_161951STELLA_W1UW1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1612 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_162251CHALUPA_W1UW1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.09 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_162541MCLNSLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3135 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_162791HRZN_SLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.288 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_162841ELARA_SL_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0321 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_163021NEBULA_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1005 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_163071ALGODON_W1UW1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0707 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_163221CORAZON_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2926 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_163321SPARTA_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.089 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_163411ELSAUZ_W1UW1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0134 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_163521PEREGRN_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7457 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_163641CHARGER_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1416 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_163691REDONDA_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4913 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_163881TULSITA_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4697 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_163931OUTPOST_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4483 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170071GID_GIDEONG1UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2531 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170072GID_GIDEONG2UN2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2694 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170073GID_GIDEONG3UN3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4741 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170101FPPYD_FPP_G1UL1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.7685 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170102FPPYD_FPP_G2UL2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.7486 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170103FPPYD_FPP_G3UL3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8768 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170126CALAVER_JKS2UL2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.5764 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170191HAY_HAYSENG1UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6749 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170192HAY_HAYSENG2UN2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7783 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170193HAY_HAYSENG3UN3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7728 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170194HAY_HAYSENG4UN4 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6913 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170521E_BLACK_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1574 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170601BIG_STAR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0545 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170671CACHENA_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.6996 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_1707717RNCHSLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0734 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170821EBELLSLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5819 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170825EASTBELL_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.194 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170901SHLA_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0887 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_170951SHLA_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0887 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_171021AURE_SLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4177 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_171091MPP_N1UN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5166 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_171111MANDORLA_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6437 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_171161SYPBRNCH_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6643 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_182151EGROVESL_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0713 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_182251HOLSTN_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.008 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_182252HOLSTN_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0085 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_182303PHOEBE_3US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.143 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_182305PHOEBE_5US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1574 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_182501RAMBLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4661 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_182601NORTON_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1112 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_183172GALLOWAY_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.696 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_183221GALLOWAY2_S1US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0347 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_183351RATLIFF_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2683 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_183401JADE_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2711 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_183402JADE_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2902 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_183451CROWDEDS_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5442 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_183521ANDMDSLR_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2713 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_183522ANDMDSLR_S2US2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2897 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_183571SUNRAY_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.325 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_183621ZIER_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2207 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_183681TENNYSON_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2239 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_183781ANG_PV_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4455 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_5920EASTDCTIE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.0649 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_6103NORTHDCTIE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8886 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888839BAS_RANCH_POIUC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.7914 | 100.1038 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888840SKULLCREEK_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.147 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888841ELMAX_POIUN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.1713 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888842IRON_BELT_POIUB1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0406 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888845DRY_CREEK_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4308 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888848BARRETT_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1413 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888851TRIFECTA_POIUN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.4412 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888854PINEFOREST_POIUB1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.103 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888854PINEFOREST_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0042 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888856HOLLY_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4601 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888856HOLLY_POIUS2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7587 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888857OYSTER_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.621 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888858ARGENTA_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8182 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888859HIGHNOON_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3662 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888861LEON_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4516 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888865MALDIVES_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5309 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888866HANSON_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3914 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888867INDIGO_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1067 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888870BTTM_GRSS_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8893 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888871ELPATR_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1396 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888872SKYSLY_POIUN1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5013 | 100.8246 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888872SKYSLY_POIUN2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8514 | 100.8317 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888874VIKING_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9551 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888875THRESLR_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0358 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888877GLASGOW_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5428 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888878ERIKA_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5418 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888879BLUBIRD_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.2602 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888881SOLAC_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.299 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888882BUZIOS_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6946 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888883QUANT_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2764 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888885GALAC_POIUS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.529 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_888888FEWELL_S1US1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.29 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G_RIO_TRAIN | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.5617 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | G8DVA1C1_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 102.9085 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | GALAC_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5706 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | GLASGOW_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5003 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | GRAHAM UNIT 2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9484 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | HANSON_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5573 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | HIGHNOON_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4474 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | HOLLY_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9294 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | INDIGO_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.148 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | IRON_BELT_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.175 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | J5CT1_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.347 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | J5CT2_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3534 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | J5CT3_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3545 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | J5GSU1_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.347 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | J5GSU2_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3534 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | J5GSU3_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3545 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | J5GSU4_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1718 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | J5LCA1C1_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.5644 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | J5ST1_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1718 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | JW-CROCKETT (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2399 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | JW-CROCKETT (SINGLE B TO B)-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2399 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_000842GPL_KINGMTSW-000843GPL_KINGMTTPC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5219 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.2578 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_000860GPL_GIRVINSW-136341TRBNT_PV_S1C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0138 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_000902POES31569-000981SPNCRINT69C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3318 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8114 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_001141HOLTSS_8-132313ECEC_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3991 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_001163LAMESA_8-132883LMESASLR_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2708 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_001444BROWN_5-151756RADN_TLINEC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0322 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_001466BYRDSW_5-143525AJAX_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0232 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_001685FARMVLSW_5-011689CYCLONE_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0291 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.42 | 100.2612 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1698 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_001730W_KRUM_5-152087NOBLESLR_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0662 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_001839STONCRK_8-140002SHER1_TLC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.774 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.4601 | 100.0876 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_001906VENUS_S5-015201FORBESR2_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0066 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.7507 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5299 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_002217BATCHLRD_8-003159ELROD_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4418 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.019 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.019 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0217 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3542 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.1292 | 100.0038 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.1244 | 100.0031 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4193 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0569 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_003133RICHLND2_5-003199CALFRESTN_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3346 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_003134RICHLND1_5-003186CALPFREST_5C2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.2652 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_003159ELROD_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3624 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1718 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_003389FORTSMITH_5-152333FILESSLR_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2325 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4055 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_003490LNGPRAIRIE_8-152736FENCESLR_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.671 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_003702RIESEL_8-153195CORAL_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2713 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_003711BALE_S5-153733TNS_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5692 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.7756 | 101.4219 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005068CACHENA-005323OLD_HCKRY_5C2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.7293 | 100.4922 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005133ELMCREEK-005380SHAULAC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.4248 | 100.7934 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005323OLD_HCKRY_5-005915SO_TEX__345AC2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.8516 | 100.1564 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005380SHAULA-005915SO_TEX__345AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.8806 | 100.1656 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005502RAYBURN8-005513RAYBURNPLNT8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1558 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005761PAREDESSW8-160981CAMWIND_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0856 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005779REDSWTAP8-005784REDGATESW8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6735 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005779REDSWTAP8-161031REDGATE_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6735 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005866PALODUROSW8-005890ELARA8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0323 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005895PEARSALLSUB8-005896MORROWSW8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2872 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005895PEARSALLSUB8-005897HORIZONSW8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2883 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005895PEARSALLSUB8-058959PEARSALLSCB8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5393 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005897HORIZONSW8-162793HRZN_SLR_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2883 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005915SO_TEX__345A-008715RADIANT7AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.452 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005915SO_TEX__345A-042400REFUGE_POI_5C27 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.6625 | 102.2981 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005915SO_TEX__345A-042530JONCRK__B345C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3459 | 100.9806 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.1677 | 102.3675 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_005915SO_TEX__345A-088800HOUDINI7AC39 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4118 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_006015MADDUX4A-183353RATLIFF_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2683 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_006111RILEY7B-141351ELECTRA_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0849 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_006216BLF_CRK4A-180455BUFF_GAP_2_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2341 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_006562FDRAN4A-136103BLUESKY_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0472 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_006601RIOPECOS4A-076601L_HORSCR8_1YC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0707 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_006630FTST4A-132482RIGGINS_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3244 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_006802RY_RYMOND_RC-120692GLENPINE_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0813 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_006903BOZE-151372LILY_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3275 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.7783 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_007055L_FPPYD25_1Y-009073HOLMANC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1191 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_007077L_AMOSCR5_1Y-182777MAVCRK_W_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1852 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_007077L_AMOSCR5_1Y-183171GALLOWAY_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1917 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_007126L_FERGUS8_1Y-180015FERGGT1_1_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4899 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_007126L_FERGUS8_1Y-180016FERGGT2_2_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4899 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_007126L_FERGUS8_1Y-180017FERGST1_1_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.567 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_007279L_MULDOO8_1Y-1707737RNCHSLR_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4511 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_007304L_WIPOPA8_2Y-007307L_PINECR8_1YC2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0168 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_007307L_PINECR8_1Y-007309L_WIPOPA8_1YC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0168 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_007337L_KIMBRO8_1Y-170523E_BLACK_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1574 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_007389L_PINNAC8_1Y-135019TI_SOLAR_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9049 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_007389L_PINNAC8_1Y-135113ARAGORN_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.48 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008102EL_CAMPO4A-008679ARROZ4AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5067 | 100.4671 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008102EL_CAMPO4A-078104L_RICEBI8_1YC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3296 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008104LANCTYPM4A-008127LAN_CTY4AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2554 | 100.2492 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008104LANCTYPM4A-008679ARROZ4AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2468 | 100.2418 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008117GANADO4A-008118EDNA4AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0289 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008117GANADO4A-008192PULSAR4AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0372 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008121BLESSING4A-008125LOLITA4AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0315 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008127LAN_CTY4A-008130LAN_CTY4BCS1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.7561 | 104.8621 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008144SEADRFTC4A-008189TUNGSTEN4AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0028 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008144SEADRFTC4A-080065MELNCRK4AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0035 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008172VICTORIA4A-110883VIC_SU5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0225 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008172VICTORIA4A-110884VIC_SU6C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1213 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008209SHAKEPOI4A-162543MCLNSLR_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3135 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008318RIOHONDO7A-162745LMJDSW_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4187 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008319RIOHONDO4A-160750LV1_AB_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8499 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008380NEDIN4A-160234NEDIN_1_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6336 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008380NEDIN4A-160235NEDIN_2_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6336 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.215 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008455LONHILL7A-008579KATOEN7AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2259 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008458B_DAVIS4A-160105B_DAVIS_1_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0502 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008458B_DAVIS4A-160106B_DAVIS_2_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2005 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008458B_DAVIS4A-160107B_DAVIS_3_9C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3652 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008458B_DAVIS4A-160108B_DAVIS_4_9C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3652 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008640KELVIN4A-088640CHLPAPOI4AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1737 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008663ELSUZPOI7A-163415ELSAUZ_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4883 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008715RADIANT7A-008728COBRA7AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.6437 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008728COBRA7A-081003HABER7AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.9012 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008795ROMA_SW4A-088795STARRPOI4AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0554 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008963HEC4A-008981HECGT14AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2978 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008963HEC4A-008983HECST14AC3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4105 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008980FRONTERA4A-160180FRONT_EC_C1TC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4457 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008980FRONTERA4A-160181FRONT_EC_C2TC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4457 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_008980FRONTERA4A-160182FRONT_EC_STTC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4861 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_009043CISTERN-009074LYTTON5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0476 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_009073HOLMAN-888870BTTM_GRSS_POIC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.5753 | 101.7658 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_011083RIVERTON_8-133342W_PECOS_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0282 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_011270DOGHOUSE_5-023876CLEARFRK_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.2179 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_011270DOGHOUSE_5-134805PROSPERO_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0015 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_011270DOGHOUSE_5-135183PRSPERO2_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7556 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_011273NELSON_8-135503RDOSLR_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5012 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_011406CENTBLUF_5-182255HOLSTN_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5038 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_011418TECUMSEH_5-151808VORTEX_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.149 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_011688THORNTRE_5-143625SAMSON_1_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.6599 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_011688THORNTRE_5-143705DELILA_1_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.2516 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_015200FORBESR1_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1813 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2975 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_023900ALIBATES_5-140653GRANDVW1_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2364 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_023906AJSWOPE_5-140442SSPURTWO_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1252 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_023910WINDMILL_5-140753HRFDWIND_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3803 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_023920ABERNATH_5-141607AEEC_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9187 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_023922WHITERVR_5-141402SPLAIN2_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0462 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_023924FARMLAND_5-133641TAHOKAW_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3988 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_038745TNATTWATER1-111971TOPAZ_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.752 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_039500TNWCOLMAIN1-039530TNWCOLLOCL1C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0088 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_039530TNWCOLLOCL1-039560TNANGLETON1C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0982 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_039600TNBRAZORIA1-039700TNSWEENY__1C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0897 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_039600TNBRAZORIA1-043170RETREV__B138C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9211 | 100.8702 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_039700TNSWEENY__1-039703TNFM524___1C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1434 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_040000CEDARP_B345A-040240CENTER_POI_5C97 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0927 | 100.2489 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_040000CEDARP_B345A-110076CBY4_1_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8678 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_040010CEDARP_B138A-049201GENGBY2_02_8CGL | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.8673 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_040715GRNBYU_POI8B-049211GENGBY7_08_8CGL | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2103 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_040850JORDAN__B345-040900KING____B345C97 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1534 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_040850JORDAN__B345-046100N_BELT__B345C99 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1787 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_040900KING____B345-046290RTHWOD__B345C74 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0759 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_040900KING____B345-046290RTHWOD__B345C75 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0759 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_041000LYDELL_POI_8-110664CHE_1_8C01 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1606 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_041000LYDELL_POI_8-110665CHE_2_8C04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3918 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042010P_H_R___B138-111131BAC_8C92 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5921 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042030SAMARI__B138-042050CLUTE___B138C26 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.1876 | 103.9769 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042030SAMARI__B138-042110ANGLTN_POI_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.1864 | 103.9756 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042050CLUTE___B138-042190BIPORT_X82B8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9193 | 100.5337 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042050CLUTE___B138-043150RIWOOD_X82B8C82 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.9796 | 103.7724 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042050CLUTE___B138-043240SINTEK_X26B8C26 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.2963 | 103.0583 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042100HUDSON_POI_8-042940MONSAN_POI_8C04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.5841 | 104.9659 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042100HUDSON_POI_8-888849CLUTCH_CITY_POIC04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.0609 | 106.433 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042110ANGLTN_POI_8-043150RIWOOD_X82B8C82 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.0096 | 103.8028 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042110ANGLTN_POI_8-043380W_COL__POI_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.2277 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042150BASF___POI_8-042210BRZPRT_S02_8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 117.3626 | 121.9781 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042150BASF___POI_8-042810HOFMAN_X02B8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 121.549 | 126.1398 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042190BIPORT_X82B8-043335OYSCRK_POI_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6687 | 100.2824 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042210BRZPRT_S02_8-042215COPPER_X02B8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 114.3229 | 118.9517 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042215COPPER_X02B8-042540JONCRK__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 112.0793 | 115.5792 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042400REFUGE_POI_5-042440HAWKIN_POI_5C27 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.6274 | 101.2546 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042410BURKE__POI_8-042980NASH___S02_8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 110.3369 | 111.5468 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042410BURKE__POI_8-888850LONG_POIC02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.0648 | 105.3642 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042420BEASLY_POI_8-044190E_BERN__B138C60 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.6096 | 111.0977 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042420BEASLY_POI_8-044541ORCHRD_T60_8C60 | 138 | 138 | Branch Amp | 1137.9656 | 106.532 | - | - | - | 116.1362 | 120.4232 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042420BEASLY_POI_8-112433TAV_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.0405 | 102.9179 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042440HAWKIN_POI_5-042530JONCRK__B345C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8034 | 100.4442 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042570ARCHER_POI_8-044430MANVEL_S26_8C26 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.1975 | 106.6011 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042810HOFMAN_X02B8-042880LKJACK_S02_8C02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 121.8213 | 126.4103 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042880LKJACK_S02_8-043170RETREV__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | 100.8948 | - | - | - | 125.6276 | 130.1903 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042940MONSAN_POI_8-043070PETSON_X04B8C04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.0442 | 105.4221 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042960MUSTNG_S04_8-043500WEBSTR_B138AC&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 110.6138 | 109.9008 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042980NASH___S02_8-888852LIATRIS_POIC02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 109.9541 | 111.165 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_042985DYANN__POI_8-043570WHARTN__60B8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | 106.0863 | - | - | - | 125.7647 | 124.1899 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_043010NEWGLF_S60_8-043190S_LANE__B138C60 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 123.689 | 116.7091 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_043010NEWGLF_S60_8-043340GLFTIE_POI_8C60 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 124.1568 | 117.1761 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_043035OASIS___B345-043060SPEDWY_POI_5C18 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.4752 | 101.385 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_043035OASIS___B345-043180SAVANA_POI_5C27 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8715 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_043035OASIS___B345-044000W_A_P__POI5AC18 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8096 | 100.1957 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_043035OASIS___B345-044000W_A_P__POI5AC99 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8038 | 100.1895 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_043070PETSON_X04B8-044890SNUG___POI_8C04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.266 | 105.6444 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_043170RETREV__B138-043380W_COL__POI_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9213 | 102.8244 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_043240SINTEK_X26B8-043365CAMDEN_X26B8C26 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.8777 | 102.6344 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_043335OYSCRK_POI_8-043345GLOBAL_X82B8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2628 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_043345GLOBAL_X82B8-043360VLASCO__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0678 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_043360VLASCO__B138-043365CAMDEN_X26B8C26 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.1805 | 101.9277 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_043570WHARTN__60B8-044150HNGFRD_POI_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | 103.6487 | - | - | - | 123.1702 | 121.7173 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044000W_A_P__POI5A-044160WOLF___POI_5C64 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0528 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044000W_A_P__POI5A-044500OBRIEN_B345AC98 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.5982 | 101.0667 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044000W_A_P__POI5A-044500OBRIEN_B345AC99 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.5982 | 101.0667 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044000W_A_P__POI5A-049205GENWAP6_06_5CGL | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3318 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044000W_A_P__POI5A-049206GENWAP7_07_5CGL | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.968 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044005W_A_P__POI5B-044070WHALEY_POI_5C72 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.1568 | 100.8884 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044005W_A_P__POI5B-047000BELAIR__B345C50 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1462 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044005W_A_P__POI5B-047300JENETA__B345C64 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7691 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044005W_A_P__POI5B-049207GENWAP8_08_5CGL | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8942 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044010W_A_P__POI8A-044015W_A_P__POI8BCR1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.0467 | 100.8005 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044010W_A_P__POI8A-044015W_A_P__POI8BCR2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.0467 | 100.8005 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044010W_A_P__POI8A-044342IMPERL05T3_8C05 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8515 | 100.197 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044015W_A_P__POI8B-044170CRABB__S09_8C09 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 119.2468 | 113.2071 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044015W_A_P__POI8B-044173CRABB_80T3_8C80 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3255 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044015W_A_P__POI8B-049212GENWAP3_03_8CGL | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8251 | 100.5675 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044030ARCOLA_S82_8-044390KARSTN__B138C82 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0034 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044040BAILEY_POI_5-044060BLUE___POI_5C72 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.7804 | 102.842 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044060BLUE___POI_5-044220JULIA__POI_5C72 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.1508 | 103.4595 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044070WHALEY_POI_5-044090CDRCRK_POI_5C72 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.7096 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044070WHALEY_POI_5-112615ROW_5C01 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2156 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044140CLODIN__B138-044592ROARK_25T8_8C25 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.731 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044150HNGFRD_POI_8-044190E_BERN__B138C60 | 138 | 138 | Branch Amp | 1137.9656 | 113.1521 | - | 104.8346 | - | 130.6976 | 132.296 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044150HNGFRD_POI_8-112094SBE_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0818 | 100.7241 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044170CRABB__S09_8-044570READNG_S09_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 113.3725 | 107.3731 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044200HILLJE__B345-044220JULIA__POI_5C72 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3209 | 103.9107 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044230FLEWLN__B138-044510OBRIEN_B138AC&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.524 | 101.6458 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044260FRANZ___09B8-044910ZENITH__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.0962 | 101.6406 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044280FTBEND__B138-044570READNG_S09_8C09 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 109.5097 | 103.5301 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044280FTBEND__B138-044615ROSNBG_S60_8C60 | 138 | 138 | Branch Amp | 1137.9656 | 102.905 | - | - | - | 112.3427 | 116.638 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044342IMPERL05T3_8-044670STAFRD_S05_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6842 | 100.0474 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044410KARSTN_C26_8-048173ALVIN_26TP_8C26 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.8563 | 105.2578 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044430MANVEL_S26_8-048173ALVIN_26TP_8C26 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.0401 | 105.4413 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044450MASON__S25_8-044510OBRIEN_B138AC25 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.2901 | 101.4496 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044540ORCHRD_S60_8-044615ROSNBG_S60_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | 105.0696 | - | - | - | 114.5338 | 118.907 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044590ROARK__S25_8-047310JENETA__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1267 | 100.3426 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044650SMTHRS_POI_5-047000BELAIR__B345C98 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1343 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044650SMTHRS_POI_5-112419RABBS_5C01 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9217 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044670STAFRD_S05_8-044760WCHASE_S05_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2112 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044840STONEL__B138-045880HOCKLY__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.551 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_044840STONEL__B138-046511TOMBAL_T66_8C66 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8381 | 101.0681 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_045500T_H_W__POI_5-046100N_BELT__B345C97 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0286 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_045500T_H_W__POI_5-049204GENTHW5X05_5CGL | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5482 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_045515T_H_W__POI_8-049202GENTHW3X03_8CGL | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4835 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_045515T_H_W__POI_8-049203GENTHW4X04_8CGL | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4833 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_045971KUYDAL74T1_5-046290RTHWOD__B345C74 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2225 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_045971KUYDAL74T1_5-046500TOMBAL__B345C74 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1656 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_046510TOMBAL__B138-046511TOMBAL_T66_8C66 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.5007 | 101.7271 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_046600WHITOK__B345-047300JENETA__B345C72 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0658 | 100.0619 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_047014BELAIR24T6_8-047442ULRICH_T24_8C24 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0027 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_047150H_O_C___B138-047175H_O_C__SB138CBR | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5031 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_047170H_O_C__POI_8-048262SOWYCK26TP_8C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3637 | 100.6706 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_047170H_O_C__POI_8-111800PRO_8C01 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7334 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_047175H_O_C__SB138-047660GARROT__B138C&1-MS | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.415 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_059900LONG_DRAW-132114SRWE1_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.041 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_059903BEARKAT-132993BEARKAT_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0396 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_059906LONGDRAW_138-134145JUNO_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9785 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_059906LONGDRAW_138-134342LGDRAW_S8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6103 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_059909NOVA_138-059998NOVA8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.5475 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_059909NOVA_138-143115NOVA1SLR_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.6209 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_059909NOVA_138-144163NOVA2SLR_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4543 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_059911MHOS-183406JADE_HI_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2284 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_060011NEBULA7A-183525ANDMDSLR_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0271 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_060383LINTERNA4A-060385SOLSTICE4AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0197 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_060383LINTERNA4A-132331REROCK_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3121 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_060387HENDRICK4A-141663SOLARA_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0755 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_060393PIGCREEK4A-134245TAYGETE_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8452 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_060393PIGCREEK4A-134705TYGTEII_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5847 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_060451GARNET4A-182603NORTON_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1112 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_060464AZUREPOI7A-060514CLEARCRO7BC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6929 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_060504TESLA7B-142815MISAE_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6484 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_060791PERIGEE7A-143222APOGEE_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0634 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_061001JIMTREEC7A-140383BLSMT1_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1579 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_068001CLAYTON_345-182455WHITHRSE_4_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.096 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_068090SAMSW-068092LIBERTYC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3077 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_068092LIBERTY-152433MERCURY_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8788 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_071050L_BITTCR5_1Y-180161SWEETWN4_1_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2239 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_076002L_BAKERS5_1Y-132732BOOTLEG_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1084 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_076002L_BAKERS5_1Y-133843WAYMARK_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4133 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_076002L_BAKERS5_1Y-135327REDBARN_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7416 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_076005L_SCHNDR5_1Y-132632SANTRITA_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3549 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_076005L_SCHNDR5_1Y-134651WHMESA_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2053 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_076015L_CEDACA5_1Y-134512HILO_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3662 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_076040L_CASTIL8_1Y-132783CASL_GAP_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4347 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_076040L_CASTIL8_1Y-132943SPTX12B_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3434 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_076090L_DIVIDE5_1Y-180759CAPRIDG4_1_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3879 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_076090L_DIVIDE5_1Y-182727AVIATOR_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2431 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_076601L_HORSCR8_1Y-182154EGROVESL_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0713 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_078103L_NADA8_1Y-078104L_RICEBI8_1YC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2727 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_078255L_PINTCR8_1Y-183623ZIER_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2679 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_079000GRAY-140473MIAMI_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0182 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_080071ZORILLO7A-080076AJO7AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3518 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_080071ZORILLO7A-080171SARITA7AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4077 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_080072STELPOI7A-080076AJO7AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1622 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_080072STELPOI7A-161953STELLA_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1617 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_080171SARITA7A-160299BAFFIN_2_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4073 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_080219LOBO7A-163223CORAZON_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4922 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_080220CENIZO7A-161105BORDAS_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0092 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_080259PELICAN4A-160394COTTON_1_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1805 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_080259PELICAN4A-160395PAP1_1_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0845 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_080260GILA4A-160095NUECES_B_2_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3695 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_080260GILA4A-160096NUECES_B_3_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.368 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_080309LASPULGA4A-160694REDFISH_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1908 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_080503SANTASW4A-085001N_SHARPE4AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3314 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_080503SANTASW4A-161455CHAWIND_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3312 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_080509LADKPOI7A-161753BBREEZE_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.256 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_081003HABER7A-081005ACME7AC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5692 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_085008PATPOI7A-161653PATWIND_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2682 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_088173JCKSLPOI4A-163575JACKALOPE_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1567 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_088573ERAYPOI7A-162151EASTRAY_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1515 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_088574WRAYPOI7A-162695ELTRUENO_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3014 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_088606JRVKPOI7A-162005KNKWA1_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.184 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_088640CHLPAPOI4A-162253CHALUPA_138C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1737 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_088656ASTRSPOI4A-163023NEBULA_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1007 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_088670BLACKPOI7A-162915BLACKJAK_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3093 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_131753PC_SOUTH_1_5-131754PC_SOUTH_2_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1419 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_131753PC_SOUTH_1_5-131755PC2_SWYD_1_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3223 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_140753HRFDWIND_5-141053JRDWIND_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0325 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_143575SAMSON_3_5-143625SAMSON_1_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6549 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_143705DELILA_1_5-143757DELILA_2_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.921 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_160298BAFFIN_5-160299BAFFIN_2_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1588 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_160750LV1_AB_8-160751LV1_A_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1773 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_160750LV1_AB_8-160752LV1_B_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.18 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_180754DIVIDE_1_8-180757CAPRIDGE_3_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3302 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2483 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_888849CLUTCH_CITY_POI-042960MUSTNG_S04_8C04 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 110.9717 | 110.2536 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_888852LIATRIS_POI-044010W_A_P__POI8AC02 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 115.8864 | 124.8941 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1698 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_888870BTTM_GRSS_POI-044200HILLJE__B345C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.0199 | 100.5827 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L_888877GLASGOW_POI-068091NAVARROC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2606 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L1000027 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1622 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L1000032 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1515 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L10005-2B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0468 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L10006-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3811 | 100.2364 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L10010006-1B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2511 | 100.2497 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L10010116 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2784 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L10010434_MODIFIED_BY_MZ | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.268 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L10010717 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2978 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L10011226 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0697 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L10011585 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4077 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L10011690 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4123 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L10011910-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.418 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L10012087 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2682 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L10012091 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.184 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L10012100 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0225 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L10012105 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1213 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L10012900 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.7561 | 104.8621 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L10012915 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3314 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L11000047 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3014 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L11000090 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4913 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L11000095 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.256 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L11000105 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.177 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L11000171 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1737 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L201000169 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8518 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | L20255426 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8518 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | LAKE CREEK - RATTLE SNAKE 345 KV WITH SANDY UNIT (SINGLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.7157 | 100.0652 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | LCRA TSC_BAKERS_CEDACA_DC | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1952 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | LCRA TSC_CEDACA_NOELKE_DC_1A-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.053 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | LCRA TSC_CEDACA_NOELKE_DC_1A-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0011 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | LCRA TSC_CEDACA_NOELKE_DC_1B-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0529 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | LCRA TSC_CEDACA_NOELKE_DC_1B-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0011 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | LCRA TSC_T21451 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3302 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | LCRA TSC_T21457 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4475 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | LCRA TSC_T255_TAE3121_1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1095 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | LCRA TSC_T451_T682 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0979 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | LCRATSC_5_HORNSB_EUCLID | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0914 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | LCRATSC_6_EUCLID_JOHNDU | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5896 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | LCRATSC_7_JOHNDU_ZORN__ | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1259 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | LEON_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.449 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | LIATRIS_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 110.7999 | 112.3982 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0004 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2945 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | M10000254106503-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0393 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | M10000271115801 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9388 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | M100052100072 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3541 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | M105311105321 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4804 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | M115851115803 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3518 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | M128103100534 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0775 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | M128104100523 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0423 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | M128152129153 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.386 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MALDIVES_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.535 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9134 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB100002711580 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9388 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB1000710005-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4027 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB1005312810 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0508 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB1101411110-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6305 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB1158011585 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3518 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB1281010052 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0157 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB1291012930 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0018 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB1291512815a | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3771 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB2084520840 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.075 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB2089220893 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2866 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB210140210145-AAAAA | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9455 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB210140210145-AAAAB | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.2093 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB210140210145-AAABA | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.1718 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB210140210145-AABA | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.6397 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB210140210145-AABB | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8586 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB210140210145-ABAAA | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.4385 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB210140210145-ABAAB | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.167 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB210140210145-ABABB | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.4422 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB210140210145-ABBA | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8518 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB210140210145-BAAA-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.345 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB210140210145-BAAA-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4187 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB210140210145-BABA | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3235 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MB2726627277 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.6066 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.8382 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.4651 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MITCHELL BEND-WOLF HOLLOW II UNIT 4 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5825 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.7332 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | MOSS - HOLT/YUCCA 138 KV/MIDLAND COUNTY NW SW 345 KV (DOUBLE B TO B) SUM 2025- FUTURE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2633 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | N5GSU2_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.5764 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4102 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | NEW-CLEBURNE-HILLSBORO 138 KV (SINGLE B TO B)-2-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1375 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | NEW-HILLSBORO-CLEBURNE_SW_8 (SINGLE B TO B )-1-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1375 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | ODESSA EHV - NORTH MCCAMEY 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5964 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | OYSTER_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.699 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1.2_2.2_BZP3_BZP4 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0892 | 100.5858 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_BTE_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1341 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_BTE_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1341 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_BTE_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1341 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_BVE_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.124 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_BVE_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1226 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_CBT_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3187 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_CBT_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.321 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_CBY_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1044 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_CBY_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1044 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_CHE_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0279 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_CHE_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2922 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_CHE_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3465 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_CVC_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1815 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_CVC_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1591 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_CVC_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1591 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_CVC_4_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1004 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_DIB_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1754 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_DIB_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1752 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_DIB_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2054 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_DPEC_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3341 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_DPEC_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3725 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_DPEC_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3343 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_DPEC_4_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3725 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_DPEC_5_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2731 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_FTR_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9399 | 100.2504 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_FTR_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.94 | 100.2504 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_FTR_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9401 | 100.2502 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_BLY-CBT_C0_111143 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0274 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_CBY-CBY_C0_110075 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.349 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_CBY-CBY_C1_110073 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2797 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_CBY-CBY_C2_110074 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2797 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_CTR-DPEC_C0_110755 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6487 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_CTR-DPEC_C1_110751 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1991 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_CTR-DPEC_C2_110752 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2381 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_CTR-DPEC_C3_110753 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1994 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_CTR-DPEC_C4_110754 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2381 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_CTR-DPEC_C6_110761 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1374 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_DPW-CHE_C2_110663 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4252 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_DPW-CHE_C3_110668 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4792 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_JFS-PSG_C0_110623 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2609 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_JFS-PSG_C2_110621 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2355 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_JFS-PSG_C3_110622 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2356 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_RNS-FTR_C0_120094 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9617 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_RNS-FTR_C1_120091 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5005 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_RNS-FTR_C2_120092 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5005 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_RNS-FTR_C3_120093 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5006 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_SDN-CVC_C0_110824 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2873 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_SDN-CVC_C1_110821 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4194 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_SDN-CVC_C2_110822 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3973 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_SDN-CVC_C3_110823 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3972 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_SMR-BVE_C0_110773 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5281 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_SMR-BVE_C1_110771 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1078 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_SMR-BVE_C2_110772 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1063 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_THW_C0_110046 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1863 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_GEN_THW_C0_110051 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1862 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_PSA_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3638 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_PSA_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3685 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_PSA_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3732 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_PSA_4_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3756 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_PSA_5_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3764 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_PSA_6_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3711 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_PSG_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9749 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_PSG_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9749 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_THW_1_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5098 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_THW_2_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5098 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_THW_3_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5098 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_THW_4_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5098 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_THW_5_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5097 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_THW_6_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5097 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_THW_7_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5096 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-1_THW_8_COMBINED-CYCLE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5096 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(02.3-CKT66_SODG_46511) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8323 | 101.0688 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(08.1_SODG_44652-44081) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6851 | 100.15 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(110666-110667-BC) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4792 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(17.1_SODG_45971) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1671 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(20.1_SODG_44592) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.7309 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(21.2_SODG_44541) | 138 | 138 | Branch Amp | 1137.9656 | 106.8659 | - | - | - | 116.5084 | 120.7604 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(24.1_SODG_44173-44341) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3255 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(33.1X_SODG_44342) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1442 | 100.4999 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(40015-49200-GL) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9239 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(40070-110975-1) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1687 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(40240-110756-01) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6487 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(40240-110757-02) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1991 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(40240-110758-03) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2381 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(40240-110759-04) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1994 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(40240-110760-05) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2381 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(40240-110762-01) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1374 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(40450-110666-02) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3802 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(40600-120095-1) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.7686 | 100.9382 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(40890-113219-01) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.514 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(41240-110624-02) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2355 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(41240-110625-03) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2356 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(41240-110626-02) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2609 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(41430-110825-03) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1815 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(41430-110826-02) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3973 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(41430-110827-01) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3972 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(42980-44010-02)-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 109.9541 | 111.165 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(42980-44010-02)-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 115.8864 | 124.8941 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(44015-49215-GL) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.6091 | 102.3997 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(44090-111865-1) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3271 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(44160-112495-1) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.482 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(44650-110774-1) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1078 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(44650-110775-2) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1063 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(44650-110776-1) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5281 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(46020-49208-GL) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.2872 | 100.3215 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(46020-49209-GL) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.3555 | 100.3407 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(47010-47014-24) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0792 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_(8130-43190-1) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.7561 | 104.8621 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_11.1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2834 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_ALVIN_CKT05 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.0319 | 105.4333 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-2_HOC_BUS_REACTOR | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.2603 | 102.3345 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P1-3_OB-A1_AUTO&SHUNT | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5516 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7.1_BZR-RTR_BRZ-DOW | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0073 | 100.9609 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7.1_CP8-CP9_CP8-CP9 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 109.6965 | 109.0563 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1/C5-CTT-38 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2312 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>JULIA | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3405 | 103.3485 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0202B1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0289 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0202C | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 121.8156 | 126.4253 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0202E | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 117.5139 | 122.1455 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0202H | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 112.0803 | 115.5801 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0202J-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 110.2741 | 111.5132 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0202J-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 111.1286 | 112.7468 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0202K-1-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.8734 | 105.864 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0202K-1-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.7448 | 107.102 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0202K-2-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 100.1282 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0405 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 110.4379 | 109.8448 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0463 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 110.6107 | 109.8951 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0493 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 110.6825 | 109.9486 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0524B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0083 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0526 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.624 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0607 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2002 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0691B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3915 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0691F_ERC | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0068 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0726 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3419 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0792B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.03 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0945A | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.6818 | 101.1505 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0972X | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.6453 | 100.4656 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0980 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 123.8898 | 117.8047 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0990A | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4451 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T0990B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4284 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T1497 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0908 | 100.247 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T1827BY | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.0465 | 103.8812 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T1827D | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.7636 | 106.5787 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T1827GX_ERC | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | - | 101.7165 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T1827H | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.6972 | 104.9868 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T1827J | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.9184 | 102.4069 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T1839X1_ERC | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.5877 | 100.5946 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T1839X2_ERC | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3929 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T1899X | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.5555 | 104.4178 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T2525C | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1292 | 100.3203 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T2573B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 106.1701 | 102.6245 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T2626D | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 107.0945 | 106.5359 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T2682EX1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 116.713 | 117.2871 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T2682EX2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 117.2695 | 117.8442 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T2682GY1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 117.3258 | 117.9008 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T2682GY2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 117.3261 | 117.9012 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T2764Y_ERCa | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.2122 | 100.8783 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T3790A | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4404 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T3790B_90RADIAL | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3214 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T3944Z_ERC | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.168 | 100.1414 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T4848K | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.9061 | 103.9263 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T5098 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.6026 | 100.6669 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T6060B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.998 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T6060D | 138 | 138 | Branch Amp | 1137.9656 | 104.9245 | - | - | - | 124.4319 | 123.0277 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T6472A | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0656 | 100.0613 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T6472B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0828 | 100.2086 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T6472CX1A | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.796 | 101.916 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T6472CX1B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6769 | 101.5469 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T6472E | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4492 | 101.0505 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T6472G | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5034 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T6472H | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9228 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T6472J | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.6576 | 100.2087 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T6681C_A2RADIAL | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0755 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T7198 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8217 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T7474_A2RADIAL | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1993 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T7475B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9392 | 100.2196 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T7475C | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3287 | 100.3862 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T7475D_75RADIAL | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1041 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T8082B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5797 | 100.3072 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T9797B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.5864 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T9799A | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.1682 | 101.1809 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T9799B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1941 | 100.619 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T9799C | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.1957 | 101.1295 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T9799D | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.9429 | 101.8094 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>>T9899A | 138 | 138 | Branch Amp | 1137.9656 | 100.2901 | - | - | - | 113.5367 | 108.086 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>LEG-OUTLAW_ERC | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1588 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>T0202GX | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 117.5439 | 121.4342 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>T0524AY | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3598 | 100.6527 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>T2682DX | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 112.7222 | 113.2773 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1_E1>T6060F | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 109.3931 | 105.0612 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | P7-1>>T2727L | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 105.248 | 105.0698 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | PARIS NW-PARIS-PARIS SW138 KV (SINGLE B TO B) A | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1467 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | PARIS SW-MOSES 345 KV-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3728 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | PARIS SW-PACIFIC SW/VALLEY S SW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2141 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | PINEFOREST_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9613 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | QUANT_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3288 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | R4U2A5C1_1_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3518 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | RAMHORN - WILLOW CREEK DC 345 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0141 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | RAT_SNAKE-SNDY_CREEK_5 (SINGLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.7157 | 100.0652 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | RYBRN_P1-2_VINSON-LORING_2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0039 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5647 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4835 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3123 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | SAM_NAV_P7F1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3967 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | SAN_PAT_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.1045 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | SKULLCREEK_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1476 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | SOLACE_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2859 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | STECL_10247 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0959 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | STECL_10248 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0959 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | STECL_10262 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.4894 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | STECL_10288 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0856 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | STECL_10588 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0535 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | STECL_4720 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3879 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | STECL_4721-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0529 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | STECL_4721-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0011 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | STP - HOUDINI & STP - SHAULA | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.172 | 100.8873 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | T_000981SPNCRINT69-000982DN_STEAM_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3318 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | T_059908NOVA_345-059998NOVA8CT1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.5475 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | T_180760DIVIDE_SC1-180754DIVIDE_1_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3302 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | T100002 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.493 | 100.4882 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3426 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | THRESLR_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0649 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | TIMBERVIEW-COMANCHE PEAK*DECORDOVA 345 KV (SINGLE B TO B)-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0096 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.1624 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0954 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | TRIFECTA_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.4411 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | TRIN-SK*ME (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4428 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | TWIN_OAK_BKR_8995_345_OAK_GROVE_SINGLE_B_T0_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.4206 | 100.3821 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | TWIN_OAK_BKR_9000_345_OAK_GROVE_SINGLE_B_T0_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.4205 | 100.3822 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | U2GSU56_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0405 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | U2GSU78_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.035 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | U3CT1_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3778 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | U3GSU1_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.3812 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | U3GSU2_B | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4971 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | VALLEY SW-COMMERCE SW 138 KV BONHAM SW 138-69KV AUTO #1 A | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0038 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.6575 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5886 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 108.2597 | 100.6188 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | VIKING_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1233 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | WAP - HOUDINI & STP - SHAULA | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8729 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | WHITERIVER-COTTONWOOD (DOUBLE B TO B)-3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9662 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.317 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | WINDMILL - AJSWOPE (SINGLE B TO B) SUM 2028 - FUTURE | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.8048 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.7011 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | WOLF HOLLOW-WOLF HOLLOW_C2_345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9806 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-CALFRESTN_5-4 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4257 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-CALFRESTN_5-5 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4249 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-CALFRESTN_5-6 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5653 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-CALPFREST_5-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3892 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-CALPFREST_5-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3892 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-CALPFREST_5-3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.5148 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-ENNSTRAC_8-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.915 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-ENNSTRAC_8-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3172 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-FSCOGEN_8-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0026 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-FSCOGEN_8-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.0026 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-GRHAMSES1_8-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0222 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-HANDLEYC_8-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.9908 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-HANDLEYC_8-3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.392 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-HANDLEYD_8-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.4178 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-LKHB_1T8-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.128 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-LKHB_2T8-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.0479 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-MARTINLK_5-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.9594 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-MARTINLK_5-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.995 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-MARTINLK_5-3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.0062 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-MDLTHELP_5-5 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.108 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-MDLTHELP_5-6 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1201 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-MDLTHELP_N5-3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1422 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-MDLTHELP_N5-4 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.1415 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-MDLTHELP_S5-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.0318 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-MDLTHELP_S5-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.133 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-MTCK_6T8-6 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3858 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-MTCK_7T8-7 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3644 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-MTCK_8T8-8 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.3974 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-MTENTRPR_5G-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4097 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-MTENTRPR_5G-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.2908 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-MTENTRPR_5G-3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.3927 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-MTENTRPR_5G-4 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.807 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-SANDYCRK_5-01 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.7157 | 100.0652 | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-STRYKER_8-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.3875 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-STRYKERND_8-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4723 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-WHCCS2_4-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5825 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-WHCCS2_5-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.2653 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-WLFHMDPT_5-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.701 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | XFMR-WLFHOSTR-3 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9805 | - | -
TCNPE | COAST | COAST | COAST, COAST | W_COL_89T4_8 (43384) -> DAMON__S89_8 (42370) CKT 89 | YELLOW_WOLF_CON | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.5089 | - | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WALNUT ( 823) -> NAAMAN ( 825) CKT 1 | L_000802APOLLO-000806JUPITERC1 | 138 | 138 | Branch Amp | 983.1688 | - | - | 103.5326 | 110.4707 | 111.4478 | 113.3556 | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WALNUT ( 823) -> NAAMAN ( 825) CKT 1 | L_000802APOLLO-002165HOLFORD_8C1 | 138 | 138 | Branch Amp | 983.1688 | - | 106.737 | 112.712 | 112.2904 | 112.5047 | 113.6817 | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WALNUT ( 823) -> NAAMAN ( 825) CKT 1 | L_000806JUPITER-000829COLLEGE8C1 | 138 | 138 | Branch Amp | 983.1688 | - | - | 110.9659 | 117.8087 | 118.7336 | 120.6595 | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WALNUT ( 823) -> NAAMAN ( 825) CKT 1 | L_000821FIREWHEEL-000833WYLIESWC1 | 138 | 138 | Branch Amp | 983.1688 | - | - | - | - | - | 100.1652 | -
TSTEC | COAST | COAST | COAST, COAST | WARBURTONSW9 ( 5605) -> WRBRTN8 ( 5607) CKT 1 | L_005607WRBRTN8-008172VICTORIA4AC1 | 69 | 138 | Branch MVA | 56 | - | - | - | - | 105.9168 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WARRIORTRL_8 ( 3366) -> HARKHTS_S18 ( 3633) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1363.8853 | - | - | - | - | 122.4597 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_8 ( 2429) -> REINDEER_8 ( 3065) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 105.3259 | 105.7541 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_8 ( 2429) -> REINDEER_8 ( 3065) CKT 1 | 3WT_002431DESSW1_5_002424DESSW1_8_012431DESSW1_3 C 1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | - | 101.1252 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_8 ( 2429) -> REINDEER_8 ( 3065) CKT 1 | L_002422CHILSW_N8-003049EGLFD2_8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.7306 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_8 ( 2429) -> REINDEER_8 ( 3065) CKT 1 | L_003058CHILTPL4_8-003059DESHPR1_8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 115.7586 | 129.6286 | 128.7832 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_8 ( 2429) -> REINDEER_8 ( 3065) CKT 1 | L_003059DESHPR1_8-003060DESPLR1_8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 113.3798 | 112.684 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_8 ( 2429) -> REINDEER_8 ( 3065) CKT 1 | WATERMILL-LOOP NINE 345 KV DCKT (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | - | 108.3443 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_8 ( 2429) -> TENMIL2_8 ( 2144) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1648.3767 | - | - | - | 107.8435 | 130.1357 | 135.28 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_8 ( 2429) -> TENMIL2_8 ( 2144) CKT 1 | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1648.3767 | - | - | - | - | 100.7403 | 109.4414 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_8 ( 2429) -> TENMILE_8 ( 2126) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1280.2113 | - | - | - | 144.1004 | 173.9003 | 180.7579 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_8 ( 2429) -> TENMILE_8 ( 2126) CKT 1 | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1280.2113 | - | - | - | 115.6118 | 134.5891 | 146.1697 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_8 ( 2429) -> WILMER1_8 ( 3083) CKT 1 | L_002263GELLER_8-003079SSWWT2T_8C1 | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | 112.452 | 114.9997 | 109.273 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_8 ( 2429) -> WILMER1_8 ( 3083) CKT 1 | L_002263GELLER_8-003083WILMER1_8C1 | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | 111.112 | 113.6262 | 108.0222 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_8 ( 2429) -> WILMER1_8 ( 3083) CKT 1 | L_002434SGVLSW1_8-003076SGVL1_8C1 | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | 120.724 | 123.3604 | 116.85 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_8 ( 2429) -> WILMER1_8 ( 3083) CKT 1 | L_003076SGVL1_8-003077KLEBRG1T_8C1 | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | 117.1949 | 119.6461 | 113.7394 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_8 ( 2429) -> WILMER1_8 ( 3083) CKT 1 | L_003077KLEBRG1T_8-003079SSWWT2T_8C1 | 138 | 138 | Branch Amp | 3196.3445 | - | - | - | 112.8477 | 115.3921 | 109.6322 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> GREENRD_5 ( 3063) CKT 1 | L_002427WATMLL_W5-003070GREENRD_5C2 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 109.0048 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> GREENRD_5 ( 3063) CKT 1 | Watermill Switch-GreenRD SW 345 kV Line CKT2(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 109.0048 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> GREENRD_5 ( 3063) CKT 2 | L_002427WATMLL_W5-003070GREENRD_5C1 | 345 | 345 | Branch Amp | 2729.4438 | - | - | - | - | - | 109.0048 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> LOOP9_5 ( 2847) CKT 2 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | - | 102.855 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> LOOP9_5 ( 2847) CKT 2 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | - | 101.8748 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> LOOP9_5 ( 2847) CKT 2 | L_002427WATMLL_W5-002847LOOP9_5C1 | 345 | 345 | Branch Amp | 1793.9694 | - | - | - | - | - | 110.5855 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 102.4709 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | 3WT_002427WATMLL_W5_002429WATMLL_8_012429WTML2_3 C 2 | 345 | 1 | Branch MVA | 695 | - | - | - | 108.9387 | 114.4082 | 143.9334 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | 3WT_002433SGVLSW1_5_002434SGVLSW1_8_012434SGVLSW1_3 C 2 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.84 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | ALLEN SW - PLANO TENNYSON 345 KV & ALLEN SW - RENNER 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.3522 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | ALLEN SW 345-138 KV AUTO #1 (SINGLE AUTO) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.5412 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.3161 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.3109 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.3117 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.4144 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.4575 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.4157 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.4585 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | ALLEN-MOSES 345-138 AUTO-2 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.2262 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.4007 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.3851 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | ANNA SW - VALLEY SOUTH 345 KV & ANNA SW - FARMERSVILLE 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.4029 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | BEPC_304_2 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.799 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 103.8302 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | BLUBIRD_CON | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 107.6251 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-2 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.881 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | DES_WILL_CON | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.1789 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | DRY_CREEK_CON | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.2346 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 108.4895 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | E_ETCCS_CC1_TRAIN | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.9141 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | E_PANDA_S_CC1_TRAIN | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.2848 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | E_WHCCS2_CC2_TRAIN | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.6095 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | E5DVA1C1_1_B | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.3793 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | ENNIS WEST - STERRETT 138 KV (SINGLE B TO B) A REAGOR SPRINGS | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.818 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | G_150051HLSES_UNIT3UN3 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.6695 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | G_150052HLSES_UNIT4UN4 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.7049 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | G_150053HLSES_UNIT5UN5 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.7098 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | G_150091LHSES_UNIT1UN1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.2425 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | G_150111CPSES_UNIT1UU1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.5594 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | G_150112CPSES_UNIT2UU2 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.5273 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | G_888879BLUBIRD_POIUS1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.6492 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | GLASGOW_CON | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.7756 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | GreenRD Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 1 | Branch MVA | 695 | - | - | - | - | 105.2702 | 133.1352 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | KRUMW-WEST DENT/DUNHAM 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 101.4827 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.6722 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.6748 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.841 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.2262 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.2849 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_001880ROCKYCRK_5-888879BLUBIRD_POIC1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.5755 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.0106 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 106.9628 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_001906VENUS_S5-015201FORBESR2_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.6638 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_001906VENUS_S5-888857OYSTER_POIC1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.2275 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_001906VENUS_S5-888880DES_WILL_POIC1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.2711 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.7403 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 107.967 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_001907VENUS_N5-015200FORBESR1_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.9286 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_001907VENUS_N5-068091NAVARROC1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.55 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.0052 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 106.8617 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.0452 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_002263GELLER_8-003079SSWWT2T_8C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | 103.5183 | 119.0759 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_002263GELLER_8-003083WILMER1_8C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | 103.144 | 118.6987 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_002315WAX_PMP2_8-002319WAX_PMP1_8C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.8763 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_002315WAX_PMP2_8-002320WAX_N_8C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.8828 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_002316MG_IND_T8-002319WAX_PMP1_8C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.8544 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_002320WAX_N_8-002321WAX_8C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.0173 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.0251 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_002372COLLINSS1_5-002373ANNASW_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.1682 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_002421CHILSW_S8-002999DVIL1_8C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 108.4569 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 107.3617 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 106.9697 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_002434SGVLSW1_8-003076SGVL1_8C1 | 345 | 1 | Branch MVA | 695 | - | - | - | 100.2646 | 105.8063 | 124.2062 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_002461ROYSE_N5-002513ALLENSW1_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.5264 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 101.8239 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_002478ROYSE_S5-002485POETRY_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.901 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_003076SGVL1_8-003077KLEBRG1T_8C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | 104.8309 | 120.432 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_003077KLEBRG1T_8-003079SSWWT2T_8C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | 103.6279 | 119.1857 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_003100MARTINLK_5-003102TYLERGND_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.3474 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.2922 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 102.1382 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.6997 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_003386OUTLAW_5-068091NAVARROC1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.1057 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.0588 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 107.2048 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.2262 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | L_888880DES_WILL_POI-001916LIGGETTA2_5C1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.3336 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | LATIMER_REATA_P7F1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.7201 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.1791 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-2 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.3338 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 108.8685 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.8008 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 107.6249 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 107.1198 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 103.7309 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.6499 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | NORTHWEST CARROLLTON - LEWISVILLE SW (BEPC) 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.8791 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | OYSTER_CON | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.1044 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.2595 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV DCKT & EAGLE MOUNTAIN - WEATHERFORD 138 KV LINE | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.2508 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | PINEFOREST_CON | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.5447 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (COMMON TOWER) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.0303 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | RAMHORN - WILLOW CREEK DC 345 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.0744 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | RENNER - NORTHWEST CARROLLTON 345 KV & RENNER - ALLEN SW 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.0058 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | S_002578CRLTNE_81 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.5566 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.7739 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | SEAGOVILLE SW - FORNEY/TRICORNER DCKT 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.8848 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | TIMBERVIEW-COMANCHE PEAK*CARMICHAEL BEND 345 KV (DOUBLE B TO B)-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.6227 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | TIMBERVIEW-COMANCHE PEAK*DECORDOVA 345 KV (SINGLE B TO B)-2 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.6827 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.3839 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 107.2279 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.7854 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | TRIN-SK*ME (DOUBLE B TO B) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.2135 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.2176 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 107.0855 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.2875 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.3008 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.291 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 101.6581 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 102.1048 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 103.9863 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.0638 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | VENUS-FORT SMITH SW 345 KV (SINGLE B TO B) new load | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.6623 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.1692 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | VENUS-SAM SW 345 KV (SINGLE B TO B) new load | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.9394 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | VIKING_CON | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.713 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 345 | 1 | Branch MVA | 695 | - | - | - | 122.3137 | 131.9365 | 159.1478 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | Watermill Switch-GreenRD SW 138 kV Line (Double B TO B) new load | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 101.4794 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | WATERMILL-LOOP NINE 345 KV DCKT (DOUBLE B TO B) A | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 102.5122 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | WAXAHACHI-WAXAHACHI OFC 69KV/ENNIS-STERRETT 138KV (DOUBLE B TO B) A REAGOR | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.2094 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 107.1421 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 345 | 1 | Branch MVA | 695 | - | - | - | 115.264 | 122.1721 | 153.5304 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | WSHACK_LATIMER_P7 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.7383 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | XFMR-HANDLEYC_8-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.6695 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | XFMR-HANDLEYC_8-3 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.7098 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | XFMR-HANDLEYD_8-2 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 104.7049 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500082) CKT 1 | XFMR-LKHB_1T8-1 | 345 | 1 | Branch MVA | 695 | - | - | - | - | - | 105.2425 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | 3WT_002427WATMLL_W5_002429WATMLL_8_012430WATMLL1_3 C 1 | 345 | 1 | Branch MVA | 750 | - | - | - | 106.251 | 110.9856 | 140.9967 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | 3WT_002433SGVLSW1_5_002434SGVLSW1_8_012434SGVLSW1_3 C 2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.9784 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | ALLEN SW - PLANO TENNYSON 345 KV & ALLEN SW - RENNER 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.9048 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | ALLEN SW 345-138 KV AUTO #1 (SINGLE AUTO) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.0581 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | ALLEN SW 345-138 KV AUTO #2 (SINGLE AUTO) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.8083 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.8219 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.8224 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.902 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.9364 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.903 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.937 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | ALLEN-MOSES 345-138 AUTO-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.7312 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.8988 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.8856 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | ANNA SW - VALLEY SOUTH 345 KV & ANNA SW - FARMERSVILLE 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.957 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | BEPC_304_2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.2702 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.4414 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | BLUBIRD_CON | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.1585 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | COMANCHE PEAK-EVERMAN/JOHNSON 345KV (DOUBLE B TO B) A TIMBERVIEW-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.3014 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | DES_WILL_CON | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.5566 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | DRY_CREEK_CON | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.742 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | DUNHAM - LEWISVILLE DC 345 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.9369 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | E_ETCCS_CC1_TRAIN | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.3474 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | E_PANDA_S_CC1_TRAIN | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.6515 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | E_WHCCS2_CC2_TRAIN | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.077 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | E5DVA1C1_1_B | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.8512 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | ENNIS WEST - STERRETT 138 KV (SINGLE B TO B) A REAGOR SPRINGS | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.3145 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | G_150051HLSES_UNIT3UN3 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1386 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | G_150052HLSES_UNIT4UN4 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1509 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | G_150053HLSES_UNIT5UN5 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1675 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | G_150091LHSES_UNIT1UN1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.5583 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | G_150111CPSES_UNIT1UU1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.0411 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | G_150112CPSES_UNIT2UU2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.002 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | G_888879BLUBIRD_POIUS1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1191 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | GreenRD Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 1 | Branch MVA | 750 | - | - | - | - | 101.5144 | 122.7231 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | KRUMW-WEST DENT/DUNHAM 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.6802 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_000192TELICO-002331ENNS_PMP_T8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.1629 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_000192TELICO-003454MONTFTSS__8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.1643 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.082 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_001696MOSES1_T5-002514ALLENSW2_5C1-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.731 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_001839STONCRK_8-140002SHER1_TLC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.6515 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_001880ROCKYCRK_5-888879BLUBIRD_POIC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.0357 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_001904WEBB3_5-002420CHILSW1_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.5542 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.6002 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_001906VENUS_S5-015201FORBESR2_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1325 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_001906VENUS_S5-888857OYSTER_POIC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.5765 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_001906VENUS_S5-888880DES_WILL_POIC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.6571 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.2052 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_001907VENUS_N5-002632MILLERRD_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.4806 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_001907VENUS_N5-015200FORBESR1_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.3471 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_001907VENUS_N5-068091NAVARROC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.8433 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.5742 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.5183 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.4899 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_002263GELLER_8-003079SSWWT2T_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | 101.959 | 114.3378 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_002263GELLER_8-003083WILMER1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | 101.6154 | 113.9969 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_002315WAX_PMP2_8-002319WAX_PMP1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.3579 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_002315WAX_PMP2_8-002320WAX_N_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.3633 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_002316MG_IND_T8-002319WAX_PMP1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.3398 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_002320WAX_N_8-002321WAX_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.4731 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_002321WAX_8-012320TMPLTON_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.4736 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_002372COLLINSS1_5-002373ANNASW_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.6908 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_002421CHILSW_S8-002999DVIL1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 105.6572 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.931 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.6084 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_002434SGVLSW1_8-003076SGVL1_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | 104.0664 | 115.5393 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_002461ROYSE_N5-002513ALLENSW1_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.0453 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_002478ROYSE_S5-002485POETRY_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.3344 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_003076SGVL1_8-003077KLEBRG1T_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | 103.1593 | 115.5524 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_003077KLEBRG1T_8-003079SSWWT2T_8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | 102.0569 | 114.4354 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_003100MARTINLK_5-003102TYLERGND_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.8573 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.8059 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1436 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_003386OUTLAW_5-068091NAVARROC1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.6419 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.4249 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.8047 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_888854PINEFOREST_POI-002514ALLENSW2_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.731 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | L_888880DES_WILL_POI-001916LIGGETTA2_5C1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.711 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | LATIMER_REATA_P7F1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1666 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.5568 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.7112 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.2515 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 106.5204 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.1582 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.733 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.3098 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 103.1412 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | NORTHWEST CARROLLTON - LEWISVILLE SW (BEPC) 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.3354 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | OYSTER_CON | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.4636 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | PARKER-EAGLE MTN*HICKS 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.6254 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | PARKER-EAGLE MTN*HICKS 345 KV DCKT & EAGLE MOUNTAIN - WEATHERFORD 138 KV LINE | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.6209 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | PINEFOREST_CON | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.9895 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (COMMON TOWER) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.431 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | RAMHORN - WILLOW CREEK DC 345 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.4642 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | RENNER - NORTHWEST CARROLLTON 345 KV & RENNER - ALLEN SW 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.4552 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | S_002578CRLTNE_81 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.0828 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.2569 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | SEAGOVILLE SW - FORNEY/TRICORNER DCKT 345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.0162 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | TIMBERVIEW-COMANCHE PEAK*CARMICHAEL BEND 345 KV (DOUBLE B TO B)-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.0959 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | TIMBERVIEW-COMANCHE PEAK*DECORDOVA 345 KV (SINGLE B TO B)-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1218 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.8901 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.8212 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | TRIN-RICH (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1182 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | TRIN-SK*ME (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.7343 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.7433 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.6933 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.7879 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.7992 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.7878 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.8973 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.5407 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 101.6186 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | VENUS-FORT SMITH SW 345 KV (SINGLE B TO B) new load | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1319 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.5727 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | VENUS-SAM SW 345 KV (SINGLE B TO B) new load | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.3547 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | VIKING_CON | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1858 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 345 | 1 | Branch MVA | 750 | - | - | - | 116.1001 | 125.0303 | 148.8898 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | WAXAHACHI-WAXAHACHI OFC 69KV/ENNIS-STERRETT 138KV (DOUBLE B TO B) A REAGOR | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.6492 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 100.7563 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 345 | 1 | Branch MVA | 750 | - | - | - | 109.8355 | 116.1648 | 140.9383 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | WSHACK_LATIMER_P7 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1739 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | XFMR-HANDLEYC_8-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1386 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | XFMR-HANDLEYC_8-3 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1675 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | XFMR-HANDLEYD_8-2 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.1509 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 ( 2427) -> WATMLSTR (500083) CKT 2 | XFMR-LKHB_1T8-1 | 345 | 1 | Branch MVA | 750 | - | - | - | - | - | 102.5583 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 (2427) -> TRICRN1_5 (2432) CKT 1 | Pre-contingency | 345 | 345 | Amps | 3199.6917 | - | - | - | 109.0017 | 132.2258 | 102.1281 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLL_W5 (2427) -> TRICRN1_5 (2432) CKT 2 | Pre-contingency | 345 | 345 | Amps | 3199.6917 | - | - | - | 109.0017 | 132.2258 | 102.1281 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500082) -> WATMLL_8 ( 2429) CKT 1 | 3WT_002427WATMLL_W5_002429WATMLL_8_012429WTML2_3 C 2 | 138 | 1 | Branch MVA | 734 | - | - | - | - | 101.596 | 124.7393 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500082) -> WATMLL_8 ( 2429) CKT 1 | GreenRD Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 1 | Branch MVA | 734 | - | - | - | - | - | 119.3151 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500082) -> WATMLL_8 ( 2429) CKT 1 | L_002263GELLER_8-003079SSWWT2T_8C1 | 138 | 1 | Branch MVA | 734 | - | - | - | - | - | 106.1507 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500082) -> WATMLL_8 ( 2429) CKT 1 | L_002263GELLER_8-003083WILMER1_8C1 | 138 | 1 | Branch MVA | 734 | - | - | - | - | - | 105.841 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500082) -> WATMLL_8 ( 2429) CKT 1 | L_002434SGVLSW1_8-003076SGVL1_8C1 | 138 | 1 | Branch MVA | 734 | - | - | - | - | - | 110.0261 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500082) -> WATMLL_8 ( 2429) CKT 1 | L_003076SGVL1_8-003077KLEBRG1T_8C1 | 138 | 1 | Branch MVA | 734 | - | - | - | - | - | 107.2791 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500082) -> WATMLL_8 ( 2429) CKT 1 | L_003077KLEBRG1T_8-003079SSWWT2T_8C1 | 138 | 1 | Branch MVA | 734 | - | - | - | - | - | 106.243 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500082) -> WATMLL_8 ( 2429) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 1 | Branch MVA | 734 | - | - | - | 113.0106 | 121.0034 | 142.5346 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500082) -> WATMLL_8 ( 2429) CKT 1 | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 138 | 1 | Branch MVA | 734 | - | - | - | 106.5497 | 112.4507 | 136.7601 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500083) -> WATMLL_8 ( 2429) CKT 2 | 3WT_002427WATMLL_W5_002429WATMLL_8_012430WATMLL1_3 C 1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | 102.3379 | 126.7248 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500083) -> WATMLL_8 ( 2429) CKT 2 | GreenRD Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 114.8671 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500083) -> WATMLL_8 ( 2429) CKT 2 | L_002263GELLER_8-003079SSWWT2T_8C1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 105.7417 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500083) -> WATMLL_8 ( 2429) CKT 2 | L_002263GELLER_8-003083WILMER1_8C1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 105.4528 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500083) -> WATMLL_8 ( 2429) CKT 2 | L_002434SGVLSW1_8-003076SGVL1_8C1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 106.9129 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500083) -> WATMLL_8 ( 2429) CKT 2 | L_003076SGVL1_8-003077KLEBRG1T_8C1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 106.7848 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500083) -> WATMLL_8 ( 2429) CKT 2 | L_003077KLEBRG1T_8-003079SSWWT2T_8C1 | 138 | 1 | Branch MVA | 750 | - | - | - | - | - | 105.8264 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500083) -> WATMLL_8 ( 2429) CKT 2 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 1 | Branch MVA | 750 | - | - | - | 110.5259 | 118.1504 | 138.3382 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WATMLSTR (500083) -> WATMLL_8 ( 2429) CKT 2 | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 138 | 1 | Branch MVA | 750 | - | - | - | 104.6138 | 110.1671 | 131.1419 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 120.0499 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | ENNIS - ENNIS SOUTH - ENNIS WEST T 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 112.3735 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | ENNIS - PEBBLE CREEK 138 KV SWITCH (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 161.2258 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | KEMP RANCH - SARDIS 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.4785 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | KEMP RANCH - SARDIS 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.4785 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | KEMP RANCH - SOAP CREEK / SARDIS 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.7302 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | L_000203SARDIS8-002309WAX_NW_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.767 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | L_000203SARDIS8-012317STERRETTL_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 107.6056 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | L_000217GLNHEIGHTS-002424DESSW1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 100.1252 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | L_000221TRUMBULL8-002229PEBBLCRK_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 151.404 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | L_000221TRUMBULL8-012344GAMMA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 161.3097 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | L_000223SAINTPAUL-000404JESSICAC1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 100.1633 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | L_000404JESSICA-000419LILLIAN8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 101.3057 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | L_002241ENNS_W_8-002324ENNS_S_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.0647 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | L_002303KEMPRNCH_8-002305AIRPRD_T8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 109.5245 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | L_002305AIRPRD_T8-002307MDLTHTXI1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 108.3374 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | L_002307MDLTHTXI1_8-012307NEWBRCH_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 105.0567 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | L_002308MDLTH_S_8-002309WAX_NW_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 104.0744 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | L_002308MDLTH_S_8-012307NEWBRCH_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 104.1618 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | L_002317STERRETT1_8-012317STERRETTL_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.7159 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 103.7195 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | L_012329SHANKLSW_8-012344GAMMA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 161.2881 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | SOAP CREEK - CEDAR HILL / SARDIS 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.091 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | STERRETT 5410-SARDIS (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 102.5249 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | STERRETT-SARDIS/DESOTO 138KV DCKT (DOULBE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | 105.8242 | 140.751 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 105.6582 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_8 ( 2321) -> WAX_N_8 ( 2320) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 104.2535 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_9 ( 2335) -> WAX_OCF_9 ( 2343) CKT 1 | L_000205MALONEY-033204BETHEL2C2 | 69 | 69 | Branch Amp | 334.6958 | - | - | 100.9683 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_9 ( 2335) -> WAX_OCF_9 ( 2343) CKT 1 | L_002295BARDWELL_9-033204BETHEL2C1 | 69 | 69 | Branch Amp | 334.6958 | - | - | 101.0425 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_9 ( 2335) -> WAX_OCF_9 ( 2343) CKT 1 | STERRETT-SARDIS/DESOTO 138KV DCKT (DOULBE B TO B) | 69 | 69 | Branch Amp | 334.6958 | - | - | 118.7429 | - | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_9 (2335) -> WAX_OCF_9 (2343) CKT 1 | Pre-contingency | 69 | 69 | Amps | 334.6958 | - | - | - | 110.3596 | 127.2243 | 105.8269 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_N_8 ( 2320) -> WAX_PMP2_8 ( 2315) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 107.7459 | 101.185 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_N_8 ( 2320) -> WAX_PMP2_8 ( 2315) CKT 1 | ENNIS - PEBBLE CREEK 138 KV SWITCH (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 134.5009 | 160.1383 | 139.2738 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_N_8 ( 2320) -> WAX_PMP2_8 ( 2315) CKT 1 | L_000217GLNHEIGHTS-002424DESSW1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | - | 104.4197 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_N_8 ( 2320) -> WAX_PMP2_8 ( 2315) CKT 1 | L_000221TRUMBULL8-002229PEBBLCRK_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 124.7201 | 150.3446 | 129.0702 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_N_8 ( 2320) -> WAX_PMP2_8 ( 2315) CKT 1 | L_000221TRUMBULL8-012344GAMMA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 134.5867 | 161.359 | 139.316 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_N_8 ( 2320) -> WAX_PMP2_8 ( 2315) CKT 1 | L_012329SHANKLSW_8-012344GAMMA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 134.5655 | 161.2971 | 139.2989 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_N_8 ( 2320) -> WAX_PMP2_8 ( 2315) CKT 1 | STERRETT-SARDIS/DESOTO 138KV DCKT (DOULBE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 112.5606 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_N_8 (2320) -> WAX_8 (2321) CKT 1 | Pre-contingency | 138 | 138 | Amps | 861.8416 | - | - | - | - | 107.0939 | 103.4176 | -
TBREC,TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_NW_8 ( 2309) -> SARDIS8 ( 203) CKT 1 | L_000404JESSICA-000419LILLIAN8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 104.7972 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_PMP1_8 ( 2319) -> MG_IND_T8 ( 2316) CKT 1 | ENNIS - PEBBLE CREEK 138 KV SWITCH (SINGLE B TO B) | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 111.198 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_PMP1_8 ( 2319) -> MG_IND_T8 ( 2316) CKT 1 | L_000221TRUMBULL8-002229PEBBLCRK_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 104.1315 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_PMP1_8 ( 2319) -> MG_IND_T8 ( 2316) CKT 1 | L_000221TRUMBULL8-012344GAMMA_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 112.045 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_PMP1_8 ( 2319) -> MG_IND_T8 ( 2316) CKT 1 | L_012329SHANKLSW_8-012344GAMMA_8C1 | 138 | 138 | Branch Amp | 1200.7211 | - | - | - | - | 112.0011 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_PMP2_8 ( 2315) -> WAX_PMP1_8 ( 2319) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | 106.4395 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_PMP2_8 ( 2315) -> WAX_PMP1_8 ( 2319) CKT 1 | ENNIS - PEBBLE CREEK 138 KV SWITCH (SINGLE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 133.3487 | 158.9591 | 138.1567 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_PMP2_8 ( 2315) -> WAX_PMP1_8 ( 2319) CKT 1 | L_000217GLNHEIGHTS-002424DESSW1_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | - | - | 103.1891 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_PMP2_8 ( 2315) -> WAX_PMP1_8 ( 2319) CKT 1 | L_000221TRUMBULL8-002229PEBBLCRK_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 123.5633 | 149.153 | 127.9476 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_PMP2_8 ( 2315) -> WAX_PMP1_8 ( 2319) CKT 1 | L_000221TRUMBULL8-012344GAMMA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 133.4346 | 160.1704 | 138.1998 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_PMP2_8 ( 2315) -> WAX_PMP1_8 ( 2319) CKT 1 | L_012329SHANKLSW_8-012344GAMMA_8C1 | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 133.4135 | 160.1087 | 138.1827 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WAX_PMP2_8 ( 2315) -> WAX_PMP1_8 ( 2319) CKT 1 | STERRETT-SARDIS/DESOTO 138KV DCKT (DOULBE B TO B) | 138 | 138 | Branch Amp | 861.8416 | - | - | - | 111.2936 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | 3WT_001907VENUS_N5_002303KEMPRNCH_8_011908VENUS3_3 C 1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 102.0579 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 122.2961 | - | 101.5004 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 116.0739 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | BEPC_015_2 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 101.5363 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 112.3056 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | DES_WILL_CON | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 108.9734 | 121.0966 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | DRY_CREEK_CON | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 100.2938 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 101.5209 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | E_FRNYPP_CC1_TRAIN | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 101.855 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | E_FRNYPP_CC2_TRAIN | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 101.8637 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 111.0665 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 100.0921 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | G_150023MCSES_UNIT8UN8 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 100.8974 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | GLASGOW_CON | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 111.1221 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 101.541 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_001906VENUS_S5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 105.6317 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_001906VENUS_S5-888880DES_WILL_POIC1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 108.5962 | 120.5481 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_001907VENUS_N5-015200FORBESR1_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 102.4223 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_001928LIGGETT_3T5-002406NORWD1_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 110.4106 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 108.7877 | 120.2075 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 112.1003 | 123.8333 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 112.3056 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 111.0665 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 102.3027 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_002427WATMLL_W5-002432TRICRN1_5C2 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 102.3027 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 104.1201 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 105.0018 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 101.8576 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 101.8365 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 111.1618 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 100.406 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_003124TRINDAD2_5-003134RICHLND1_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 103.9726 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 110.1823 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 104.6708 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 109.3593 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | L_888880DES_WILL_POI-001916LIGGETTA2_5C1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 109.6009 | 121.7615 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 107.5287 | 119.7374 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/CEDAR HILL - EXECUTIVE PKWY 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 108.5118 | 120.6263 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 108.5778 | 120.5765 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-2 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 109.5718 | 121.5331 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 108.9904 | 121.115 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-2 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 109.6179 | 121.7798 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 118.6041 | 131.0813 | 104.4025 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | LIGGETT-NORWOOD 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 109.4625 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 118.4714 | 131.1094 | 104.5796 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 119.0637 | 131.6758 | 105.3543 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 102.9313 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 101.2193 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | NORWOOD-LIGGETT 345 & MOUNTAIN CREEK - LIGGETT 138 KV DCKT A BLUBONT | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 109.869 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 100.1518 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV DCKT & EAGLE MOUNTAIN - WEATHERFORD 138 KV LINE | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 100.2208 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | RICH-BBROWN (DOUBLE B TO B)A | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 100.8626 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | SHERRY-TIMBERVIEW*VENUS 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 100.2168 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | TIMBERVIEW-CEDAR HILL SW 345 KV (SINGLE B TO B) | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 109.3462 | 120.6116 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 113.9751 | 125.3878 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | TIMBERVIEW-VENUS 345 KV DOUBLE-CIRCUIT LINE (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 106.8224 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 100.7036 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | TRIN-RICH (DOUBLE B TO B) | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 110.9199 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 100.1475 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 102.0252 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 100.6189 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 121.3689 | 135.4383 | 107.3435 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 107.8991 | 119.9936 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 108.44 | 120.5927 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 107.9382 | 120.06 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A TYRE PARK-2 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 108.922 | 121.0858 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-1 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 109.0246 | 121.007 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-2 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 109.5893 | 121.5514 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | VENUS-SAM SW 345 KV (SINGLE B TO B) new load | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 103.9735 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | WATERMILL-LOOP NINE 345 KV DCKT (DOUBLE B TO B) A | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 101.589 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | WATERMILL-TRICORNER (DOUBLE B TO B) B | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | 109.4433 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | WSHACK_LATIMER_P7 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 100.3926 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WEBB3_5 ( 1904) -> CHILSW1_5 ( 2420) CKT 1 | XFMR-MTCK_8T8-8 | 345 | 345 | Branch Amp | 2632.0476 | - | - | - | - | 100.8974 | - | -
TONCOR | EAST | EAST | EAST, EAST | WHITEOAK_T (11796) -> BRINKER_A8 (11797) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 116.7339 | 133.9293 | 117.324 | -
TONCOR | EAST | EAST | EAST, EAST | WHITEOAK_T (11796) -> BRINKER_A8 (11797) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 138 | 138 | Branch Amp | 748.8818 | - | - | 100.1842 | 126.1333 | 143.8824 | 125.7605 | -
TONCOR | EAST | EAST | EAST, EAST | WHITEOAK_T (11796) -> BRINKER_A8 (11797) CKT 1 | L_001695MOSES_5-001697SULSP_SS1_5C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 107.495 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | WHITEPT4A ( 8961) -> HECKER4A ( 8565) CKT 1 | L_008659NAISMITH7A-080039LUCERO7AC1 | 138 | 138 | Branch Amp | 995.72 | - | - | - | - | 110.8897 | 110.085 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | WHITEPT4A ( 8961) -> HECKER4A ( 8565) CKT 1 | SAN_PAT_CON | 138 | 138 | Branch Amp | 995.72 | - | - | - | - | 114.4135 | 109.8185 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | WHITEPT4A ( 8961) -> HECKER4A ( 8565) CKT 2 | L_008659NAISMITH7A-080039LUCERO7AC1 | 138 | 138 | Branch Amp | 995.72 | - | - | - | - | 119.3667 | 118.5008 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | WHITEPT4A ( 8961) -> HECKER4A ( 8565) CKT 2 | SAN_PAT_CON | 138 | 138 | Branch Amp | 995.72 | - | - | - | - | 123.1593 | 118.2139 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | WHITEPT7A ( 8956) -> LONHILL7A ( 8455) CKT 1 | L_008455LONHILL7A-008624GRISSOM7AC1 | 345 | 345 | Branch Amp | 1768.8671 | - | - | - | - | 118.6974 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | WHITEPT7A ( 8956) -> LONHILL7A ( 8455) CKT 1 | M10000254106503-1 | 345 | 345 | Branch Amp | 1768.8671 | - | - | - | - | 120.1788 | - | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | WHITEPT7A ( 8956) -> LONHILL7A ( 8455) CKT 1 | MB106501000025-2 | 345 | 345 | Branch Amp | 1768.8671 | - | - | - | - | 120.0612 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WHITNEYSW ( 243) -> PEORIA ( 228) CKT 1 | 3WT_003522HILLBORO1_8_003523HILLBORO1_9_003519HILLBORO1_3 C 1 | 69 | 69 | Branch Amp | 560.6154 | - | - | - | - | 108.0299 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WHITNEYSW ( 243) -> PEORIA ( 228) CKT 1 | BARDWELL LAKE-ITALY-WAX_9 (SINGLE B TO B ) B | 69 | 69 | Branch Amp | 560.6154 | - | - | - | - | 101.1351 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WHITNEYSW ( 243) -> PEORIA ( 228) CKT 1 | L_002336FORESTON_9-002337ITALY_9C1 | 69 | 69 | Branch Amp | 560.6154 | - | - | - | - | 101.0714 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WHITNEYSW ( 243) -> PEORIA ( 228) CKT 1 | L_002337ITALY_9-002338MILFRDEXN_T9C1 | 69 | 69 | Branch Amp | 560.6154 | - | - | - | - | 102.731 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WHITNEYSW ( 243) -> PEORIA ( 228) CKT 1 | L_002338MILFRDEXN_T9-003523HILLBORO1_9C1 | 69 | 69 | Branch Amp | 560.6154 | - | - | - | - | 102.7451 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WHITNEYSW ( 243) -> PEORIA ( 228) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 69 | 69 | Branch Amp | 560.6154 | - | - | - | - | 105.2963 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WHITNEYSW ( 243) -> PEORIA ( 228) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 69 | 69 | Branch Amp | 560.6154 | - | - | - | - | 103.1879 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WHITNEYSW ( 243) -> PEORIA ( 228) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 69 | 69 | Branch Amp | 560.6154 | - | - | - | - | 100.376 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | 3WT_002433SGVLSW1_5_002434SGVLSW1_8_012434SGVLSW1_3 C 2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 109.1851 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.8901 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.4582 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.1234 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.6739 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.9225 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-1-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.4819 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.1563 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.7146 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1441 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1345 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | BARRETT_CON | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1645 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | BAS_RANCH_CON | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.4784 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 103.6872 | - | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 105.7465 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 105.1011 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.939 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | BEPC_015_2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.1569 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | Big Onion Switch-Batchler Rd SW 345 kV Line(SINGLE B TO B) new load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 108.023 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | BIGBRN__5-NAVARRO & BIGBRN__5-NAVARRO (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 114.1015 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | BLUBIRD_CON | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.8094 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 104.0476 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | CARTWHEEL_CON | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.3134 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | CEDAR HILL - WEBB / COURTLAND 345KV DCKT (DOUBLE TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 105.0881 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | CEDAR HILL-VENUS/TIMBERVIEW 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.885 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | DES_WILL_CON | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.7085 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | DRY_CREEK_CON | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 105.5402 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | DUNHAM - LEWISVILLE DC 345 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.1829 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | E_FRNYPP_CC1_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 106.6604 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | E_FRNYPP_CC2_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 106.7341 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | E_JACKCNTY_CC1_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.0486 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | E_JCKCNTY2_CC1_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.4351 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | E_KMCHI_CC1_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.8018 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | E_KMCHI_CC2_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.8308 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | E_LPCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.2947 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | E_LPCCS_CC2_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.9816 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | E_OECCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.172 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | E_OECCS_CC2_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.177 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | E_PANDA_S_CC1_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.7807 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | E_TNSKA_CC1_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.038 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | E_WCPP_CC1_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.2741 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | E_WHCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.5732 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | E_WHCCS2_CC2_TRAIN | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.2688 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | EDGEWOOD-ROYSE_8 (SINGLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1979 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ELKTON-TRI CORNER 345 KV (SINGLE B TO B) new_load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 104.5727 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | Elrod Switch-Batchler Rd SW 345 kV Line (Double B TO B) new load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 107.2105 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ENNIS - MONTFORTT 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 115.5039 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ENNIS - PEBBLE CREEK 138 KV SWITCH (SINGLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 105.0506 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ENNIS WEST - STERRETT 138 KV (SINGLE B TO B) A REAGOR SPRINGS | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.9942 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ERIKA_CON | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.3377 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | FARMERSVILLE - ROYSE 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 104.6452 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | FORNEY-EAST MESQUITE DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.0221 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_000575JCKCNTY5UN1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.5665 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_000579JCKCNTY8UN1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.3672 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_006100OKLA7AUC0 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.2377 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_079000GRAYUS1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.428 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_144211HRNTSLR_S1US1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.0972 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_150023MCSES_UNIT8UN8 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.5801 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_150042GRSES_UNIT2UN2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.0959 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_150051HLSES_UNIT3UN3 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.4563 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_150052HLSES_UNIT4UN4 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.0184 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_150053HLSES_UNIT5UN5 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.9319 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_150083OLIN_OLING_3UN3 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1811 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_150091LHSES_UNIT1UN1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.1378 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_150092LH2SES_UNIT2UN2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.6916 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_150111CPSES_UNIT1UU1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.6147 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_150112CPSES_UNIT2UU2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 104.0261 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_151371LILY_S1US1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 112.155 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_153361SWRSTRG_B1UB1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.6514 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_153911PNGT1_PV_S1US1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.7769 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_5920EASTDCTIE | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.7139 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_888839BAS_RANCH_POIUC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.4833 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_888854PINEFOREST_POIUS1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1704 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | G_888879BLUBIRD_POIUS1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.949 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | GLASGOW_CON | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 107.4717 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | GRAHAM UNIT 2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.0959 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | GreenRD Switch-Watermill Switch 345 kV Line(Double B TO B) new load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.1474 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | HILLSBORO-ASH CREEK 138 KV (SINGLE B TO B) B | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.7408 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_000192TELICO-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 115.7022 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_000192TELICO-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 115.8676 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_000221TRUMBULL8-002229PEBBLCRK_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 104.2216 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_000221TRUMBULL8-012344GAMMA_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 105.0756 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_000234CHATT-003352PECANST_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.7146 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_000234CHATT-003522HILLBORO1_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.4881 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 108.2263 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001697SULSP_SS1_5-888847CARTWHEEL_POIC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.8334 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.6674 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001904WEBB3_5-002420CHILSW1_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.0825 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001904WEBB3_5-011901BRITNRD1_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.3488 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.1877 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001906VENUS_S5-011901BRITNRD1_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.5006 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001906VENUS_S5-015201FORBESR2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.0779 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001906VENUS_S5-888857OYSTER_POIC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.0567 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001906VENUS_S5-888880DES_WILL_POIC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.3195 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001907VENUS_N5-001940MDLTHELP_N5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.8042 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001907VENUS_N5-002632MILLERRD_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.3916 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001907VENUS_N5-015200FORBESR1_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.3889 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001907VENUS_N5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.9426 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001921LIGGETTA1_5-002632MILLERRD_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.2826 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001928LIGGETT_3T5-002406NORWD1_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.3367 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001931COURTLND1_5-002420CHILSW1_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.4483 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_001931COURTLND1_5-011886TIMBERVW_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.7868 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002217BATCHLRD_8-002466BIGONION_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 108.023 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002217BATCHLRD_8-003159ELROD_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 107.2105 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002241ENNS_W_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.4231 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002290CLEBRN_8-002291CLEBRN_W_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1358 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002291CLEBRN_W_8-037810TNHILL_CO_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.3957 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002315WAX_PMP2_8-002319WAX_PMP1_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.7471 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002315WAX_PMP2_8-002320WAX_N_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.7872 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002316MG_IND_T8-002319WAX_PMP1_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.6008 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002320WAX_N_8-002321WAX_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.6811 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002321WAX_8-012320TMPLTON_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.2873 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002330CRISP1_8-002331ENNS_PMP_T8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 114.5187 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002330CRISP1_8-012329SHANKLSW_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 114.162 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002429WATMLL_8-003083WILMER1_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.3974 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002432TRICRN1_5-003123TRINDAD1_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 107.5622 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002432TRICRN1_5-003124TRINDAD2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 115.867 | 141.5411 | 116.7012 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002432TRICRN1_5-888878ERIKA_POIC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.1176 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 106.7163 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 106.6735 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002465DUCKCOVE_P8-003163DCVERC_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.0274 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002466BIGONION_5-888877GLASGOW_POIC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 107.2217 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002478ROYSE_S5-002485POETRY_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.2231 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_002485POETRY_5-003103SHAMBRGR_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.3311 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003100MARTINLK_5-003102TYLERGND_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.7294 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003100MARTINLK_5-888845DRY_CREEK_POIC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 104.4763 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003109STRYKER_5-003123TRINDAD1_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.7648 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003123TRINDAD1_5-003133RICHLND2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.2785 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003127TRINIDAD_8-003723OLYMPUS_SWC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.5644 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003159ELROD_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 106.5529 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003163DCVERC_8-003169IRONBRG_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.0275 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003165TAWAKRC_T8-003167ENTERPRI_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1722 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003165TAWAKRC_T8-003169IRONBRG_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.135 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003167ENTERPRI_8-003188WILLSPNT_9C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.5794 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003174CANTNSW_8-003181EDGEWOOD_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.0381 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003181EDGEWOOD_8-003188WILLSPNT_9C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.9749 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003352PECANST_8-003473ASHCREEK_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.7548 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003374FILESVALY_5-003389FORTSMITH_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.8988 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003374FILESVALY_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.4665 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003380BIGBRNE_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 111.8654 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003381BIGBRNW_5-003391JEWETT_N5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.3235 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003384STJOHNS_5-003409LAKE_CRK1_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.5875 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003384STJOHNS_5-003711BALE_S5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.9493 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003386OUTLAW_5-046020LIMEST_POI_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.1633 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003386OUTLAW_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.2739 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003388FOURBTHRS_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.2908 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003413KNOBCRKSS_5-003699SALADOSS_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.1652 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003518BLUMPUMP1_8-037810TNHILL_CO_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.4578 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_003723OLYMPUS_SW-003454MONTFTSS__8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.3319 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_005068CACHENA-005133ELMCREEKC2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.6819 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_005915SO_TEX__345A-083211BLKPEARL_P8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.5572 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_006802RY_RYMOND_RC-006829GLNPSSRC_138C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.0412 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_006903BOZE-006908SCURY_RCC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.4156 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_006903BOZE-151372LILY_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 112.843 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_011688THORNTRE_5-143625SAMSON_1_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.2452 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_011688THORNTRE_5-143705DELILA_1_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.7688 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_012329SHANKLSW_8-012344GAMMA_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 105.0806 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_013401TIGERCK_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.019 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_015200FORBESR1_5-068090SAMSWC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.9032 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_015201FORBESR2_5-003389FORTSMITH_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.5995 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_046020LIMEST_POI_5-068091NAVARROC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.3417 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_059909NOVA_138-059998NOVA8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1817 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_143705DELILA_1_5-143757DELILA_2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.0669 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_888845DRY_CREEK_POI-003105ELKTON_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 106.0667 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_888847CARTWHEEL_POI-002464CASHSW_T5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.1128 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_888857OYSTER_POI-068091NAVARROC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.3586 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_888877GLASGOW_POI-068091NAVARROC1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 105.9875 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_888878ERIKA_POI-003105ELKTON_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.9707 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_888880DES_WILL_POI-001916LIGGETTA2_5C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.549 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | L_888889MIDPOINT_POI-003518BLUMPUMP1_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.4748 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | LAKE CREEK - LAKE HALL/TRADINGHOUSE_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.3297 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | LAKE CREEK-RATTLESNAKE/ST JOHNS_5 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.5879 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | LATIMER_REATA_P7F1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.7961 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | LIGGETT - VENUS 345 KV CKT 1/LIGGETT - GENRAL MOTORS 138 KV (DOUBLE B TO B) DIVISION-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.0579 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.712 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | LIGGETT 7330-VENUS 345KV (SINGLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.5525 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | Liggett SW - Miller RD & Liggett SW - Venus SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.8297 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.9336 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | LIGGETT-VENUS DCKT 345KV (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.7245 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.8171 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 112.8409 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | MB210140210145-AAAAA | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.6083 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | MB210140210145-AAAAB | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.8024 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | MB210140210145-AABA | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.3981 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | MB210140210145-ABAAA | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.2976 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | MB210140210145-ABAAB | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1135 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | MB210140210145-ABABB | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1244 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 104.6164 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.8096 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.6022 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ML-EL*TG-TR1 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 113.318 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | MOSES-SULPHUR SPRINGS SW 345-138 KV AUTO SULPHUR SPRINGS SW 345-138 KV AUTO #1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.471 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | NAVARRO - LONG PRAIRIE 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.3899 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | NAVARRO - OUTLAW / LIMESTONE_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 108.7788 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | NAV-CORS_W-MONTFORT_8 (SINGLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.9524 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 113.4261 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | NEW-MONTFORT_8-NAVARRO_8/TRINIDAD_8(DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 102.4128 | 119.5204 | 103.442 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | NORTHWEST CARROLLTON - LEWISVILLE SW (BEPC) 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1543 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | NORWOOD-LIGGETT 345 & MOUNTAIN CREEK - LIGGETT 138 KV DCKT A BLUBONT | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.0857 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | OYSTER_CON | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.3903 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | P7-1_E1>LEG-OUTLAW_ERC | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 106.6636 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.3519 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV DCKT & EAGLE MOUNTAIN - WEATHERFORD 138 KV LINE | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.1934 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | PINEFOREST_CON | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.4877 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | RAMHORN - WILLOW CREEK & BASE CAMP - BENNET DC 345 &138 (COMMON TOWER) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.8214 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | RAMHORN - WILLOW CREEK DC 345 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.1362 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | ROYSE-EDGEWOOD 138 KV (SINGLE B TO B) A | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1979 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | RYBRN_P1-2_CANTON TAP-CANTON | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.9454 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | SALTILLO SW-FARMERSVILLE/CYCLONE SW-BIRTHRIGHT SW 345 KV CYCLONE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.3329 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | SAM - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 106.9189 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | SAM - TIGER CREEK / FOUR BROTHERS - TRADINGHOUSE_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 105.7126 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | SEAGOVILLE SW - FORNEY/TRICORNER DCKT 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 108.7471 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | SHAMBURGER - POETRY_5(SINGLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.3311 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | SHAMBURGER-BLACKFORK/POETRY_8_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.6526 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | T_002474ROYSE1_T5-002473ROYSE1_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.8043 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | T_002483ROYSE3_5-002460ROYSE3_8C1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.8012 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | T_059908NOVA_345-059998NOVA8CT1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.1817 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | TEMPLE__5-BELL_CNTY_E__5___BCE BUS NORMAL (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.2043 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | THORNTREE-BIRTHTRIGHT SW/SALTILLO SW-FARMERSVILLE SW 345 KV CYCLONE (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.6692 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | TIMBERVIEW-SHERRY*CEDAR HILL 345 KV WITH SHERRY AUTO (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.021 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | TNP ONE - GIBSON/HOGCREEK_5 (DOUBLE B TO B ) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.1027 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | TRADINGHOUSE - FOURBROTHERS/TIGER CREEK_5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 104.1828 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | TRICORNER - TYLER GRANDE (single B TO B) new_load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 104.0127 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B) new_load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 115.5399 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 110.9455 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | TRICORNER - TYLER GRANDE / ELKTON_5 (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 109.4268 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 112.6518 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | TRI-TYML-EL (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 116.3154 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | TR-TC1 (DOUBLE B TO B)_B | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | 129.431 | - | 127.0412 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.2056 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.1347 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | TWIN_OAK__5-TNTNP_ONE_3 & TWIN_OAK__5-TNTNP_ONE_3 (CAT_C) (DOUBLE B TO B)-3 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.2498 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | VENUS - BRITTON ROAD / WEBB 345KV DCKT (DOUBLE B TO B) BRITTONRD2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.0381 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | Venus SW - Miller RD & Venus SW - Liggett SW 345 kV(DOUBLE B TO B) New Load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 105.8177 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 107.4455 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | VENUS TO NAVARRO DCKT (DOUBLE B TO B)-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 106.6748 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 106.408 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | VENUS-CEDAR HILL SW 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.8158 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | VENUS-CEDAR HILL*SHERRY 345 KV (DOUBLE B TO B) BRITTON RD | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.7024 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | VENUS-FORT SMITH SW 345 KV (SINGLE B TO B) new load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.0342 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | VENUS-LIGGETT 345KV/EXECUTIVE PARKWAY-CEDAR HILL 138KV DCKT (DOUBLE B TO B) A-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.0308 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.2814 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | VENUS-LIGGETT 345KV/LIGGETT-GENERAL MOTORS 138KV DCKT (DOUBLE B TO B) A-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.0612 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | VENUS-SAM SW 345 KV (SINGLE B TO B) new load | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.4318 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | VIKING_CON | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.0318 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | WATERMILL - SARGENT RD / WEST LEVEE 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.6454 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | WAXAHACHI-WAXAHACHI OFC 69KV/ENNIS-STERRETT 138KV (DOUBLE B TO B) A REAGOR | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.2497 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | WEBB - CEDAR HILL / CENTURY 345KV DCKT (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.7263 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | WEBB - VENUS / BRITTON 345KV DCKT (DOUBLE B TO B) BRITTON RD | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.8819 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | WEST LEVEE - WATERMILL/SARGENT RD 345 KV (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.6531 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.2747 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.5608 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | WSHACK_LATIMER_P7 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.242 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | XFMR-HANDLEYC_8-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.4563 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | XFMR-HANDLEYC_8-3 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.9319 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | XFMR-HANDLEYD_8-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.0184 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | XFMR-LKHB_1T8-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.1378 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | XFMR-LKHB_2T8-2 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 103.6916 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | XFMR-MTCK_8T8-8 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 102.5801 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | XFMR-WHCCS2_5-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 101.7655 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILL_WHT_8 ( 3287) -> SEVENPTS_8 ( 3264) CKT 1 | XFMR-WLFHMDPT_5-1 | 138 | 138 | Branch Amp | 1008.2711 | - | - | - | - | 100.5606 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILLOW ( 588) -> SWIMMER ( 543) CKT 1 | BEPC_242 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 118.4615 | 112.2134 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILLOW ( 588) -> SWIMMER ( 543) CKT 1 | BEPC_283_1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 102.1568 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILLOW ( 588) -> SWIMMER ( 543) CKT 1 | L_000541RENO-000595KEETERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 116.8082 | 110.4869 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILLOW ( 588) -> SWIMMER ( 543) CKT 1 | L_000570WISECNTY-000571HIDEOUTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 101.3493 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILLOW ( 588) -> SWIMMER ( 543) CKT 1 | L_000571HIDEOUT-000579JCKCNTY8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 102.1448 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILLOW ( 588) -> SWIMMER ( 543) CKT 1 | L_000579JCKCNTY8-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 118.9063 | 112.5213 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILLOW ( 588) -> SWIMMER ( 543) CKT 1 | L_000595KEETER-000596COTTONDALEC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.5667 | 111.224 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WILLOW ( 588) -> SWIMMER ( 543) CKT 1 | L_000596COTTONDALE-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 118.8976 | 112.5125 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | DERMOTT - BLUFF CREEK SW & DERMOTT - ENNIS CREEK 138 KV (DOUBLE B TO B) 2023 WIN - FUTURE | 138 | 138 | Branch Amp | 748.8818 | 127.9688 | 111.9631 | 132.564 | 134.6975 | 152.9728 | 153.5265 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | DERMOTT - BLUFF CREEK SW & ENNIS CREEK - GOLDEN SW 138 KV (DOUBLE B TO B) 2023 WIN - FUTURE | 138 | 138 | Branch Amp | 748.8818 | 116.9382 | 105.9132 | 121.4351 | 124.2387 | 140.4036 | 141.1057 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | DERMOTT - BLUFF CREEK SW 138 KV (SINGLE B TO B) 2023 SUM - FUTURE | 138 | 138 | Branch Amp | 748.8818 | 107.4758 | - | 111.1717 | 114.3486 | 124.2559 | 126.6487 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | L_001064SUN_8-001311SACROC_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | - | 104.7372 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | L_001304DEEPCRK_8-001305SNYDER_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | - | 102.7164 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | L_001304DEEPCRK_8-001311SACROC_8C1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | - | 103.2049 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | L_001309BLUFCKTA_8-001310KNAPP_8C1 | 138 | 138 | Branch Amp | 748.8818 | 107.6005 | - | 111.2812 | 114.4498 | 124.3531 | 126.7368 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | L_001310KNAPP_8-001366ONC900041_TAPC1 | 138 | 138 | Branch Amp | 748.8818 | 110.1698 | - | 113.8425 | 116.8777 | 126.6983 | 128.9402 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | L_001312SCURYCHV_8-011130KNDRSACRC_8C1 | 138 | 138 | Branch Amp | 748.8818 | 114.723 | 101.4345 | 118.3059 | 121.0205 | 130.7632 | 133.0219 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | L_001312SCURYCHV_8-011306DERMOTT_8C1 | 138 | 138 | Branch Amp | 748.8818 | 116.643 | 102.532 | 120.213 | 122.8873 | 132.6709 | 134.953 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | L_001366ONC900041_TAP-011130KNDRSACRC_8C1 | 138 | 138 | Branch Amp | 748.8818 | 111.2091 | - | 114.8675 | 117.8326 | 127.6373 | 129.8722 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | L_888842IRON_BELT_POI-059910VOLTAC1 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | - | 100.6125 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | Ranger Camp-Barber Lake Dbl Ckt 138 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | 110.141 | - | 106.2722 | 107.484 | 112.8999 | 121.2107 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | Ranger Camp-Tonkawa Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | - | 103.0656 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 1 & TONKAWA SW - SCURRY COUNTY SOUTH SW CKT 2 345 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 748.8818 | - | - | - | 111.5033 | 122.7151 | 126.1622 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | WETT LONG DRAW - WETT VOLTA 345 KV LINE (SINGLE B TO B)-2 | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | - | 100.6125 | -
TONCOR | FAR_WEST | FAR_WEST | FAR_WEST, FAR_WEST | WILLOWVAL_8 ( 1301) -> ONC900119_TAP (901303) CKT 1 | XFMR-RANGER_5 | 138 | 138 | Branch Amp | 748.8818 | - | 130.8578 | - | - | - | - | -
TETRTX,TAEPTN | WEST | WEST | WEST, WEST | WINT2A ( 6333) -> STMBOAT2A (60332) CKT 1 | L_006326ROBT2A-006327CEDARGAP2AC1 | 69 | 69 | Branch Amp | 209.1849 | 108.0457 | - | 106.523 | 106.2756 | 106.047 | 108.205 | -
TETRTX,TAEPTN | WEST | WEST | WEST, WEST | WINT2A ( 6333) -> STMBOAT2A (60332) CKT 1 | L_006327CEDARGAP2A-006636ABSO2BC1 | 69 | 69 | Branch Amp | 209.1849 | 134.7073 | - | 131.84 | 130.119 | 131.9796 | 132.3571 | -
TETRTX,TAEPTN | WEST | WEST | WEST, WEST | WINT2A ( 6333) -> STMBOAT2A (60332) CKT 1 | M2056620529-1 | 69 | 69 | Branch Amp | 209.1849 | 134.7059 | - | 131.8388 | 130.1199 | 131.9801 | 132.3578 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | ALVORD - WISE COUNTY 138 KV & BENNETT RD - CHICO WEST 69 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 103.5082 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.4825 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | BEPC_005_1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 103.2595 | 125.5352 | 116.61 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | BEPC_006 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 106.4351 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | BEPC_014_2 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.1698 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | BEPC_114 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 108.1368 | 101.4791 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | BEPC_242 | 138 | 138 | Branch Amp | 1313.6809 | - | - | 100.6615 | 107.5712 | 128.5802 | 120.5465 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | BEPC_243 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 101.3281 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | BEPC_245 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 103.5421 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | BEPC_246 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 107.2213 | 100.6697 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | BEPC_2541 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 107.2679 | 100.6408 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | BEPC_432 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.1933 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | BEPC_458 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 104.7217 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | BLUBIRD_CON | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.4354 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | E_FRNYPP_CC1_TRAIN | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.5854 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | E_FRNYPP_CC2_TRAIN | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.6001 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | E_PANDA_S_CC1_TRAIN | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.1194 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | E_TGCCS_CC1_TRAIN | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.0157 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | EAGLE MOUNTAIN - HICKS/WEATHERFORD 138 KV (DOUBLE B TO B) NEWLOAD | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.4193 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | EAGLE MTN-WEATHERFORD 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.9958 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | G_120041MLSES_UNIT1UL1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.0095 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | G_120042MLSES_UNIT2UL2 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.0167 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | G_120043MLSES_UNIT3UL3 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.0239 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000501HILLTOP8-000508RIKERC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 116.4958 | 109.2661 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000508RIKER-000516ZIONHILLC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 116.4936 | 109.2641 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000516ZIONHILL-000543SWIMMERC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 117.7797 | 110.4865 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000541RENO-000595KEETERC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 105.9667 | 127.0504 | 118.9492 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000543SWIMMER-000588WILLOWC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 118.3474 | 111.0327 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000570WISECNTY-001564CHCOGHLL1_8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 103.2169 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000576RHOME-000585CHISOLMC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.5745 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000579JCKCNTY8-000580WSTBROOKC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 118.6596 | 111.3329 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000579JCKCNTY8-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | 100.5052 | 107.4204 | 128.566 | 120.405 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000580WSTBROOK-000588WILLOWC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 118.4556 | 111.1372 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000595KEETER-000596COTTONDALEC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 106.4918 | 127.5994 | 119.4786 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000596COTTONDALE-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | 100.5072 | 107.4218 | 128.5676 | 120.406 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000620BOWIE8-000741DYEMOUNDC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 107.5544 | 100.9606 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000684SPRING-000691VALLEYVIEWC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 108.6687 | 102.0759 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000690MYRA-000691VALLEYVIEWC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 109.2751 | 102.6699 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000690MYRA-000695MUENSTERC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 106.3314 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000695MUENSTER-000730WOLFRIDGEC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 107.0235 | 100.4942 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000730WOLFRIDGE-000746STJO8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 104.2397 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000741DYEMOUND-000762HARDYSWC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 107.1451 | 100.5918 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_000746STJO8-000762HARDYSWC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 106.9087 | 100.389 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_001561ALVORD1_8-001562CHCOWEST_T8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.756 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_001562CHCOWEST_T8-001564CHCOGHLL1_8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 101.8478 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_001592WTHFRDSS_8-015015FLAT_RCK_T8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 101.4658 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.9302 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_001839STONCRK_8-140002SHER1_TLC1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.0974 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_001906VENUS_S5-001939MDLTHELP_S5C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.2553 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_002062AZLE1_8-015015FLAT_RCK_T8C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 101.4603 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_002437FRNY1_5-150189FRNYPP_1_5C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.5973 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | L_002437FRNY1_5-150190FRNYPP_2_5C1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.5906 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.1513 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.4356 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | PARKER-EAGLE MTN*HICKS 345 KV DCKT & EAGLE MOUNTAIN - WEATHERFORD 138 KV LINE | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 106.6807 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.5208 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | WISE COUNTY - ALVORD TAP 138 KV (SINGLE B TO B) | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 103.7584 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | WISE COUNTY (BEC) - ALVORD/BRIDGEPORT(BEC) (DOUBLE B TO B) A | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | 103.2087 | 125.4835 | 116.5614 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | XFMR-MARTINLK_5-1 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.0095 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | XFMR-MARTINLK_5-2 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.0167 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> BRDGPORT_8 ( 1565) CKT 1 | XFMR-MARTINLK_5-3 | 138 | 138 | Branch Amp | 1313.6809 | - | - | - | - | 100.0239 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WISECNTY ( 570) -> CHCOGHLL1_8 ( 1564) CKT 1 | BENNETT RD-WISE CTY 138 KV | 138 | 138 | Branch Amp | 748.8818 | - | - | - | - | 101.1005 | - | -
TONCOR | EAST | NORTH | EAST, NORTH | WOODARD_5 (11699) -> UMBRA_POI (888843) CKT 1 | VALLEY SW-PACIFIC SW/VALLEY S SW - PARIS SW345 KV (DOUBLE B TO B) | 345 | 345 | Branch Amp | 1725.3568 | - | - | - | 102.9176 | 101.5939 | 103.1608 | -
TONCOR | EAST | EAST | EAST, EAST | WORTHAM1_9 ( 3605) -> WRTHMPOD_9 ( 3487) CKT 1 | L_003597GROESBECP_8-888888FEWELL_S1C1 | 69 | 69 | Branch Amp | 292.8588 | - | - | - | 132.9064 | 249.3395 | 214.7142 | -
TSTEC , TAEPTC | COAST | COAST | COAST, COAST | WRBRTN8 (5607) -> VICTORIA4A (8172) CKT 1 | Pre-contingency | 138 | 138 | Amps | 510.4111 | - | - | - | 123.8592 | 156.7347 | 110.858 | -
TONCOR | NORTH_CE | EAST | NORTH_CE, EAST | WRTHMPOD_9 ( 3487) -> RICHLAND1_9 ( 3486) CKT 1 | L_003597GROESBECP_8-888888FEWELL_S1C1 | 69 | 69 | Branch Amp | 292.8588 | - | - | - | 114.4306 | 229.8466 | 195.9645 | -
TONCOR | EAST | EAST | EAST, EAST | WRTHMPOD_9 ( 3487) -> WORTHAM1_9 ( 3605) CKT 1 | L_003632MEXIA2_1_8-003634GROES_SE1_8C1 | 69 | 69 | Branch Amp | 292.8588 | 100.675 | - | 100.6393 | 100.4861 | - | 100.2541 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WSTBROOK ( 580) -> WILLOW ( 588) CKT 1 | BEPC_242 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 118.8068 | 112.5569 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WSTBROOK ( 580) -> WILLOW ( 588) CKT 1 | BEPC_283_1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 102.4974 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WSTBROOK ( 580) -> WILLOW ( 588) CKT 1 | L_000541RENO-000595KEETERC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.1531 | 110.8298 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WSTBROOK ( 580) -> WILLOW ( 588) CKT 1 | L_000570WISECNTY-000571HIDEOUTC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 101.6898 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WSTBROOK ( 580) -> WILLOW ( 588) CKT 1 | L_000571HIDEOUT-000579JCKCNTY8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 102.4854 | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WSTBROOK ( 580) -> WILLOW ( 588) CKT 1 | L_000579JCKCNTY8-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 119.2516 | 112.8651 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WSTBROOK ( 580) -> WILLOW ( 588) CKT 1 | L_000595KEETER-000596COTTONDALEC1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 117.9118 | 111.5672 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WSTBROOK ( 580) -> WILLOW ( 588) CKT 1 | L_000596COTTONDALE-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1606.5397 | - | - | - | - | 119.2428 | 112.8563 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WTHFRDSS_8 ( 1592) -> FLAT_RCK_T8 (15015) CKT 1 | BEPC_006 | 138 | 138 | Branch Amp | 968.1075 | - | - | - | 103.3344 | 120.5707 | 110.378 | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WTHFRDSS_8 ( 1592) -> FLAT_RCK_T8 (15015) CKT 1 | BEPC_283_1 | 138 | 138 | Branch Amp | 968.1075 | - | - | - | - | 104.3994 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WTHFRDSS_8 ( 1592) -> FLAT_RCK_T8 (15015) CKT 1 | L_000570WISECNTY-000571HIDEOUTC1 | 138 | 138 | Branch Amp | 968.1075 | - | - | - | - | 103.7308 | - | -
TONCOR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WTHFRDSS_8 ( 1592) -> FLAT_RCK_T8 (15015) CKT 1 | L_000571HIDEOUT-000579JCKCNTY8C1 | 138 | 138 | Branch Amp | 968.1075 | - | - | - | - | 104.4314 | - | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WYLIESW ( 833) -> FIREWHEEL ( 821) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.8449 | - | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WYLIESW ( 833) -> FIREWHEEL ( 821) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.36 | - | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WYLIESW ( 833) -> FIREWHEEL ( 821) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9005 | - | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WYLIESW ( 833) -> FIREWHEEL ( 821) CKT 1 | ALLEN SW-MOSES 345-138 KV AUTO & ROYSE-WEILAND 345 KV W/O MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.4078 | - | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WYLIESW ( 833) -> FIREWHEEL ( 821) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.1839 | 101.3248 | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WYLIESW ( 833) -> FIREWHEEL ( 821) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | 101.6133 | 106.6603 | 103.5353 | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WYLIESW ( 833) -> FIREWHEEL ( 821) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 104.2353 | 101.3656 | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WYLIESW ( 833) -> FIREWHEEL ( 821) CKT 1 | ALLEN SW-ROYSE 345 KV & ALLEN SW-MOSES 345-138 KV AUTO W/O MOSES 345-138 KV AUTO #1-2 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | 101.6433 | 106.6915 | 103.581 | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WYLIESW ( 833) -> FIREWHEEL ( 821) CKT 1 | L_000802APOLLO-000806JUPITERC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.4898 | - | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WYLIESW ( 833) -> FIREWHEEL ( 821) CKT 1 | L_000802APOLLO-000828LOOKOUTC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | 100.2035 | 101.4608 | 101.5315 | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WYLIESW ( 833) -> FIREWHEEL ( 821) CKT 1 | L_000806JUPITER-000829COLLEGE8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 102.7668 | 101.8046 | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WYLIESW ( 833) -> FIREWHEEL ( 821) CKT 1 | L_000833WYLIESW-000856MILLWOODC1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 100.9034 | - | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WYLIESW ( 833) -> FIREWHEEL ( 821) CKT 1 | L_002471ROYSE_S_8-002702RCKWL_8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 103.6086 | 102.0788 | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WYLIESW ( 833) -> FIREWHEEL ( 821) CKT 1 | L_002701GARL1_8-012736ROWLETT_T8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2541 | - | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WYLIESW ( 833) -> FIREWHEEL ( 821) CKT 1 | L_002702RCKWL_8-012736ROWLETT_T8C1 | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.2526 | - | -
TGAR | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | WYLIESW ( 833) -> FIREWHEEL ( 821) CKT 1 | ROYSE-OATES/RICHARDSON EAST DCKT 138 KV (DOUBLE B TO B) | 138 | 138 | Branch Amp | 1137.9656 | - | - | - | - | 101.7298 | 100.0187 | -
TAEPTC | SOUTHERN | SOUTHERN | SOUTHERN, SOUTHERN | ZAPATA4A ( 8299) -> ZAPATA0A (89443) CKT T1 | G_163371BRP_ZPT1UB1 | 138 | 12.47 | Branch MVA | 25 | 100.7449 | - | 100.1365 | - | - | - | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ZIONHILL ( 516) -> RIKER ( 508) CKT 1 | BEPC_242 | 138 | 138 | Branch Amp | 1623.2745 | - | - | - | - | 111.6731 | 105.5296 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ZIONHILL ( 516) -> RIKER ( 508) CKT 1 | L_000541RENO-000595KEETERC1 | 138 | 138 | Branch Amp | 1623.2745 | - | - | - | - | 110.0453 | 103.8295 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ZIONHILL ( 516) -> RIKER ( 508) CKT 1 | L_000579JCKCNTY8-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1623.2745 | - | - | - | - | 112.1063 | 105.8288 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ZIONHILL ( 516) -> RIKER ( 508) CKT 1 | L_000595KEETER-000596COTTONDALEC1 | 138 | 138 | Branch Amp | 1623.2745 | - | - | - | - | 110.7904 | 104.5533 | -
TBREC | NORTH_CE | NORTH_CE | NORTH_CE, NORTH_CE | ZIONHILL ( 516) -> RIKER ( 508) CKT 1 | L_000596COTTONDALE-001598BALSORA_8C1 | 138 | 138 | Branch Amp | 1623.2745 | - | - | - | - | 112.0969 | 105.8194 | -

## Interfaces
Interface | Contingency | Category | Limit | Value | 2026sum % | 2027min % | 2027sum % | 2029sum % | 2030sum % | 2030sum_EHV % | Notes
Panhandle | Pre-contingency | Interface | 3239.4001 | 3414.7262 | - | - | - | - | 105.4123 | 100.081 | -
Panhandle | 3WT_013125TDADTMOD_5_003127TRINIDAD_8_120151TRSES_UNIT6 C 1 | Interface MW | 3239.4001 | 3242.0249 | - | - | - | - | - | 100.1625 | -
Panhandle | AEN_P1-1_GEN_SH5A+5C | Interface MW | 3239.4001 | 3244.6631 | - | - | - | - | - | 100.3057 | -
Panhandle | AEN_P2HLJ345_RB_570_610_1(94OF224): | Interface MW | 3239.4001 | 3249.3044 | - | - | - | - | - | 100.2744 | -
Panhandle | AEN_P2HO345_RB_1201_1203(107OF224):-1 | Interface MW | 3239.4001 | 3248.2886 | - | - | - | - | - | 100.0021 | -
Panhandle | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV MOSES 345-138 KV AUTO #1-2-2 | Interface MW | 3239.4001 | 3239.4697 | - | - | - | - | - | 100.0024 | -
Panhandle | ALLEN SW-MOSES 345-138 KV AUTO & WEILAND-SULPHUR SPRINGS 345 KV W/O MOSES 345-138 KV AUTO #1-2-2 | Interface MW | 3239.4001 | 3239.479 | - | - | - | - | - | 100.0074 | -
Panhandle | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W AUTO-2 | Interface MW | 3239.4001 | 3239.6401 | - | - | - | - | - | 100.0028 | -
Panhandle | ALLENSW-MOSES 345KV AUTO & MOSES-SLPHRSPRGS 345KV AUTO W/O AUTO-2 | Interface MW | 3239.4001 | 3239.49 | - | - | - | - | - | 100.1405 | -
Panhandle | ARGENTA_CON | Interface MW | 3239.4001 | 3243.95 | - | - | - | - | - | 101.2352 | -
Panhandle | BAS_RANCH_CON | Interface MW | 3239.4001 | 3241.8542 | - | - | - | 100.0758 | - | 101.2352 | -
Panhandle | BAS_RANCH_CON | Interface MW | 3239.4001 | 3279.4133 | - | - | - | 100.0758 | - | 100.0868 | -
Panhandle | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | Interface MW | 3239.4001 | 3242.2126 | - | - | - | - | - | 100.0475 | -
Panhandle | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | Interface MW | 3239.4001 | 3240.9385 | - | - | - | - | - | 100.1203 | -
Panhandle | BELL COUNTY E - BRANGUS/LITTLE POND_5 (DOUBLE B TO B ) | Interface MW | 3239.4001 | 3243.2971 | - | - | - | - | - | 100.0831 | -
Panhandle | BELLCNTY E - LITTLE POND / BRANGUS - GIBSON_5 (DOUBLE B TO B ) | Interface MW | 3239.4001 | 3242.0916 | - | - | - | - | - | 100.6106 | -
Panhandle | BENBROOK-SYCAMORE CRK*MITCHELL BEND-ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | Interface MW | 3239.4001 | 3259.1807 | - | - | - | - | - | 100.0087 | -
Panhandle | BEPC_22 | Interface MW | 3239.4001 | 3239.6819 | - | - | - | - | - | 100.0173 | -
Panhandle | BEPC_23_2 | Interface MW | 3239.4001 | 3239.9604 | - | - | - | - | - | 100.0203 | -
Panhandle | BEPC_311_2 | Interface MW | 3239.4001 | 3240.0569 | - | - | - | - | - | 100.0548 | -
Panhandle | BITTER CREEK SW (LCRA) - CATTLEMEN SW & BITTER CREEK SW (LCRA) - SWEETWATER EAST 345 KV (DOUBLE B TO B) | Interface MW | 3239.4001 | 3241.1755 | - | - | - | - | - | 100.6092 | -
Panhandle | BLUBIRD_CON | Interface MW | 3239.4001 | 3259.135 | - | - | - | - | - | 100.0457 | -
Panhandle | BRANGUS/LITTLE POND - HOG CREEK/GIBSON_5 (DOUBLE B TO B ) | Interface MW | 3239.4001 | 3240.8794 | - | - | - | - | - | 100.0467 | -
Panhandle | CACTUS_CON | Interface MW | 3239.4001 | 3240.9124 | - | - | - | - | - | 100.0195 | -
Panhandle | CLUTCH_CITY_CON | Interface MW | 3239.4001 | 3240.0325 | - | - | - | - | - | 100.2114 | -
Panhandle | DERMOTT - KIRCHHOF CKT 1 & DERMOTT - KIRCHHOF CKT 2 345 KV (DOUBLE B TO B) C | Interface MW | 3239.4001 | 3246.248 | - | - | - | - | - | 100.1989 | -
Panhandle | DERMOTT - KIRCHHOF CKT 1 345 KV WIN 2023 - FUTURE (SINGLE B TO B) | Interface MW | 3239.4001 | 3245.8423 | - | - | - | - | - | 100.0689 | -
Panhandle | DRY_CREEK_CON | Interface MW | 3239.4001 | 3241.6309 | - | - | - | - | - | 100.042 | -
Panhandle | DUNE - WINK/YUKON 138 KV 2019 SUM - FUTURE (DOUBLE B TO B) | Interface MW | 3239.4001 | 3240.7607 | - | - | - | - | - | 100.3189 | -
Panhandle | E_AMOCOOIL_CC2_TRAIN | Interface MW | 3239.4001 | 3249.7312 | - | - | - | - | - | 100.3839 | -
Panhandle | E_AMOCOOIL_CC2_TRAIN_NSO | Interface MW | 3239.4001 | 3251.8362 | - | - | - | - | - | 100.4909 | -
Panhandle | E_B_DAVIS_CC1_TRAIN | Interface MW | 3239.4001 | 3255.304 | - | - | - | - | - | 100.4284 | -
Panhandle | E_BASTEN_CC1_TRAIN | Interface MW | 3239.4001 | 3253.2761 | - | - | - | - | - | 100.0729 | -
Panhandle | E_BOSQUESW_CC1_TRAIN | Interface MW | 3239.4001 | 3241.7605 | - | - | - | - | - | 100.3206 | -
Panhandle | E_BOSQUESW_CC2_TRAIN | Interface MW | 3239.4001 | 3249.7844 | - | - | - | - | - | 100.3943 | -
Panhandle | E_BRAUNIG_CC1_TRAIN | Interface MW | 3239.4001 | 3252.1726 | - | - | - | - | - | 100.411 | -
Panhandle | E_BTE_CC1_TRAIN | Interface MW | 3239.4001 | 3252.7139 | - | - | - | - | - | 100.3497 | -
Panhandle | E_BVE_CC1_TRAIN | Interface MW | 3239.4001 | 3250.729 | - | - | - | - | - | 100.1518 | -
Panhandle | E_BYU_CC1_TRAIN | Interface MW | 3239.4001 | 3244.3164 | - | - | - | - | - | 100.0364 | -
Panhandle | E_CAL_CC1_TRAIN | Interface MW | 3239.4001 | 3240.5789 | - | - | - | - | - | 100.0787 | -
Panhandle | E_CBEC_CC1_TRAIN | Interface MW | 3239.4001 | 3241.95 | - | - | - | - | - | 100.0835 | -
Panhandle | E_CBEC_CC2_TRAIN | Interface MW | 3239.4001 | 3242.1064 | - | - | - | - | - | 100.8591 | -
Panhandle | E_CBECII_CC3_TRAIN | Interface MW | 3239.4001 | 3267.2312 | - | - | - | - | - | 100.3004 | -
Panhandle | E_CBY4_CC1_TRAIN | Interface MW | 3239.4001 | 3249.1311 | - | - | - | - | - | 100.2471 | -
Panhandle | E_CCEC_CC1_TRAIN | Interface MW | 3239.4001 | 3247.4038 | - | - | - | - | - | 100.428 | -
Panhandle | E_CHE_CC1_TRAIN | Interface MW | 3239.4001 | 3253.2664 | - | - | - | - | - | 100.4229 | -
Panhandle | E_CVC_CC1_TRAIN | Interface MW | 3239.4001 | 3253.1008 | - | - | - | - | - | 100.8506 | -
Panhandle | E_DDPEC_CC1_TRAIN | Interface MW | 3239.4001 | 3266.9536 | - | - | - | - | - | 100.1351 | -
Panhandle | E_DIB_CC1_TRAIN | Interface MW | 3239.4001 | 3243.7761 | - | - | - | - | - | 100.3178 | -
Panhandle | E_DUKE_CC1_TRAIN | Interface MW | 3239.4001 | 3249.6953 | - | - | - | - | - | 100.1833 | -
Panhandle | E_ETCCS_CC1_TRAIN | Interface MW | 3239.4001 | 3245.3369 | - | - | - | - | - | 100.3955 | -
Panhandle | E_FERGCC_CC1_TRAIN | Interface MW | 3239.4001 | 3252.2112 | - | - | - | - | - | 100.0229 | -
Panhandle | E_FLCNS_CC1_TRAIN | Interface MW | 3239.4001 | 3240.1418 | - | - | - | - | - | 100.294 | -
Panhandle | E_FORMOSA_CC1_TRAIN | Interface MW | 3239.4001 | 3248.9233 | - | - | - | - | - | 100.194 | -
Panhandle | E_FREC_CC1_TRAIN | Interface MW | 3239.4001 | 3245.686 | - | - | - | - | - | 100.2848 | -
Panhandle | E_FREC_CC2_TRAIN | Interface MW | 3239.4001 | 3248.6274 | - | - | - | - | - | 100.7173 | -
Panhandle | E_FRNYPP_CC1_TRAIN | Interface MW | 3239.4001 | 3262.636 | - | - | - | - | - | 100.7164 | -
Panhandle | E_FRNYPP_CC2_TRAIN | Interface MW | 3239.4001 | 3262.6072 | - | - | - | - | - | 100.6422 | -
Panhandle | E_FTR_CC1_TRAIN | Interface MW | 3239.4001 | 3260.2041 | - | - | - | - | - | 100.3382 | -
Panhandle | E_GUADG_CC1_TRAIN | Interface MW | 3239.4001 | 3250.3564 | - | - | - | - | - | 100.3344 | -
Panhandle | E_GUADG_CC2_TRAIN | Interface MW | 3239.4001 | 3250.2319 | - | - | - | - | - | 100.325 | -
Panhandle | E_INGLCOSW_CC1_TRAIN | Interface MW | 3239.4001 | 3249.927 | - | - | - | - | - | 100.3841 | -
Panhandle | E_JACKCNTY_CC1_TRAIN | Interface MW | 3239.4001 | 3251.843 | - | - | - | - | - | 100.4425 | -
Panhandle | E_JCKCNTY2_CC1_TRAIN | Interface MW | 3239.4001 | 3253.7351 | - | - | - | - | - | 100.405 | -
Panhandle | E_KMCHI_CC1_TRAIN | Interface MW | 3239.4001 | 3252.5203 | - | - | - | - | - | 100.4086 | -
Panhandle | E_KMCHI_CC2_TRAIN | Interface MW | 3239.4001 | 3252.635 | - | - | - | - | - | 100.2269 | -
Panhandle | E_LGE_CC1_TRAIN | Interface MW | 3239.4001 | 3246.752 | - | - | - | - | - | 100.3758 | -
Panhandle | E_LOSTPI_CC1_TRAIN | Interface MW | 3239.4001 | 3251.5745 | - | - | - | - | - | 100.3516 | -
Panhandle | E_LPCCS_CC1_TRAIN | Interface MW | 3239.4001 | 3250.7903 | - | - | - | - | - | 100.3184 | -
Panhandle | E_LPCCS_CC2_TRAIN | Interface MW | 3239.4001 | 3249.7141 | - | - | - | - | - | 100.5117 | -
Panhandle | E_NEDIN_CC1_TRAIN | Interface MW | 3239.4001 | 3255.9751 | - | - | - | - | - | 100.4875 | -
Panhandle | E_NUECES_B_CC1_TRAIN | Interface MW | 3239.4001 | 3255.1924 | - | - | - | - | - | 100.4045 | -
Panhandle | E_OECCS_CC1_TRAIN | Interface MW | 3239.4001 | 3252.5032 | - | - | - | - | - | 100.4059 | -
Panhandle | E_OECCS_CC2_TRAIN | Interface MW | 3239.4001 | 3252.5481 | - | - | - | - | - | 100.5092 | -
Panhandle | E_PANDA_S_CC1_TRAIN | Interface MW | 3239.4001 | 3255.8958 | - | - | - | - | - | 100.5903 | -
Panhandle | E_PANDA_T1_CC1_TRAIN | Interface MW | 3239.4001 | 3258.5212 | - | - | - | - | - | 100.5956 | -
Panhandle | E_PANDA_T2_CC1_TRAIN | Interface MW | 3239.4001 | 3258.6943 | - | - | - | - | - | 100.2832 | -
Panhandle | E_PSA_CC1_TRAIN | Interface MW | 3239.4001 | 3248.5752 | - | - | - | - | - | 100.3028 | -
Panhandle | E_PSG_CC1_TRAIN | Interface MW | 3239.4001 | 3249.2078 | - | - | - | - | - | 100.119 | -
Panhandle | E_QALSW_CC1_TRAIN | Interface MW | 3239.4001 | 3243.2542 | - | - | - | - | - | 100.1148 | -
Panhandle | E_QALSW_CC2_TRAIN | Interface MW | 3239.4001 | 3243.1204 | - | - | - | - | - | 100.0427 | -
Panhandle | E_RAYBURN_CC1_TRAIN | Interface MW | 3239.4001 | 3240.7844 | - | - | - | - | - | 100.1278 | -
Panhandle | E_TEN_CC1_TRAIN | Interface MW | 3239.4001 | 3243.54 | - | - | - | - | - | 100.5979 | -
Panhandle | E_TGCCS_CC1_TRAIN | Interface MW | 3239.4001 | 3258.7698 | - | - | - | - | - | 100.1539 | -
Panhandle | E_THW_CC1_TRAIN | Interface MW | 3239.4001 | 3244.3853 | - | - | - | - | - | 100.1539 | -
Panhandle | E_THW_CC2_TRAIN | Interface MW | 3239.4001 | 3244.3855 | - | - | - | - | - | 100.0724 | -
Panhandle | E_TNSKA_CC1_TRAIN | Interface MW | 3239.4001 | 3241.7451 | - | - | - | - | - | 100.1825 | -
Panhandle | E_TXCTY_CC1_TRAIN | Interface MW | 3239.4001 | 3245.312 | - | - | - | - | - | 100.1317 | -
Panhandle | E_VICTORIA_CC1_TRAIN | Interface MW | 3239.4001 | 3243.667 | - | - | - | - | - | 100.6032 | -
Panhandle | E_WCPP_CC1_TRAIN | Interface MW | 3239.4001 | 3258.9392 | - | - | - | - | - | 100.5677 | -
Panhandle | E_WHCCS_CC1_TRAIN | Interface MW | 3239.4001 | 3257.7898 | - | - | - | - | - | 100.9155 | -
Panhandle | E_WHCCS2_CC2_TRAIN | Interface MW | 3239.4001 | 3269.0576 | - | - | - | - | - | 100.0504 | -
Panhandle | E5DVA1C1_1_B | Interface MW | 3239.4001 | 3241.0312 | - | - | - | - | - | 100.3204 | -
Panhandle | ELMAX_POI_Con | Interface MW | 3239.4001 | 3249.7798 | - | - | - | - | - | 100.0465 | -
Panhandle | ERIKA_CON | Interface MW | 3239.4001 | 3240.9055 | - | - | - | - | - | 100.4894 | -
Panhandle | G_000575JCKCNTY5UN1 | Interface MW | 3239.4001 | 3255.2544 | - | - | - | - | - | 100.3443 | -
Panhandle | G_000579JCKCNTY8UN1 | Interface MW | 3239.4001 | 3250.5527 | - | - | - | - | - | 100.1634 | -
Panhandle | G_001877MITCHBND_5UN1 | Interface MW | 3239.4001 | 3244.6926 | - | - | - | - | - | 100.0635 | -
Panhandle | G_003306STEKLY_DAM_5US1 | Interface MW | 3239.4001 | 3241.4583 | - | - | - | - | - | 100.3975 | -
Panhandle | G_003321REDLAND_5UN1 | Interface MW | 3239.4001 | 3252.2773 | - | - | - | - | - | 100.0214 | -
Panhandle | G_003377LITTLEPOND_5US1 | Interface MW | 3239.4001 | 3240.0938 | - | - | - | - | - | 100.0193 | -
Panhandle | G_003420TEMP_PEC__8US1 | Interface MW | 3239.4001 | 3240.0266 | - | - | - | - | - | 100.0119 | -
Panhandle | G_003478NAVARRO1_8US1 | Interface MW | 3239.4001 | 3239.7871 | - | - | - | - | - | 100.0147 | -
Panhandle | G_003706GIBSON_5US1 | Interface MW | 3239.4001 | 3239.8765 | - | - | - | - | - | 100.0206 | -
Panhandle | G_003707CANNON_8US1 | Interface MW | 3239.4001 | 3240.0688 | - | - | - | - | - | 100.0218 | -
Panhandle | G_003717TORTOISE_5US1 | Interface MW | 3239.4001 | 3240.1069 | - | - | - | - | - | 100.4605 | -
Panhandle | G_006100OKLA7AUC0 | Interface MW | 3239.4001 | 3254.3186 | - | - | - | - | - | 100.0386 | -
Panhandle | G_006111RILEY7BUS1 | Interface MW | 3239.4001 | 3240.6494 | - | - | - | - | - | 100.0572 | -
Panhandle | G_007041L_JOHNDU5_1YUN1 | Interface MW | 3239.4001 | 3241.252 | - | - | - | - | - | 100.3067 | -
Panhandle | G_007044L_MARION5_1YUN1 | Interface MW | 3239.4001 | 3249.335 | - | - | - | - | - | 100.3336 | -
Panhandle | G_007048L_GARFIE5_1YUN1 | Interface MW | 3239.4001 | 3250.2078 | - | - | - | - | - | 100.0589 | -
Panhandle | G_008249ANGSTRM7AUS1 | Interface MW | 3239.4001 | 3241.3071 | - | - | - | - | - | 100.0557 | -
Panhandle | G_008573BONILLA7AUW1 | Interface MW | 3239.4001 | 3241.2061 | - | - | - | - | - | 100.0023 | -
Panhandle | G_008707DRYFRIOUS1 | Interface MW | 3239.4001 | 3239.4744 | - | - | - | - | - | 100.3374 | -
Panhandle | G_010012METEOR_5US1 | Interface MW | 3239.4001 | 3250.3291 | - | - | - | - | - | 100.1124 | -
Panhandle | G_039703TNFM524___1UN1 | Interface MW | 3239.4001 | 3243.0417 | - | - | - | - | - | 100.4664 | -
Panhandle | G_040000CEDARP_B345AUC1 | Interface MW | 3239.4001 | 3254.5098 | - | - | - | - | - | 100.263 | -
Panhandle | G_040700GRNBYU__B345UN1 | Interface MW | 3239.4001 | 3247.9182 | - | - | - | - | - | 100.2629 | -
Panhandle | G_040710GRNBYU_POI8AUN1 | Interface MW | 3239.4001 | 3247.9158 | - | - | - | - | - | 100.0728 | -
Panhandle | G_042199BSTCM12_36_8US1 | Interface MW | 3239.4001 | 3241.7573 | - | - | - | - | - | 100.0343 | -
Panhandle | G_042440HAWKIN_POI_5US1 | Interface MW | 3239.4001 | 3240.5105 | - | - | - | - | - | 100.0191 | -
Panhandle | G_043060SPEDWY_POI_5US1 | Interface MW | 3239.4001 | 3240.0195 | - | - | - | - | - | 100.2025 | -
Panhandle | G_043060SPEDWY_POI_5US2 | Interface MW | 3239.4001 | 3245.96 | - | - | - | - | - | 100.3603 | -
Panhandle | G_043060SPEDWY_POI_5US4 | Interface MW | 3239.4001 | 3251.0725 | - | - | - | - | - | 100.1731 | -
Panhandle | G_043340GLFTIE_POI_8UN1 | Interface MW | 3239.4001 | 3245.0063 | - | - | - | - | - | 100.0073 | -
Panhandle | G_043990ELMATO_POI_5US1 | Interface MW | 3239.4001 | 3239.6365 | - | - | - | - | - | 100.2368 | -
Panhandle | G_043990ELMATO_POI_5US2 | Interface MW | 3239.4001 | 3247.0708 | - | - | - | - | - | 100.0064 | -
Panhandle | G_044040BAILEY_POI_5US1 | Interface MW | 3239.4001 | 3239.6067 | - | - | - | - | - | 100.2685 | -
Panhandle | G_045500T_H_W__POI_5UN1 | Interface MW | 3239.4001 | 3248.0967 | - | - | - | - | - | 100.2686 | -
Panhandle | G_045515T_H_W__POI_8UN1 | Interface MW | 3239.4001 | 3248.1016 | - | - | - | - | - | 100.1259 | -
Panhandle | G_048262SOWYCK26TP_8UN1 | Interface MW | 3239.4001 | 3243.4778 | - | - | - | - | - | 100.0314 | -
Panhandle | G_059904COTTONWOODUS1 | Interface MW | 3239.4001 | 3240.4185 | - | - | - | - | - | 100.1802 | -
Panhandle | G_060700GAUSS7AUS1 | Interface MW | 3239.4001 | 3245.2361 | - | - | - | - | - | 100.1041 | -
Panhandle | G_060716SGSA4AUS1 | Interface MW | 3239.4001 | 3242.7722 | - | - | - | - | - | 100.0173 | -
Panhandle | G_068004PHNTMHLUS1 | Interface MW | 3239.4001 | 3239.9609 | - | - | - | - | - | 100.0101 | -
Panhandle | G_068014OPENSKYUS1 | Interface MW | 3239.4001 | 3239.7263 | - | - | - | - | - | 100.017 | -
Panhandle | G_068025WRANGLERUS1 | Interface MW | 3239.4001 | 3239.9524 | - | - | - | - | - | 100.1699 | -
Panhandle | G_068051REATAUS1 | Interface MW | 3239.4001 | 3244.9033 | - | - | - | - | - | 100.1745 | -
Panhandle | G_079007YELLOWWOLFUS1 | Interface MW | 3239.4001 | 3245.052 | - | - | - | - | - | 100.0982 | -
Panhandle | G_080039LUCERO7AUS1 | Interface MW | 3239.4001 | 3242.5808 | - | - | - | - | - | 100.0599 | -
Panhandle | G_080039LUCERO7AUS2 | Interface MW | 3239.4001 | 3241.3411 | - | - | - | - | - | 100.0932 | -
Panhandle | G_080219LOBO7AUS1 | Interface MW | 3239.4001 | 3242.4189 | - | - | - | - | - | 100.0203 | -
Panhandle | G_080219LOBO7AUS2 | Interface MW | 3239.4001 | 3240.0581 | - | - | - | - | - | 100.0199 | -
Panhandle | G_080355DELSOL7AUS1 | Interface MW | 3239.4001 | 3240.0444 | - | - | - | - | - | 100.0151 | -
Panhandle | G_110011WAP_WAP_G1UN1 | Interface MW | 3239.4001 | 3239.8904 | - | - | - | - | - | 100.0151 | -
Panhandle | G_110012WAP_WAP_G2UN2 | Interface MW | 3239.4001 | 3239.8909 | - | - | - | - | - | 100.0747 | -
Panhandle | G_110013WAP_WAP_G3UN3 | Interface MW | 3239.4001 | 3241.8193 | - | - | - | - | - | 100.316 | -
Panhandle | G_110014WAP_WAP_G4UN4 | Interface MW | 3239.4001 | 3249.6353 | - | - | - | - | - | 100.0064 | -
Panhandle | G_110015WAP_WAP_G5UL5 | Interface MW | 3239.4001 | 3239.6064 | - | - | - | - | - | 100.4441 | -
Panhandle | G_110016WAP_WAP_G6UL6 | Interface MW | 3239.4001 | 3253.7856 | - | - | - | - | - | 100.3696 | -
Panhandle | G_110017WAP_WAP_G7UL7 | Interface MW | 3239.4001 | 3251.374 | - | - | - | - | - | 100.3944 | -
Panhandle | G_110018WAP_WAP_G8UL8 | Interface MW | 3239.4001 | 3252.1753 | - | - | - | - | - | 100.5058 | -
Panhandle | G_110071CBY_CBY_G1UN1 | Interface MW | 3239.4001 | 3255.7852 | - | - | - | - | - | 100.5112 | -
Panhandle | G_110072CBY_CBY_G2UN2 | Interface MW | 3239.4001 | 3255.959 | - | - | - | - | - | 100.0216 | -
Panhandle | G_110146DOW_DOW_GT96UP1 | Interface MW | 3239.4001 | 3240.1003 | - | - | - | - | - | 100.0003 | -
Panhandle | G_110280AMO_AMOCO_G1UPE | Interface MW | 3239.4001 | 3239.4084 | - | - | - | - | - | 100.0003 | -
Panhandle | G_110281AMO_AMOCO_G2UPE | Interface MW | 3239.4001 | 3239.4092 | - | - | - | - | - | 100.0002 | -
Panhandle | G_110282AMO_AMOCO_G3UPE | Interface MW | 3239.4001 | 3239.4082 | - | - | - | - | - | 101.0199 | -
Panhandle | G_110351STP_STP_G1UU1 | Interface MW | 3239.4001 | 3272.4402 | - | - | - | - | - | 101.0082 | -
Panhandle | G_110352STP_STP_G2UU2 | Interface MW | 3239.4001 | 3272.0593 | - | - | - | - | - | 100.0197 | -
Panhandle | G_110662CHE_CHEST1UPE | Interface MW | 3239.4001 | 3240.0378 | - | - | - | - | - | 100.0155 | -
Panhandle | G_110701LHM_CVC_G4UPE | Interface MW | 3239.4001 | 3239.9038 | - | - | - | - | - | 100.04 | -
Panhandle | G_110731BTE_BTE_G1UPE | Interface MW | 3239.4001 | 3240.6968 | - | - | - | - | - | 100.0744 | -
Panhandle | G_111631DANISH_S1US1 | Interface MW | 3239.4001 | 3241.8101 | - | - | - | - | - | 100.0152 | -
Panhandle | G_111861BCK_S1US1 | Interface MW | 3239.4001 | 3239.8936 | - | - | - | - | - | 100.0177 | -
Panhandle | G_111862BCK_S2US2 | Interface MW | 3239.4001 | 3239.9729 | - | - | - | - | - | 100.0171 | -
Panhandle | G_112091SBE_S1US1 | Interface MW | 3239.4001 | 3239.9548 | - | - | - | - | - | 100.0452 | -
Panhandle | G_112141PLN_S1US1 | Interface MW | 3239.4001 | 3240.8635 | - | - | - | - | - | 100.0452 | -
Panhandle | G_112146PLN_S2US2 | Interface MW | 3239.4001 | 3240.8633 | - | - | - | - | - | 100.2836 | -
Panhandle | G_112261SPACECI_S1US1 | Interface MW | 3239.4001 | 3248.5862 | - | - | - | - | - | 100.0294 | -
Panhandle | G_112351OLDHCKRY_S1US1 | Interface MW | 3239.4001 | 3240.3513 | - | - | - | - | - | 100.0038 | -
Panhandle | G_112612ROW_S2US2 | Interface MW | 3239.4001 | 3239.5237 | - | - | - | - | - | 100.0188 | -
Panhandle | G_113051GARCITAS_S1US1 | Interface MW | 3239.4001 | 3240.01 | - | - | - | - | - | 100.2922 | -
Panhandle | G_113111LUNIS_CK_S1US1 | Interface MW | 3239.4001 | 3248.8647 | - | - | - | - | - | 100.0426 | -
Panhandle | G_113251MLZSLR_S1US1 | Interface MW | 3239.4001 | 3240.7798 | - | - | - | - | - | 100.0411 | -
Panhandle | G_113341TNGLWDPV_S1US1 | Interface MW | 3239.4001 | 3240.7312 | - | - | - | - | - | 100.039 | -
Panhandle | G_113751CASCADE_S1US1 | Interface MW | 3239.4001 | 3240.665 | - | - | - | - | - | 100.1945 | -
Panhandle | G_113921PARLIMNT_S1US1 | Interface MW | 3239.4001 | 3245.6995 | - | - | - | - | - | 100.5623 | -
Panhandle | G_120041MLSES_UNIT1UL1 | Interface MW | 3239.4001 | 3257.6147 | - | - | - | - | - | 100.5628 | -
Panhandle | G_120042MLSES_UNIT2UL2 | Interface MW | 3239.4001 | 3257.6318 | - | - | - | - | - | 100.568 | -
Panhandle | G_120043MLSES_UNIT3UL3 | Interface MW | 3239.4001 | 3257.8005 | - | - | - | - | - | 100.0121 | -
Panhandle | G_120071TNP__TNP_O_1UL1 | Interface MW | 3239.4001 | 3239.7913 | - | - | - | - | - | 100.0121 | -
Panhandle | G_120072TNP__TNP_O_2UL2 | Interface MW | 3239.4001 | 3239.7913 | - | - | - | - | - | 100.6287 | -
Panhandle | G_120131OGSES_UNIT1AUL1 | Interface MW | 3239.4001 | 3259.7651 | - | - | - | - | - | 100.6287 | -
Panhandle | G_120132OGSES_UNIT2UL2 | Interface MW | 3239.4001 | 3259.7656 | - | - | - | - | - | 100.0154 | -
Panhandle | G_120141SCSES_UNIT1AUN1 | Interface MW | 3239.4001 | 3239.8989 | - | - | - | - | - | 100.3017 | -
Panhandle | G_120142SCSES_UNIT2UN2 | Interface MW | 3239.4001 | 3249.1724 | - | - | - | - | - | 100.081 | -
Panhandle | G_120151TRSES_UNIT6UN6 | Interface MW | 3239.4001 | 3242.0249 | - | - | - | - | - | 100.0134 | -
Panhandle | G_120751GRIMES_S1US1 | Interface MW | 3239.4001 | 3239.835 | - | - | - | - | - | 100.0195 | -
Panhandle | G_132311ECEC_G1UN1 | Interface MW | 3239.4001 | 3240.0315 | - | - | - | - | - | 100.0195 | -
Panhandle | G_132312ECEC_G2UN2 | Interface MW | 3239.4001 | 3240.0317 | - | - | - | - | - | 100.0107 | -
Panhandle | G_132781CASLGP_UNIT1US1 | Interface MW | 3239.4001 | 3239.7471 | - | - | - | - | - | 100.0105 | -
Panhandle | G_133841WAYMARK_W1US1 | Interface MW | 3239.4001 | 3239.74 | - | - | - | - | - | 100.0102 | -
Panhandle | G_134091OBERON_S1US1 | Interface MW | 3239.4001 | 3239.731 | - | - | - | - | - | 100.0166 | -
Panhandle | G_134951EUNICE_S1US1 | Interface MW | 3239.4001 | 3239.9375 | - | - | - | - | - | 100.0522 | -
Panhandle | G_134953EUNICE_S2US2 | Interface MW | 3239.4001 | 3241.0896 | - | - | - | - | - | 100.0151 | -
Panhandle | G_135111ARAGORN_S1US1 | Interface MW | 3239.4001 | 3239.8889 | - | - | - | - | - | 100.0396 | -
Panhandle | G_135321REDBARN_S1US1 | Interface MW | 3239.4001 | 3240.6814 | - | - | - | - | - | 100.0237 | -
Panhandle | G_135501RDOSLR_S1US1 | Interface MW | 3239.4001 | 3240.1675 | - | - | - | - | - | 100.1051 | -
Panhandle | G_136341TRBNT_PV_S1US1 | Interface MW | 3239.4001 | 3242.8037 | - | - | - | - | - | 100.1314 | -
Panhandle | G_141607AEEC_5UN1 | Interface MW | 3239.4001 | 3243.6562 | - | - | - | - | - | 100.1099 | -
Panhandle | G_141609ELK_G3UN6 | Interface MW | 3239.4001 | 3242.9614 | - | - | - | - | - | 100.028 | -
Panhandle | G_143116SRNOVA2_S1US1 | Interface MW | 3239.4001 | 3240.3059 | - | - | - | - | - | 100.085 | -
Panhandle | G_144011BRSFORK_S1US1 | Interface MW | 3239.4001 | 3242.1538 | - | - | - | - | - | 100.014 | -
Panhandle | G_144064INERTIA_S1US1 | Interface MW | 3239.4001 | 3239.8545 | - | - | - | - | - | 100.0237 | -
Panhandle | G_144161NOVA2SLR_S1US1 | Interface MW | 3239.4001 | 3240.1682 | - | - | - | - | - | 100.0309 | -
Panhandle | G_144261EIFSLR_S1US1 | Interface MW | 3239.4001 | 3240.3999 | - | - | - | - | - | 100.0297 | -
Panhandle | G_144561BAKE_SLR_S1US1 | Interface MW | 3239.4001 | 3240.363 | - | - | - | - | - | 100.0297 | -
Panhandle | G_144562BAKE_SLR_S2US2 | Interface MW | 3239.4001 | 3240.3628 | - | - | - | - | - | 100.4295 | -
Panhandle | G_150023MCSES_UNIT8UN8 | Interface MW | 3239.4001 | 3253.3132 | - | - | - | - | - | 100.0941 | -
Panhandle | G_150041GRSES_UNIT1UN1 | Interface MW | 3239.4001 | 3242.447 | - | - | - | - | - | 100.2359 | -
Panhandle | G_150042GRSES_UNIT2UN2 | Interface MW | 3239.4001 | 3247.0427 | - | - | - | - | - | 100.2337 | -
Panhandle | G_150051HLSES_UNIT3UN3 | Interface MW | 3239.4001 | 3246.9722 | - | - | - | - | - | 100.2957 | -
Panhandle | G_150052HLSES_UNIT4UN4 | Interface MW | 3239.4001 | 3248.9775 | - | - | - | - | - | 100.2912 | -
Panhandle | G_150053HLSES_UNIT5UN5 | Interface MW | 3239.4001 | 3248.8333 | - | - | - | - | - | 100.0162 | -
Panhandle | G_150083OLIN_OLING_3UN3 | Interface MW | 3239.4001 | 3239.9258 | - | - | - | - | - | 100.2506 | -
Panhandle | G_150091LHSES_UNIT1UN1 | Interface MW | 3239.4001 | 3247.5166 | - | - | - | - | - | 100.3755 | -
Panhandle | G_150092LH2SES_UNIT2UN2 | Interface MW | 3239.4001 | 3251.5645 | - | - | - | - | - | 100.6004 | -
Panhandle | G_150101LEG_LEG_G1UL1 | Interface MW | 3239.4001 | 3258.8494 | - | - | - | - | - | 100.611 | -
Panhandle | G_150102LEG_LEG_G2UL2 | Interface MW | 3239.4001 | 3259.1921 | - | - | - | - | - | 101.017 | -
Panhandle | G_150111CPSES_UNIT1UU1 | Interface MW | 3239.4001 | 3272.3452 | - | - | - | - | - | 101.0084 | -
Panhandle | G_150112CPSES_UNIT2UU2 | Interface MW | 3239.4001 | 3272.0674 | - | - | - | - | - | 100.059 | -
Panhandle | G_150133MIL_MILLERG3UN3 | Interface MW | 3239.4001 | 3241.3103 | - | - | - | - | - | 100.0931 | -
Panhandle | G_150151MDANP_CT1UN1 | Interface MW | 3239.4001 | 3242.417 | - | - | - | - | - | 100.1081 | -
Panhandle | G_150152MDANP_CT2UN2 | Interface MW | 3239.4001 | 3242.9004 | - | - | - | - | - | 100.1102 | -
Panhandle | G_150153MDANP_CT3UN3 | Interface MW | 3239.4001 | 3242.9707 | - | - | - | - | - | 100.1102 | -
Panhandle | G_150154MDANP_CT4UN4 | Interface MW | 3239.4001 | 3242.969 | - | - | - | - | - | 100.1044 | -
Panhandle | G_150155MDANP_CT5UN5 | Interface MW | 3239.4001 | 3242.7808 | - | - | - | - | - | 100.1062 | -
Panhandle | G_150156MDANP_CT6UN6 | Interface MW | 3239.4001 | 3242.8389 | - | - | - | - | - | 100.716 | -
Panhandle | G_150741SCES_UNIT1UL1 | Interface MW | 3239.4001 | 3262.5952 | - | - | - | - | - | 100.0028 | -
Panhandle | G_152381PISGAH_S1US1 | Interface MW | 3239.4001 | 3239.49 | - | - | - | - | - | 100.0144 | -
Panhandle | G_152431MERCURY_S1US1 | Interface MW | 3239.4001 | 3239.8672 | - | - | - | - | - | 100.0144 | -
Panhandle | G_152481MERCURY_S2US2 | Interface MW | 3239.4001 | 3239.8674 | - | - | - | - | - | 100.05 | -
Panhandle | G_153141PORT_SLR_S1US1 | Interface MW | 3239.4001 | 3241.0195 | - | - | - | - | - | 100.0171 | -
Panhandle | G_153291BIGELM_S1US1 | Interface MW | 3239.4001 | 3239.9536 | - | - | - | - | - | 100.0105 | -
Panhandle | G_153381FIVEWLLS_S1US1 | Interface MW | 3239.4001 | 3239.7395 | - | - | - | - | - | 100.1569 | -
Panhandle | G_153631DORADO_S1US1 | Interface MW | 3239.4001 | 3244.4841 | - | - | - | - | - | 100.0516 | -
Panhandle | G_153681HALO_SLR_S1US1 | Interface MW | 3239.4001 | 3241.071 | - | - | - | - | - | 100.0797 | -
Panhandle | G_153781JAGUARSP_S1US1 | Interface MW | 3239.4001 | 3241.9812 | - | - | - | - | - | 100.3476 | -
Panhandle | G_153911PNGT1_PV_S1US1 | Interface MW | 3239.4001 | 3250.6614 | - | - | - | - | - | 100.0268 | -
Panhandle | G_154061DIVER_PV_S1US1 | Interface MW | 3239.4001 | 3240.2693 | - | - | - | - | - | 100.0458 | -
Panhandle | G_154161LANGER_S1US1 | Interface MW | 3239.4001 | 3240.8826 | - | - | - | - | - | 100.1639 | -
Panhandle | G_154221ASHCRKSL_S1US1 | Interface MW | 3239.4001 | 3244.7095 | - | - | - | - | - | 100.1235 | -
Panhandle | G_154281CLINGHAM_S1US1 | Interface MW | 3239.4001 | 3243.4011 | - | - | - | - | - | 100.163 | -
Panhandle | G_154331CMPDREPV_S1US1 | Interface MW | 3239.4001 | 3244.6802 | - | - | - | - | - | 100.1554 | -
Panhandle | G_160101B_D_B_DAVIG1UN1 | Interface MW | 3239.4001 | 3244.4355 | - | - | - | - | - | 100.2468 | -
Panhandle | G_160131SAN_SANMIGG1UL1 | Interface MW | 3239.4001 | 3247.396 | - | - | - | - | - | 100.0241 | -
Panhandle | G_160151INGLCOS_CTG1UPE | Interface MW | 3239.4001 | 3240.1819 | - | - | - | - | - | 100.0241 | -
Panhandle | G_160152INGLCOS_CTG2UPE | Interface MW | 3239.4001 | 3240.1819 | - | - | - | - | - | 100.0195 | -
Panhandle | G_160153INGLCOSW_STGUPE | Interface MW | 3239.4001 | 3240.0325 | - | - | - | - | - | 100.0145 | -
Panhandle | G_160201LGE_LGE_GT1UPE | Interface MW | 3239.4001 | 3239.8691 | - | - | - | - | - | 100.0144 | -
Panhandle | G_160202LGE_LGE_GT2UPE | Interface MW | 3239.4001 | 3239.8679 | - | - | - | - | - | 100.0066 | -
Panhandle | G_160263CCEC_ST1UPE | Interface MW | 3239.4001 | 3239.6147 | - | - | - | - | - | 100.0054 | -
Panhandle | G_161651PATWND_UNIT1UW1 | Interface MW | 3239.4001 | 3239.5762 | - | - | - | - | - | 100.0182 | -
Panhandle | G_162541MCLNSLR_S1US1 | Interface MW | 3239.4001 | 3239.9905 | - | - | - | - | - | 100.0152 | -
Panhandle | G_162791HRZN_SLR_S1US1 | Interface MW | 3239.4001 | 3239.8911 | - | - | - | - | - | 100.0189 | -
Panhandle | G_163221CORAZON_S1US1 | Interface MW | 3239.4001 | 3240.0125 | - | - | - | - | - | 100.0936 | -
Panhandle | G_163521PEREGRN_S1US1 | Interface MW | 3239.4001 | 3242.4333 | - | - | - | - | - | 100.1705 | -
Panhandle | G_163641CHARGER_S1US1 | Interface MW | 3239.4001 | 3244.9221 | - | - | - | - | - | 100.0566 | -
Panhandle | G_163691REDONDA_S1US1 | Interface MW | 3239.4001 | 3241.2346 | - | - | - | - | - | 100.0608 | -
Panhandle | G_163881TULSITA_S1US1 | Interface MW | 3239.4001 | 3241.3711 | - | - | - | - | - | 100.2419 | -
Panhandle | G_163931OUTPOST_S1US1 | Interface MW | 3239.4001 | 3247.2351 | - | - | - | - | - | 100.0002 | -
Panhandle | G_170071GID_GIDEONG1UN1 | Interface MW | 3239.4001 | 3239.408 | - | - | - | - | - | 100.0048 | -
Panhandle | G_170072GID_GIDEONG2UN2 | Interface MW | 3239.4001 | 3239.5544 | - | - | - | - | - | 100.1995 | -
Panhandle | G_170073GID_GIDEONG3UN3 | Interface MW | 3239.4001 | 3245.8618 | - | - | - | - | - | 100.4316 | -
Panhandle | G_170101FPPYD_FPP_G1UL1 | Interface MW | 3239.4001 | 3253.3823 | - | - | - | - | - | 100.4287 | -
Panhandle | G_170102FPPYD_FPP_G2UL2 | Interface MW | 3239.4001 | 3253.2859 | - | - | - | - | - | 100.2782 | -
Panhandle | G_170103FPPYD_FPP_G3UL3 | Interface MW | 3239.4001 | 3248.4136 | - | - | - | - | - | 100.633 | -
Panhandle | G_170126CALAVER_JKS2UL2 | Interface MW | 3239.4001 | 3259.906 | - | - | - | - | - | 100.0766 | -
Panhandle | G_170191HAY_HAYSENG1UN1 | Interface MW | 3239.4001 | 3241.8818 | - | - | - | - | - | 100.0948 | -
Panhandle | G_170192HAY_HAYSENG2UN2 | Interface MW | 3239.4001 | 3242.4719 | - | - | - | - | - | 100.0939 | -
Panhandle | G_170193HAY_HAYSENG3UN3 | Interface MW | 3239.4001 | 3242.4409 | - | - | - | - | - | 100.0795 | -
Panhandle | G_170194HAY_HAYSENG4UN4 | Interface MW | 3239.4001 | 3241.9751 | - | - | - | - | - | 100.3034 | -
Panhandle | G_170671CACHENA_S1US1 | Interface MW | 3239.4001 | 3249.2297 | - | - | - | - | - | 100.0382 | -
Panhandle | G_170821EBELLSLR_S1US1 | Interface MW | 3239.4001 | 3240.636 | - | - | - | - | - | 100.0161 | -
Panhandle | G_170901SHLA_S1US1 | Interface MW | 3239.4001 | 3239.9207 | - | - | - | - | - | 100.0161 | -
Panhandle | G_170951SHLA_S1US1 | Interface MW | 3239.4001 | 3239.9207 | - | - | - | - | - | 100.0148 | -
Panhandle | G_171021AURE_SLR_S1US1 | Interface MW | 3239.4001 | 3239.8811 | - | - | - | - | - | 100.0501 | -
Panhandle | G_171091MPP_N1UN1 | Interface MW | 3239.4001 | 3241.0227 | - | - | - | - | - | 100.049 | -
Panhandle | G_171111MANDORLA_S1US1 | Interface MW | 3239.4001 | 3240.9863 | - | - | - | - | - | 100.0652 | -
Panhandle | G_171161SYPBRNCH_S1US1 | Interface MW | 3239.4001 | 3241.5112 | - | - | - | - | - | 100.0209 | -
Panhandle | G_182501RAMBLR_S1US1 | Interface MW | 3239.4001 | 3240.0757 | - | - | - | - | - | 100.056 | -
Panhandle | G_183172GALLOWAY_S1US1 | Interface MW | 3239.4001 | 3241.2148 | - | - | - | - | - | 100.0292 | -
Panhandle | G_183451CROWDEDS_S1US1 | Interface MW | 3239.4001 | 3240.3457 | - | - | - | - | - | 100.0194 | -
Panhandle | G_183571SUNRAY_S1US1 | Interface MW | 3239.4001 | 3240.0293 | - | - | - | - | - | 100.0177 | -
Panhandle | G_183781ANG_PV_S1US1 | Interface MW | 3239.4001 | 3239.9724 | - | - | - | - | - | 100.4067 | -
Panhandle | G_5920EASTDCTIE | Interface MW | 3239.4001 | 3252.574 | - | - | - | - | - | 100.0651 | -
Panhandle | G_6103NORTHDCTIE | Interface MW | 3239.4001 | 3241.5078 | - | - | - | - | - | 101.234 | -
Panhandle | G_888839BAS_RANCH_POIUC1 | Interface MW | 3239.4001 | 3241.8552 | - | - | - | 100.0758 | - | 101.234 | -
Panhandle | G_888839BAS_RANCH_POIUC1 | Interface MW | 3239.4001 | 3279.375 | - | - | - | 100.0758 | - | 100.3164 | -
Panhandle | G_888841ELMAX_POIUN1 | Interface MW | 3239.4001 | 3249.6492 | - | - | - | - | - | 100.0075 | -
Panhandle | G_888845DRY_CREEK_POIUS1 | Interface MW | 3239.4001 | 3239.6443 | - | - | - | - | - | 100.3266 | -
Panhandle | G_888851TRIFECTA_POIUN1 | Interface MW | 3239.4001 | 3249.9802 | - | - | - | - | - | 100.0411 | -
Panhandle | G_888852LIATRIS_POIUN1 | Interface MW | 3239.4001 | 3240.73 | - | - | - | - | - | 100.0891 | -
Panhandle | G_888854PINEFOREST_POIUS1 | Interface MW | 3239.4001 | 3242.2854 | - | - | - | - | - | 100.2007 | -
Panhandle | G_888856HOLLY_POIUS1 | Interface MW | 3239.4001 | 3245.9009 | - | - | - | - | - | 100.0791 | -
Panhandle | G_888856HOLLY_POIUS2 | Interface MW | 3239.4001 | 3241.9609 | - | - | - | - | - | 100.0329 | -
Panhandle | G_888857OYSTER_POIUS1 | Interface MW | 3239.4001 | 3240.4668 | - | - | - | - | - | 100.1097 | -
Panhandle | G_888858ARGENTA_POIUS1 | Interface MW | 3239.4001 | 3242.9531 | - | - | - | - | - | 100.0112 | -
Panhandle | G_888861LEON_POIUS1 | Interface MW | 3239.4001 | 3239.7632 | - | - | - | - | - | 100.0334 | -
Panhandle | G_888865MALDIVES_POIUS1 | Interface MW | 3239.4001 | 3240.4827 | - | - | - | - | - | 100.1657 | -
Panhandle | G_888866HANSON_POIUS1 | Interface MW | 3239.4001 | 3244.7668 | - | - | - | - | - | 100.2205 | -
Panhandle | G_888870BTTM_GRSS_POIUS1 | Interface MW | 3239.4001 | 3246.5439 | - | - | - | - | - | 100.0844 | -
Panhandle | G_888874VIKING_POIUS1 | Interface MW | 3239.4001 | 3242.1335 | - | - | - | - | - | 100.0203 | -
Panhandle | G_888877GLASGOW_POIUS1 | Interface MW | 3239.4001 | 3240.0579 | - | - | - | - | - | 100.0193 | -
Panhandle | G_888878ERIKA_POIUS1 | Interface MW | 3239.4001 | 3240.0247 | - | - | - | - | - | 100.5967 | -
Panhandle | G_888879BLUBIRD_POIUS1 | Interface MW | 3239.4001 | 3258.731 | - | - | - | - | - | 100.1443 | -
Panhandle | G_888881SOLAC_POIUS1 | Interface MW | 3239.4001 | 3244.0737 | - | - | - | - | - | 100.0753 | -
Panhandle | G_888882BUZIOS_POIUS1 | Interface MW | 3239.4001 | 3241.8401 | - | - | - | - | - | 100.1347 | -
Panhandle | G_888883QUANT_POIUS1 | Interface MW | 3239.4001 | 3243.7634 | - | - | - | - | - | 100.0184 | -
Panhandle | G_888885GALAC_POIUS1 | Interface MW | 3239.4001 | 3239.9971 | - | - | - | - | - | 100.6229 | -
Panhandle | G_RIO_TRAIN | Interface MW | 3239.4001 | 3259.5791 | - | - | - | - | - | 100.025 | -
Panhandle | GALAC_CON | Interface MW | 3239.4001 | 3240.2095 | - | - | - | - | - | 100.0992 | -
Panhandle | GLASGOW_CON | Interface MW | 3239.4001 | 3242.6138 | - | - | - | - | - | 100.2359 | -
Panhandle | GRAHAM UNIT 2 | Interface MW | 3239.4001 | 3247.0427 | - | - | - | - | - | 100.1867 | -
Panhandle | HANSON_CON | Interface MW | 3239.4001 | 3245.4475 | - | - | - | - | - | 100.0057 | -
Panhandle | HIGHNOON_CON | Interface MW | 3239.4001 | 3239.5847 | - | - | - | - | - | 100.1037 | -
Panhandle | HOLLY_CON | Interface MW | 3239.4001 | 3242.7578 | - | - | - | - | - | 100.0196 | -
Panhandle | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | Interface MW | 3239.4001 | 3240.0337 | - | - | - | - | - | 100.0259 | -
Panhandle | J5CT1_B | Interface MW | 3239.4001 | 3240.2407 | - | - | - | - | - | 100.0264 | -
Panhandle | J5CT2_B | Interface MW | 3239.4001 | 3240.2556 | - | - | - | - | - | 100.0264 | -
Panhandle | J5CT3_B | Interface MW | 3239.4001 | 3240.2559 | - | - | - | - | - | 100.0259 | -
Panhandle | J5GSU1_B | Interface MW | 3239.4001 | 3240.2407 | - | - | - | - | - | 100.0264 | -
Panhandle | J5GSU2_B | Interface MW | 3239.4001 | 3240.2556 | - | - | - | - | - | 100.0264 | -
Panhandle | J5GSU3_B | Interface MW | 3239.4001 | 3240.2559 | - | - | - | - | - | 100.1649 | -
Panhandle | J5GSU4_B | Interface MW | 3239.4001 | 3244.7427 | - | - | - | - | - | 100.623 | -
Panhandle | J5LCA1C1_B | Interface MW | 3239.4001 | 3259.5806 | - | - | - | - | - | 100.1649 | -
Panhandle | J5ST1_B | Interface MW | 3239.4001 | 3244.7427 | - | - | - | - | - | 100.0008 | -
Panhandle | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | Interface MW | 3239.4001 | 3239.4248 | - | - | - | - | - | 100.0212 | -
Panhandle | L_000004IOLA-120332BLUEJAY_8C1 | Interface MW | 3239.4001 | 3240.0879 | - | - | - | - | - | 100.1833 | -
Panhandle | L_000842GPL_KINGMTSW-000843GPL_KINGMTTPC1 | Interface MW | 3239.4001 | 3245.3367 | - | - | - | - | - | 100.2962 | -
Panhandle | L_000844GPL_NEVILLSW-000860GPL_GIRVINSWC1 | Interface MW | 3239.4001 | 3248.9944 | - | - | - | - | - | 100.1051 | -
Panhandle | L_000860GPL_GIRVINSW-136341TRBNT_PV_S1C1 | Interface MW | 3239.4001 | 3242.804 | - | - | - | - | - | 100.2131 | -
Panhandle | L_001097CULBERSON_8-007389L_PINNAC8_1YC1 | Interface MW | 3239.4001 | 3246.3035 | - | - | - | - | - | 100.1648 | -
Panhandle | L_001141HOLTSS_8-132313ECEC_8C1 | Interface MW | 3239.4001 | 3244.7388 | - | - | - | - | - | 100.1079 | -
Panhandle | L_001444BROWN_5-151756RADN_TLINEC1 | Interface MW | 3239.4001 | 3242.897 | - | - | - | - | - | 100.9629 | -
Panhandle | L_001690VALLYSES1_5-140078KMCHI_2_5C1 | Interface MW | 3239.4001 | 3270.5913 | - | - | - | - | - | 100.4064 | -
Panhandle | L_001695MOSES_5-005925DCEASTC1 | Interface MW | 3239.4001 | 3252.5659 | - | - | - | - | - | 100.0949 | -
Panhandle | L_001730W_KRUM_5-152087NOBLESLR_5C1 | Interface MW | 3239.4001 | 3242.4739 | - | - | - | - | - | 100.5092 | -
Panhandle | L_001839STONCRK_8-140002SHER1_TLC1 | Interface MW | 3239.4001 | 3255.8958 | - | - | - | - | - | 100.7884 | -
Panhandle | L_001906VENUS_S5-001939MDLTHELP_S5C1 | Interface MW | 3239.4001 | 3264.939 | - | - | - | - | - | 100.3446 | -
Panhandle | L_001907VENUS_N5-001940MDLTHELP_N5C1 | Interface MW | 3239.4001 | 3250.562 | - | - | - | - | - | 100.7173 | -
Panhandle | L_002437FRNY1_5-150189FRNYPP_1_5C1 | Interface MW | 3239.4001 | 3262.636 | - | - | - | - | - | 100.7164 | -
Panhandle | L_002437FRNY1_5-150190FRNYPP_2_5C1 | Interface MW | 3239.4001 | 3262.6072 | - | - | - | - | - | 100.2849 | -
Panhandle | L_003133RICHLND2_5-003199CALFRESTN_5C1 | Interface MW | 3239.4001 | 3248.6306 | - | - | - | - | - | 100.1941 | -
Panhandle | L_003134RICHLND1_5-003186CALPFREST_5C2 | Interface MW | 3239.4001 | 3245.6863 | - | - | - | - | - | 100.0437 | -
Panhandle | L_003490LNGPRAIRIE_8-152736FENCESLR_8C1 | Interface MW | 3239.4001 | 3240.8162 | - | - | - | - | - | 100.0334 | -
Panhandle | L_003711BALE_S5-153733TNS_5C1 | Interface MW | 3239.4001 | 3240.4822 | - | - | - | - | - | 100.0427 | -
Panhandle | L_005502RAYBURN8-005513RAYBURNPLNT8C1 | Interface MW | 3239.4001 | 3240.7844 | - | - | - | - | - | 100.0843 | -
Panhandle | L_005779REDSWTAP8-005784REDGATESW8C1 | Interface MW | 3239.4001 | 3242.1304 | - | - | - | - | - | 100.0843 | -
Panhandle | L_005779REDSWTAP8-161031REDGATE_5C1 | Interface MW | 3239.4001 | 3242.1304 | - | - | - | - | - | 100.0709 | -
Panhandle | L_005784REDGATESW8-008380NEDIN4AC1 | Interface MW | 3239.4001 | 3241.6958 | - | - | - | - | - | 100.0151 | -
Panhandle | L_005895PEARSALLSUB8-005896MORROWSW8C1 | Interface MW | 3239.4001 | 3239.8906 | - | - | - | - | - | 100.0153 | -
Panhandle | L_005895PEARSALLSUB8-005897HORIZONSW8C1 | Interface MW | 3239.4001 | 3239.8953 | - | - | - | - | - | 100.0627 | -
Panhandle | L_005895PEARSALLSUB8-058959PEARSALLSCB8C1 | Interface MW | 3239.4001 | 3241.4299 | - | - | - | - | - | 100.0153 | -
Panhandle | L_005897HORIZONSW8-162793HRZN_SLR_8C1 | Interface MW | 3239.4001 | 3239.8953 | - | - | - | - | - | 100.4284 | -
Panhandle | L_007048L_GARFIE5_1Y-007049L_BASTEN5_1YC1 | Interface MW | 3239.4001 | 3253.2761 | - | - | - | - | - | 100.1363 | -
Panhandle | L_007077L_AMOSCR5_1Y-183171GALLOWAY_5C1 | Interface MW | 3239.4001 | 3243.8147 | - | - | - | - | - | 100.0411 | -
Panhandle | L_007126L_FERGUS8_1Y-180015FERGGT1_1_8C1 | Interface MW | 3239.4001 | 3240.7307 | - | - | - | - | - | 100.0411 | -
Panhandle | L_007126L_FERGUS8_1Y-180016FERGGT2_2_8C1 | Interface MW | 3239.4001 | 3240.7305 | - | - | - | - | - | 100.0541 | -
Panhandle | L_007126L_FERGUS8_1Y-180017FERGST1_1_8C1 | Interface MW | 3239.4001 | 3241.1511 | - | - | - | - | - | 100.0424 | -
Panhandle | L_007279L_MULDOO8_1Y-1707737RNCHSLR_8C1 | Interface MW | 3239.4001 | 3240.7742 | - | - | - | - | - | 100.0779 | -
Panhandle | L_007389L_PINNAC8_1Y-135019TI_SOLAR_8C1 | Interface MW | 3239.4001 | 3241.9221 | - | - | - | - | - | 100.0151 | -
Panhandle | L_007389L_PINNAC8_1Y-135113ARAGORN_8C1 | Interface MW | 3239.4001 | 3239.8889 | - | - | - | - | - | 100.0181 | -
Panhandle | L_008172VICTORIA4A-110884VIC_SU6C1 | Interface MW | 3239.4001 | 3239.9863 | - | - | - | - | - | 100.0182 | -
Panhandle | L_008209SHAKEPOI4A-162543MCLNSLR_8C1 | Interface MW | 3239.4001 | 3239.9895 | - | - | - | - | - | 100.0372 | -
Panhandle | L_008318RIOHONDO7A-162745LMJDSW_5C1 | Interface MW | 3239.4001 | 3240.6042 | - | - | - | - | - | 100.1129 | -
Panhandle | L_008319RIOHONDO4A-160750LV1_AB_8C1 | Interface MW | 3239.4001 | 3243.0569 | - | - | - | - | - | 100.0774 | -
Panhandle | L_008380NEDIN4A-160234NEDIN_1_8C1 | Interface MW | 3239.4001 | 3241.9089 | - | - | - | - | - | 100.0774 | -
Panhandle | L_008380NEDIN4A-160235NEDIN_2_8C1 | Interface MW | 3239.4001 | 3241.9089 | - | - | - | - | - | 100.0968 | -
Panhandle | L_008380NEDIN4A-160236NEDIN_3_8C1 | Interface MW | 3239.4001 | 3242.5371 | - | - | - | - | - | 100.1813 | -
Panhandle | L_008441NUECES_B4A-160094NUECES_B_1_8C1 | Interface MW | 3239.4001 | 3245.2732 | - | - | - | - | - | 100.1554 | -
Panhandle | L_008458B_DAVIS4A-160105B_DAVIS_1_8C1 | Interface MW | 3239.4001 | 3244.4355 | - | - | - | - | - | 100.1818 | -
Panhandle | L_008458B_DAVIS4A-160106B_DAVIS_2_8C1 | Interface MW | 3239.4001 | 3245.2878 | - | - | - | - | - | 100.0257 | -
Panhandle | L_008458B_DAVIS4A-160107B_DAVIS_3_9C1 | Interface MW | 3239.4001 | 3240.2341 | - | - | - | - | - | 100.0257 | -
Panhandle | L_008458B_DAVIS4A-160108B_DAVIS_4_9C1 | Interface MW | 3239.4001 | 3240.2339 | - | - | - | - | - | 100.0506 | -
Panhandle | L_008663ELSUZPOI7A-163415ELSAUZ_5C1 | Interface MW | 3239.4001 | 3241.0378 | - | - | - | - | - | 100.0151 | -
Panhandle | L_008963HEC4A-008981HECGT14AC1 | Interface MW | 3239.4001 | 3239.8889 | - | - | - | - | - | 100.0331 | -
Panhandle | L_008963HEC4A-008983HECST14AC3 | Interface MW | 3239.4001 | 3240.4719 | - | - | - | - | - | 100.0425 | -
Panhandle | L_008980FRONTERA4A-160180FRONT_EC_C1TC1 | Interface MW | 3239.4001 | 3240.7783 | - | - | - | - | - | 100.0425 | -
Panhandle | L_008980FRONTERA4A-160181FRONT_EC_C2TC1 | Interface MW | 3239.4001 | 3240.7783 | - | - | - | - | - | 100.0497 | -
Panhandle | L_008980FRONTERA4A-160182FRONT_EC_STTC1 | Interface MW | 3239.4001 | 3241.0095 | - | - | - | - | - | 100.2913 | -
Panhandle | L_011270DOGHOUSE_5-023876CLEARFRK_5C1 | Interface MW | 3239.4001 | 3248.8367 | - | - | - | - | - | 100.1003 | -
Panhandle | L_011270DOGHOUSE_5-134805PROSPERO_5C1 | Interface MW | 3239.4001 | 3242.6479 | - | - | - | - | - | 100.0628 | -
Panhandle | L_011270DOGHOUSE_5-135183PRSPERO2_5C1 | Interface MW | 3239.4001 | 3241.4358 | - | - | - | - | - | 100.0237 | -
Panhandle | L_011273NELSON_8-135503RDOSLR_8C1 | Interface MW | 3239.4001 | 3240.1672 | - | - | - | - | - | 100.0239 | -
Panhandle | L_011406CENTBLUF_5-182255HOLSTN_5C1 | Interface MW | 3239.4001 | 3240.1758 | - | - | - | - | - | 100.0892 | -
Panhandle | L_011688THORNTRE_5-143625SAMSON_1_5C1 | Interface MW | 3239.4001 | 3242.2908 | - | - | - | - | - | 100.1225 | -
Panhandle | L_011688THORNTRE_5-143705DELILA_1_5C1 | Interface MW | 3239.4001 | 3243.3696 | - | - | - | - | - | 104.1316 | -
Panhandle | L_023908DEAFSMITH_5-142663CBREAKSC1 | Interface MW | 3239.4001 | 3352.1299 | - | - | - | 103.48 | - | 104.1316 | -
Panhandle | L_023908DEAFSMITH_5-142663CBREAKSC1 | Interface MW | 3239.4001 | 3373.2383 | - | - | - | 103.48 | - | 100.3668 | -
Panhandle | L_023920ABERNATH_5-141607AEEC_5C1 | Interface MW | 3239.4001 | 3251.2817 | - | - | - | - | - | 100.0229 | -
Panhandle | L_023924FARMLAND_5-133641TAHOKAW_5C1 | Interface MW | 3239.4001 | 3240.1411 | - | - | - | - | - | 100.249 | -
Panhandle | L_038745TNATTWATER1-111971TOPAZ_8C1 | Interface MW | 3239.4001 | 3247.4658 | - | - | - | - | - | 100.3004 | -
Panhandle | L_040000CEDARP_B345A-110076CBY4_1_5C1 | Interface MW | 3239.4001 | 3249.1311 | - | - | - | - | - | 100.5112 | -
Panhandle | L_040010CEDARP_B138A-049201GENGBY2_02_8CGL | Interface MW | 3239.4001 | 3255.959 | - | - | - | - | - | 100.155 | -
Panhandle | L_040715GRNBYU_POI8B-049211GENGBY7_08_8CGL | Interface MW | 3239.4001 | 3244.4226 | - | - | - | - | - | 100.0197 | -
Panhandle | L_041000LYDELL_POI_8-110665CHE_2_8C04 | Interface MW | 3239.4001 | 3240.0378 | - | - | - | - | - | 100.1545 | -
Panhandle | L_042010P_H_R___B138-111131BAC_8C92 | Interface MW | 3239.4001 | 3244.4043 | - | - | - | - | - | 100.0763 | -
Panhandle | L_042110ANGLTN_POI_8-111535MYR_8C01 | Interface MW | 3239.4001 | 3241.8733 | - | - | - | - | - | 100.1444 | -
Panhandle | L_042110ANGLTN_POI_8-112597BCH_8C1 | Interface MW | 3239.4001 | 3244.0776 | - | - | - | - | - | 100.0816 | -
Panhandle | L_042215COPPER_X02B8-042540JONCRK__B138C&1-MS | Interface MW | 3239.4001 | 3242.0425 | - | - | - | - | - | 100.0249 | -
Panhandle | L_042420BEASLY_POI_8-112433TAV_8C1 | Interface MW | 3239.4001 | 3240.208 | - | - | - | - | - | 100.1171 | -
Panhandle | L_042570ARCHER_POI_8-112969BTM_8C01 | Interface MW | 3239.4001 | 3243.1926 | - | - | - | - | - | 100.4441 | -
Panhandle | L_044000W_A_P__POI5A-049205GENWAP6_06_5CGL | Interface MW | 3239.4001 | 3253.7856 | - | - | - | - | - | 100.3696 | -
Panhandle | L_044000W_A_P__POI5A-049206GENWAP7_07_5CGL | Interface MW | 3239.4001 | 3251.374 | - | - | - | - | - | 100.3944 | -
Panhandle | L_044005W_A_P__POI5B-049207GENWAP8_08_5CGL | Interface MW | 3239.4001 | 3252.1753 | - | - | - | - | - | 100.0747 | -
Panhandle | L_044015W_A_P__POI8B-049212GENWAP3_03_8CGL | Interface MW | 3239.4001 | 3241.8193 | - | - | - | - | - | 100.1054 | -
Panhandle | L_044060BLUE___POI_5-112043HOL_5C1 | Interface MW | 3239.4001 | 3242.8159 | - | - | - | - | - | 100.0683 | -
Panhandle | L_044070WHALEY_POI_5-112615ROW_5C01 | Interface MW | 3239.4001 | 3241.6138 | - | - | - | - | - | 100.0171 | -
Panhandle | L_044150HNGFRD_POI_8-112094SBE_8C1 | Interface MW | 3239.4001 | 3239.9548 | - | - | - | - | - | 100.3036 | -
Panhandle | L_044200HILLJE__B345-111637DANISH_5C01 | Interface MW | 3239.4001 | 3249.2346 | - | - | - | - | - | 100.2177 | -
Panhandle | L_044200HILLJE__B345-112147PLN_5C1 | Interface MW | 3239.4001 | 3246.4519 | - | - | - | - | - | 100.1774 | -
Panhandle | L_044650SMTHRS_POI_5-112419RABBS_5C01 | Interface MW | 3239.4001 | 3245.1475 | - | - | - | - | - | 100.1946 | -
Panhandle | L_044880WATERH_POI_5-112878GSTAR_5C1 | Interface MW | 3239.4001 | 3245.7026 | - | - | - | - | - | 100.0868 | -
Panhandle | L_044890SNUG___POI_8-113435COTBAYOU_8C1 | Interface MW | 3239.4001 | 3242.2126 | - | - | - | - | - | 100.1641 | -
Panhandle | L_045500T_H_W__POI_5-049204GENTHW5X05_5CGL | Interface MW | 3239.4001 | 3244.7151 | - | - | - | - | - | 100.1539 | -
Panhandle | L_045515T_H_W__POI_8-049202GENTHW3X03_8CGL | Interface MW | 3239.4001 | 3244.385 | - | - | - | - | - | 100.1539 | -
Panhandle | L_045515T_H_W__POI_8-049203GENTHW4X04_8CGL | Interface MW | 3239.4001 | 3244.3855 | - | - | - | - | - | 100.1767 | -
Panhandle | L_047170H_O_C__POI_8-111800PRO_8C01 | Interface MW | 3239.4001 | 3245.125 | - | - | - | - | - | 100.109 | -
Panhandle | L_059906LONGDRAW_138-134145JUNO_8C1 | Interface MW | 3239.4001 | 3242.9309 | - | - | - | - | - | 100.0491 | -
Panhandle | L_059906LONGDRAW_138-134342LGDRAW_S8C1 | Interface MW | 3239.4001 | 3240.9897 | - | - | - | - | - | 100.3678 | -
Panhandle | L_059909NOVA_138-059998NOVA8C1 | Interface MW | 3239.4001 | 3251.3157 | - | - | - | - | - | 100.2164 | -
Panhandle | L_059909NOVA_138-143115NOVA1SLR_8C1 | Interface MW | 3239.4001 | 3246.4099 | - | - | - | - | - | 100.0236 | -
Panhandle | L_059909NOVA_138-144163NOVA2SLR_8C1 | Interface MW | 3239.4001 | 3240.165 | - | - | - | - | - | 100.1424 | -
Panhandle | L_059911MHOS-183406JADE_HI_5C1 | Interface MW | 3239.4001 | 3244.0125 | - | - | - | - | - | 100.1077 | -
Panhandle | L_060011NEBULA7A-183525ANDMDSLR_5C1 | Interface MW | 3239.4001 | 3242.8875 | - | - | - | - | - | 100.0724 | -
Panhandle | L_060393PIGCREEK4A-134245TAYGETE_8C1 | Interface MW | 3239.4001 | 3241.7449 | - | - | - | - | - | 100.0332 | -
Panhandle | L_060393PIGCREEK4A-134705TYGTEII_8C1 | Interface MW | 3239.4001 | 3240.4763 | - | - | - | - | - | 100.0483 | -
Panhandle | L_060464AZUREPOI7A-060514CLEARCRO7BC1 | Interface MW | 3239.4001 | 3240.9641 | - | - | - | - | - | 100.0034 | -
Panhandle | L_060501TESLA7A-061616FOURCORNERSC1 | Interface MW | 3239.4001 | 3239.5103 | - | - | - | - | - | 100.215 | -
Panhandle | L_068090SAMSW-068092LIBERTYC1 | Interface MW | 3239.4001 | 3246.3665 | - | - | - | - | - | 100.1556 | -
Panhandle | L_068092LIBERTY-152433MERCURY_5C1 | Interface MW | 3239.4001 | 3244.4404 | - | - | - | - | - | 100.0105 | -
Panhandle | L_076002L_BAKERS5_1Y-133843WAYMARK_5C1 | Interface MW | 3239.4001 | 3239.74 | - | - | - | - | - | 100.0604 | -
Panhandle | L_076002L_BAKERS5_1Y-135327REDBARN_5C1 | Interface MW | 3239.4001 | 3241.3564 | - | - | - | - | - | 100.0037 | -
Panhandle | L_076005L_SCHNDR5_1Y-132632SANTRITA_5C1 | Interface MW | 3239.4001 | 3239.52 | - | - | - | - | - | 100.0041 | -
Panhandle | L_076015L_CEDACA5_1Y-134512HILO_5C1 | Interface MW | 3239.4001 | 3239.5332 | - | - | - | - | - | 100.0127 | -
Panhandle | L_076040L_CASTIL8_1Y-132783CASL_GAP_8C1 | Interface MW | 3239.4001 | 3239.8118 | - | - | - | - | - | 100.008 | -
Panhandle | L_076090L_DIVIDE5_1Y-180759CAPRIDG4_1_5C1 | Interface MW | 3239.4001 | 3239.6609 | - | - | - | - | - | 100.0034 | -
Panhandle | L_078255L_PINTCR8_1Y-183623ZIER_8C1 | Interface MW | 3239.4001 | 3239.5103 | - | - | - | - | - | 100.384 | -
Panhandle | L_080071ZORILLO7A-080076AJO7AC1 | Interface MW | 3239.4001 | 3251.8408 | - | - | - | - | - | 100.2204 | -
Panhandle | L_080071ZORILLO7A-080171SARITA7AC1 | Interface MW | 3239.4001 | 3246.5386 | - | - | - | - | - | 100.2204 | -
Panhandle | L_080171SARITA7A-160299BAFFIN_2_5C1 | Interface MW | 3239.4001 | 3246.5386 | - | - | - | - | - | 100.0574 | -
Panhandle | L_080219LOBO7A-163223CORAZON_5C1 | Interface MW | 3239.4001 | 3241.2583 | - | - | - | - | - | 100.0258 | -
Panhandle | L_080260GILA4A-160095NUECES_B_2_8C1 | Interface MW | 3239.4001 | 3240.2371 | - | - | - | - | - | 100.0256 | -
Panhandle | L_080260GILA4A-160096NUECES_B_3_8C1 | Interface MW | 3239.4001 | 3240.23 | - | - | - | - | - | 100.0186 | -
Panhandle | L_080503SANTASW4A-085001N_SHARPE4AC1 | Interface MW | 3239.4001 | 3240.0039 | - | - | - | - | - | 100.0186 | -
Panhandle | L_080503SANTASW4A-161455CHAWIND_8C1 | Interface MW | 3239.4001 | 3240.0037 | - | - | - | - | - | 100.0078 | -
Panhandle | L_080509LADKPOI7A-161753BBREEZE_5C1 | Interface MW | 3239.4001 | 3239.6514 | - | - | - | - | - | 100.0054 | -
Panhandle | L_085008PATPOI7A-161653PATWIND_5C1 | Interface MW | 3239.4001 | 3239.5762 | - | - | - | - | - | 100.0153 | -
Panhandle | L_088574WRAYPOI7A-162695ELTRUENO_5C1 | Interface MW | 3239.4001 | 3239.896 | - | - | - | - | - | 100.0105 | -
Panhandle | L_088670BLACKPOI7A-162915BLACKJAK_5C1 | Interface MW | 3239.4001 | 3239.739 | - | - | - | - | - | 100.0088 | -
Panhandle | L10010434_MODIFIED_BY_MZ | Interface MW | 3239.4001 | 3239.6865 | - | - | - | - | - | 100.0151 | -
Panhandle | L10010717 | Interface MW | 3239.4001 | 3239.8887 | - | - | - | - | - | 100.2204 | -
Panhandle | L10011585 | Interface MW | 3239.4001 | 3246.5388 | - | - | - | - | - | 100.0368 | -
Panhandle | L10011690 | Interface MW | 3239.4001 | 3240.592 | - | - | - | - | - | 100.0335 | -
Panhandle | L10011910-1 | Interface MW | 3239.4001 | 3240.4868 | - | - | - | - | - | 100.0054 | -
Panhandle | L10012087 | Interface MW | 3239.4001 | 3239.5759 | - | - | - | - | - | 100.0181 | -
Panhandle | L10012105 | Interface MW | 3239.4001 | 3239.9863 | - | - | - | - | - | 100.0186 | -
Panhandle | L10012915 | Interface MW | 3239.4001 | 3240.0034 | - | - | - | - | - | 100.0153 | -
Panhandle | L11000047 | Interface MW | 3239.4001 | 3239.896 | - | - | - | - | - | 100.0552 | -
Panhandle | L11000090 | Interface MW | 3239.4001 | 3241.187 | - | - | - | - | - | 100.0078 | -
Panhandle | L11000095 | Interface MW | 3239.4001 | 3239.6514 | - | - | - | - | - | 100.2087 | -
Panhandle | L201000169 | Interface MW | 3239.4001 | 3246.1594 | - | - | - | - | - | 100.0651 | -
Panhandle | L2020817 | Interface MW | 3239.4001 | 3241.5078 | - | - | - | - | - | 100.0651 | -
Panhandle | L2020818 | Interface MW | 3239.4001 | 3241.5078 | - | - | - | - | - | 100.2087 | -
Panhandle | L20255426 | Interface MW | 3239.4001 | 3246.1594 | - | - | - | - | - | 100.716 | -
Panhandle | LAKE CREEK - RATTLE SNAKE 345 KV WITH SANDY UNIT (SINGLE B TO B) | Interface MW | 3239.4001 | 3262.5952 | - | - | - | - | - | 100.0154 | -
Panhandle | LCRA TSC_T21457 | Interface MW | 3239.4001 | 3239.8979 | - | - | - | - | - | 100.0823 | -
Panhandle | LCRA TSC_T255_TAE3121_1 | Interface MW | 3239.4001 | 3242.0671 | - | - | - | - | - | 100.0112 | -
Panhandle | LEON_CON | Interface MW | 3239.4001 | 3239.7634 | - | - | - | - | - | 100.0499 | -
Panhandle | LIATRIS_CON | Interface MW | 3239.4001 | 3241.0171 | - | - | - | - | - | 100.0077 | -
Panhandle | LITTLE POND - HOG CREEK / GIBSON - TNP_5 (DOUBLE B TO B ) | Interface MW | 3239.4001 | 3239.6482 | - | - | - | - | - | 100.5007 | -
Panhandle | M10000271115801 | Interface MW | 3239.4001 | 3255.6199 | - | - | - | - | - | 100.227 | -
Panhandle | M105311105321 | Interface MW | 3239.4001 | 3246.7522 | - | - | - | - | - | 100.384 | -
Panhandle | M115851115803 | Interface MW | 3239.4001 | 3251.8408 | - | - | - | - | - | 100.0312 | -
Panhandle | M128152129153 | Interface MW | 3239.4001 | 3240.4111 | - | - | - | - | - | 100.0376 | -
Panhandle | MALDIVES_CON | Interface MW | 3239.4001 | 3240.6179 | - | - | - | - | - | 100.0074 | -
Panhandle | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-1 | Interface MW | 3239.4001 | 3239.6409 | - | - | - | - | - | 100.0313 | -
Panhandle | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | Interface MW | 3239.4001 | 3240.4146 | - | - | - | - | - | 100.5007 | -
Panhandle | MB100002711580 | Interface MW | 3239.4001 | 3255.6199 | - | - | - | - | - | 100.0959 | -
Panhandle | MB1101411110-1 | Interface MW | 3239.4001 | 3242.5056 | - | - | - | - | - | 100.384 | -
Panhandle | MB1158011585 | Interface MW | 3239.4001 | 3251.8408 | - | - | - | - | - | 100.0297 | -
Panhandle | MB1291512815a | Interface MW | 3239.4001 | 3240.3613 | - | - | - | - | - | 100.3443 | -
Panhandle | MB210140210145-AAAAA | Interface MW | 3239.4001 | 3250.5525 | - | - | - | - | - | 100.3805 | -
Panhandle | MB210140210145-AAAAB | Interface MW | 3239.4001 | 3251.7256 | - | - | - | - | - | 100.2665 | -
Panhandle | MB210140210145-AAABA | Interface MW | 3239.4001 | 3248.0339 | - | - | - | - | - | 100.3038 | -
Panhandle | MB210140210145-AABA | Interface MW | 3239.4001 | 3249.2424 | - | - | - | - | - | 100.2253 | -
Panhandle | MB210140210145-AABB | Interface MW | 3239.4001 | 3246.697 | - | - | - | - | - | 100.2758 | -
Panhandle | MB210140210145-ABAAA | Interface MW | 3239.4001 | 3248.3335 | - | - | - | - | - | 100.2392 | -
Panhandle | MB210140210145-ABAAB | Interface MW | 3239.4001 | 3247.1484 | - | - | - | - | - | 100.3031 | -
Panhandle | MB210140210145-ABABB | Interface MW | 3239.4001 | 3249.2188 | - | - | - | - | - | 100.1979 | -
Panhandle | MB210140210145-ABBA | Interface MW | 3239.4001 | 3245.8105 | - | - | - | - | - | 100.0274 | -
Panhandle | MB210140210145-BAAA-1 | Interface MW | 3239.4001 | 3240.2878 | - | - | - | - | - | 100.0673 | -
Panhandle | MB210140210145-BAAA-2 | Interface MW | 3239.4001 | 3241.5793 | - | - | - | - | - | 100.1963 | -
Panhandle | MB2726627277 | Interface MW | 3239.4001 | 3245.7585 | - | - | - | - | - | 100.6153 | -
Panhandle | MITCHELL BEND-CARMICHAEL BEND*ROCKY CREEK 345 KV (DOUBLE B TO B)-1 | Interface MW | 3239.4001 | 3259.3315 | - | - | - | - | - | 100.6092 | -
Panhandle | MITCHELL BEND-ROCKY CREEK 345 KV (SINGLE B TO B)-1 | Interface MW | 3239.4001 | 3259.1357 | - | - | - | - | - | 100.1831 | -
Panhandle | MITCHELL BEND-WOLF HOLLOW II UNIT 4 345 KV (SINGLE B TO B) | Interface MW | 3239.4001 | 3245.332 | - | - | - | - | - | 100.3528 | -
Panhandle | MITCHELL BEND-WOLF HOLLOW II UNITS 5_6 345 KV (SINGLE B TO B) | Interface MW | 3239.4001 | 3250.8289 | - | - | - | - | - | 100.633 | -
Panhandle | N5GSU2_B | Interface MW | 3239.4001 | 3259.906 | - | - | - | - | - | 100.1934 | -
Panhandle | ODESSA EHV - NORTH MCCAMEY 345 KV (SINGLE B TO B) | Interface MW | 3239.4001 | 3245.6643 | - | - | - | - | - | 100.0482 | -
Panhandle | OYSTER_CON | Interface MW | 3239.4001 | 3240.9619 | - | - | - | - | - | 100.1631 | -
Panhandle | P1-1_BTE_1_COMBINED-CYCLE | Interface MW | 3239.4001 | 3244.6833 | - | - | - | - | - | 100.1631 | -
Panhandle | P1-1_BTE_2_COMBINED-CYCLE | Interface MW | 3239.4001 | 3244.6833 | - | - | - | - | - | 100.1631 | -
Panhandle | P1-1_BTE_3_COMBINED-CYCLE | Interface MW | 3239.4001 | 3244.6833 | - | - | - | - | - | 100.2218 | -
Panhandle | P1-1_BVE_1_COMBINED-CYCLE | Interface MW | 3239.4001 | 3246.5847 | - | - | - | - | - | 100.2215 | -
Panhandle | P1-1_BVE_2_COMBINED-CYCLE | Interface MW | 3239.4001 | 3246.5747 | - | - | - | - | - | 100.0196 | -
Panhandle | P1-1_CBE_1_COMBINED-CYCLE | Interface MW | 3239.4001 | 3240.0366 | - | - | - | - | - | 100.0144 | -
Panhandle | P1-1_CBE_2_COMBINED-CYCLE | Interface MW | 3239.4001 | 3239.8665 | - | - | - | - | - | 100.0236 | -
Panhandle | P1-1_CBE_3_COMBINED-CYCLE | Interface MW | 3239.4001 | 3240.1641 | - | - | - | - | - | 100.0187 | -
Panhandle | P1-1_CBE_4_COMBINED-CYCLE | Interface MW | 3239.4001 | 3240.0068 | - | - | - | - | - | 100.5674 | -
Panhandle | P1-1_CBT_1_COMBINED-CYCLE | Interface MW | 3239.4001 | 3257.78 | - | - | - | - | - | 100.5725 | -
Panhandle | P1-1_CBT_2_COMBINED-CYCLE | Interface MW | 3239.4001 | 3257.9443 | - | - | - | - | - | 100.1621 | -
Panhandle | P1-1_CBY_1_COMBINED-CYCLE | Interface MW | 3239.4001 | 3244.6521 | - | - | - | - | - | 100.1621 | -
Panhandle | P1-1_CBY_2_COMBINED-CYCLE | Interface MW | 3239.4001 | 3244.6519 | - | - | - | - | - | 100.1272 | -
Panhandle | P1-1_CHE_1_COMBINED-CYCLE | Interface MW | 3239.4001 | 3243.5198 | - | - | - | - | - | 100.1649 | -
Panhandle | P1-1_CHE_2_COMBINED-CYCLE | Interface MW | 3239.4001 | 3244.7432 | - | - | - | - | - | 100.1736 | -
Panhandle | P1-1_CHE_3_COMBINED-CYCLE | Interface MW | 3239.4001 | 3245.0249 | - | - | - | - | - | 100.1408 | -
Panhandle | P1-1_CVC_1_COMBINED-CYCLE | Interface MW | 3239.4001 | 3243.9604 | - | - | - | - | - | 100.1371 | -
Panhandle | P1-1_CVC_2_COMBINED-CYCLE | Interface MW | 3239.4001 | 3243.8406 | - | - | - | - | - | 100.1371 | -
Panhandle | P1-1_CVC_3_COMBINED-CYCLE | Interface MW | 3239.4001 | 3243.8406 | - | - | - | - | - | 100.1379 | -
Panhandle | P1-1_CVC_4_COMBINED-CYCLE | Interface MW | 3239.4001 | 3243.8669 | - | - | - | - | - | 100.0116 | -
Panhandle | P1-1_DIB_1_COMBINED-CYCLE | Interface MW | 3239.4001 | 3239.7764 | - | - | - | - | - | 100.0116 | -
Panhandle | P1-1_DIB_2_COMBINED-CYCLE | Interface MW | 3239.4001 | 3239.7759 | - | - | - | - | - | 100.0173 | -
Panhandle | P1-1_DIB_3_COMBINED-CYCLE | Interface MW | 3239.4001 | 3239.959 | - | - | - | - | - | 100.2591 | -
Panhandle | P1-1_DPEC_1_COMBINED-CYCLE | Interface MW | 3239.4001 | 3247.7942 | - | - | - | - | - | 100.2675 | -
Panhandle | P1-1_DPEC_2_COMBINED-CYCLE | Interface MW | 3239.4001 | 3248.0667 | - | - | - | - | - | 100.2592 | -
Panhandle | P1-1_DPEC_3_COMBINED-CYCLE | Interface MW | 3239.4001 | 3247.7964 | - | - | - | - | - | 100.2676 | -
Panhandle | P1-1_DPEC_4_COMBINED-CYCLE | Interface MW | 3239.4001 | 3248.0674 | - | - | - | - | - | 100.2458 | -
Panhandle | P1-1_DPEC_5_COMBINED-CYCLE | Interface MW | 3239.4001 | 3247.3625 | - | - | - | - | - | 100.3613 | -
Panhandle | P1-1_FTR_1_COMBINED-CYCLE | Interface MW | 3239.4001 | 3251.1057 | - | - | - | - | - | 100.3614 | -
Panhandle | P1-1_FTR_2_COMBINED-CYCLE | Interface MW | 3239.4001 | 3251.106 | - | - | - | - | - | 100.3614 | -
Panhandle | P1-1_FTR_3_COMBINED-CYCLE | Interface MW | 3239.4001 | 3251.1062 | - | - | - | - | - | 100.2834 | -
Panhandle | P1-1_GEN_BLY-CBT_C0_111143 | Interface MW | 3239.4001 | 3248.5796 | - | - | - | - | - | 100.1555 | -
Panhandle | P1-1_GEN_BLY-CBT_C1_111141 | Interface MW | 3239.4001 | 3244.4363 | - | - | - | - | - | 100.1605 | -
Panhandle | P1-1_GEN_BLY-CBT_C2_111142 | Interface MW | 3239.4001 | 3244.5984 | - | - | - | - | - | 100.0246 | -
Panhandle | P1-1_GEN_CBY-CBY_C0_110075 | Interface MW | 3239.4001 | 3240.1963 | - | - | - | - | - | 100.012 | -
Panhandle | P1-1_GEN_CBY-CBY_C1_110073 | Interface MW | 3239.4001 | 3239.7886 | - | - | - | - | - | 100.012 | -
Panhandle | P1-1_GEN_CBY-CBY_C2_110074 | Interface MW | 3239.4001 | 3239.7883 | - | - | - | - | - | 100.1144 | -
Panhandle | P1-1_GEN_CTR-DPEC_C0_110755 | Interface MW | 3239.4001 | 3243.1072 | - | - | - | - | - | 100.0184 | -
Panhandle | P1-1_GEN_CTR-DPEC_C1_110751 | Interface MW | 3239.4001 | 3239.9973 | - | - | - | - | - | 100.0268 | -
Panhandle | P1-1_GEN_CTR-DPEC_C2_110752 | Interface MW | 3239.4001 | 3240.2671 | - | - | - | - | - | 100.0185 | -
Panhandle | P1-1_GEN_CTR-DPEC_C3_110753 | Interface MW | 3239.4001 | 3239.9995 | - | - | - | - | - | 100.0268 | -
Panhandle | P1-1_GEN_CTR-DPEC_C4_110754 | Interface MW | 3239.4001 | 3240.2678 | - | - | - | - | - | 100.0052 | -
Panhandle | P1-1_GEN_CTR-DPEC_C6_110761 | Interface MW | 3239.4001 | 3239.5701 | - | - | - | - | - | 100.0197 | -
Panhandle | P1-1_GEN_DPW-CHE_C2_110663 | Interface MW | 3239.4001 | 3240.0398 | - | - | - | - | - | 100.0284 | -
Panhandle | P1-1_GEN_DPW-CHE_C3_110668 | Interface MW | 3239.4001 | 3240.3201 | - | - | - | - | - | 100.0198 | -
Panhandle | P1-1_GEN_JFS-PSG_C0_110623 | Interface MW | 3239.4001 | 3240.0422 | - | - | - | - | - | 100.0148 | -
Panhandle | P1-1_GEN_JFS-PSG_C2_110621 | Interface MW | 3239.4001 | 3239.8799 | - | - | - | - | - | 100.0148 | -
Panhandle | P1-1_GEN_JFS-PSG_C3_110622 | Interface MW | 3239.4001 | 3239.8801 | - | - | - | - | - | 100.2218 | -
Panhandle | P1-1_GEN_RNS-FTR_C0_120094 | Interface MW | 3239.4001 | 3246.5842 | - | - | - | - | - | 100.0126 | -
Panhandle | P1-1_GEN_RNS-FTR_C1_120091 | Interface MW | 3239.4001 | 3239.8093 | - | - | - | - | - | 100.0126 | -
Panhandle | P1-1_GEN_RNS-FTR_C2_120092 | Interface MW | 3239.4001 | 3239.8093 | - | - | - | - | - | 100.0126 | -
Panhandle | P1-1_GEN_RNS-FTR_C3_120093 | Interface MW | 3239.4001 | 3239.8093 | - | - | - | - | - | 100.0183 | -
Panhandle | P1-1_GEN_SDN-CVC_C1_110821 | Interface MW | 3239.4001 | 3239.9922 | - | - | - | - | - | 100.0146 | -
Panhandle | P1-1_GEN_SDN-CVC_C2_110822 | Interface MW | 3239.4001 | 3239.8743 | - | - | - | - | - | 100.0146 | -
Panhandle | P1-1_GEN_SDN-CVC_C3_110823 | Interface MW | 3239.4001 | 3239.8743 | - | - | - | - | - | 100.0941 | -
Panhandle | P1-1_GEN_SMR-BVE_C0_110773 | Interface MW | 3239.4001 | 3242.4473 | - | - | - | - | - | 100.0021 | -
Panhandle | P1-1_GEN_SMR-BVE_C1_110771 | Interface MW | 3239.4001 | 3239.4673 | - | - | - | - | - | 100.0018 | -
Panhandle | P1-1_GEN_SMR-BVE_C2_110772 | Interface MW | 3239.4001 | 3239.4573 | - | - | - | - | - | 100.0234 | -
Panhandle | P1-1_PSA_1_COMBINED-CYCLE | Interface MW | 3239.4001 | 3240.1577 | - | - | - | - | - | 100.0242 | -
Panhandle | P1-1_PSA_2_COMBINED-CYCLE | Interface MW | 3239.4001 | 3240.1848 | - | - | - | - | - | 100.0251 | -
Panhandle | P1-1_PSA_3_COMBINED-CYCLE | Interface MW | 3239.4001 | 3240.2119 | - | - | - | - | - | 100.0255 | -
Panhandle | P1-1_PSA_4_COMBINED-CYCLE | Interface MW | 3239.4001 | 3240.2253 | - | - | - | - | - | 100.0245 | -
Panhandle | P1-1_PSA_5_COMBINED-CYCLE | Interface MW | 3239.4001 | 3240.1934 | - | - | - | - | - | 100.0236 | -
Panhandle | P1-1_PSA_6_COMBINED-CYCLE | Interface MW | 3239.4001 | 3240.1631 | - | - | - | - | - | 100.1607 | -
Panhandle | P1-1_PSG_1_COMBINED-CYCLE | Interface MW | 3239.4001 | 3244.6045 | - | - | - | - | - | 100.1607 | -
Panhandle | P1-1_PSG_2_COMBINED-CYCLE | Interface MW | 3239.4001 | 3244.6047 | - | - | - | - | - | 100.015 | -
Panhandle | P1-1_THW_1_COMBINED-CYCLE | Interface MW | 3239.4001 | 3239.8867 | - | - | - | - | - | 100.015 | -
Panhandle | P1-1_THW_2_COMBINED-CYCLE | Interface MW | 3239.4001 | 3239.8867 | - | - | - | - | - | 100.015 | -
Panhandle | P1-1_THW_3_COMBINED-CYCLE | Interface MW | 3239.4001 | 3239.8867 | - | - | - | - | - | 100.015 | -
Panhandle | P1-1_THW_4_COMBINED-CYCLE | Interface MW | 3239.4001 | 3239.8867 | - | - | - | - | - | 100.015 | -
Panhandle | P1-1_THW_5_COMBINED-CYCLE | Interface MW | 3239.4001 | 3239.8867 | - | - | - | - | - | 100.015 | -
Panhandle | P1-1_THW_6_COMBINED-CYCLE | Interface MW | 3239.4001 | 3239.8867 | - | - | - | - | - | 100.015 | -
Panhandle | P1-1_THW_7_COMBINED-CYCLE | Interface MW | 3239.4001 | 3239.8867 | - | - | - | - | - | 100.015 | -
Panhandle | P1-1_THW_8_COMBINED-CYCLE | Interface MW | 3239.4001 | 3239.8867 | - | - | - | - | - | 100.0284 | -
Panhandle | P1-2_(110666-110667-BC) | Interface MW | 3239.4001 | 3240.3201 | - | - | - | - | - | 100.5058 | -
Panhandle | P1-2_(40015-49200-GL) | Interface MW | 3239.4001 | 3255.7854 | - | - | - | - | - | 100.1144 | -
Panhandle | P1-2_(40240-110756-01) | Interface MW | 3239.4001 | 3243.1072 | - | - | - | - | - | 100.0184 | -
Panhandle | P1-2_(40240-110757-02) | Interface MW | 3239.4001 | 3239.9973 | - | - | - | - | - | 100.0268 | -
Panhandle | P1-2_(40240-110758-03) | Interface MW | 3239.4001 | 3240.2671 | - | - | - | - | - | 100.0185 | -
Panhandle | P1-2_(40240-110759-04) | Interface MW | 3239.4001 | 3239.9995 | - | - | - | - | - | 100.0268 | -
Panhandle | P1-2_(40240-110760-05) | Interface MW | 3239.4001 | 3240.2678 | - | - | - | - | - | 100.0052 | -
Panhandle | P1-2_(40240-110762-01) | Interface MW | 3239.4001 | 3239.5701 | - | - | - | - | - | 100.1737 | -
Panhandle | P1-2_(40450-110666-02) | Interface MW | 3239.4001 | 3245.0271 | - | - | - | - | - | 100.6422 | -
Panhandle | P1-2_(40600-120095-1) | Interface MW | 3239.4001 | 3260.2041 | - | - | - | - | - | 100.2184 | -
Panhandle | P1-2_(40890-113219-01) | Interface MW | 3239.4001 | 3246.4763 | - | - | - | - | - | 100.0148 | -
Panhandle | P1-2_(41240-110624-02) | Interface MW | 3239.4001 | 3239.8799 | - | - | - | - | - | 100.0148 | -
Panhandle | P1-2_(41240-110625-03) | Interface MW | 3239.4001 | 3239.8801 | - | - | - | - | - | 100.0198 | -
Panhandle | P1-2_(41240-110626-02) | Interface MW | 3239.4001 | 3240.0422 | - | - | - | - | - | 100.1408 | -
Panhandle | P1-2_(41430-110825-03) | Interface MW | 3239.4001 | 3243.9604 | - | - | - | - | - | 100.0146 | -
Panhandle | P1-2_(41430-110826-02) | Interface MW | 3239.4001 | 3239.8743 | - | - | - | - | - | 100.0146 | -
Panhandle | P1-2_(41430-110827-01) | Interface MW | 3239.4001 | 3239.8743 | - | - | - | - | - | 100.3573 | -
Panhandle | P1-2_(42985-110797-60) | Interface MW | 3239.4001 | 3250.9734 | - | - | - | - | - | 100.0411 | -
Panhandle | P1-2_(43020-113341-1) | Interface MW | 3239.4001 | 3240.7314 | - | - | - | - | - | 100.0151 | -
Panhandle | P1-2_(44010-49213-GL) | Interface MW | 3239.4001 | 3239.8904 | - | - | - | - | - | 100.0151 | -
Panhandle | P1-2_(44010-49214-GL) | Interface MW | 3239.4001 | 3239.8909 | - | - | - | - | - | 100.0064 | -
Panhandle | P1-2_(44010-49216-GL) | Interface MW | 3239.4001 | 3239.6064 | - | - | - | - | - | 100.316 | -
Panhandle | P1-2_(44015-49215-GL) | Interface MW | 3239.4001 | 3249.6353 | - | - | - | - | - | 100.1584 | -
Panhandle | P1-2_(44090-111865-1) | Interface MW | 3239.4001 | 3244.53 | - | - | - | - | - | 100.1045 | -
Panhandle | P1-2_(44160-112495-1) | Interface MW | 3239.4001 | 3242.7866 | - | - | - | - | - | 100.2836 | -
Panhandle | P1-2_(44200-112261-1) | Interface MW | 3239.4001 | 3248.5862 | - | - | - | - | - | 100.0426 | -
Panhandle | P1-2_(44220-113251-1) | Interface MW | 3239.4001 | 3240.7795 | - | - | - | - | - | 100.0021 | -
Panhandle | P1-2_(44650-110774-1) | Interface MW | 3239.4001 | 3239.4673 | - | - | - | - | - | 100.0018 | -
Panhandle | P1-2_(44650-110775-2) | Interface MW | 3239.4001 | 3239.4573 | - | - | - | - | - | 100.0941 | -
Panhandle | P1-2_(44650-110776-1) | Interface MW | 3239.4001 | 3242.4473 | - | - | - | - | - | 100.6004 | -
Panhandle | P1-2_(46020-49208-GL) | Interface MW | 3239.4001 | 3258.8494 | - | - | - | - | - | 100.611 | -
Panhandle | P1-2_(46020-49209-GL) | Interface MW | 3239.4001 | 3259.1921 | - | - | - | - | - | 100.1299 | -
Panhandle | P1-2_11.1 | Interface MW | 3239.4001 | 3243.6082 | - | - | - | - | - | 100.1339 | -
Panhandle | P7-1_E1>>JULIA | Interface MW | 3239.4001 | 3243.7393 | - | - | - | - | - | 100.0815 | -
Panhandle | P7-1_E1>>T0202H | Interface MW | 3239.4001 | 3242.0417 | - | - | - | - | - | 100.0457 | -
Panhandle | P7-1_E1>>T0202J-2 | Interface MW | 3239.4001 | 3240.8794 | - | - | - | - | - | 100.1169 | -
Panhandle | P7-1_E1>>T0202K-1-2 | Interface MW | 3239.4001 | 3243.187 | - | - | - | - | - | 100.034 | -
Panhandle | P7-1_E1>>T0202K-2-1 | Interface MW | 3239.4001 | 3240.5005 | - | - | - | - | - | 100.2044 | -
Panhandle | P7-1_E1>>T0202K-2-2 | Interface MW | 3239.4001 | 3246.0227 | - | - | - | - | - | 100.0702 | -
Panhandle | P7-1_E1>>T0226 | Interface MW | 3239.4001 | 3241.6733 | - | - | - | - | - | 100.0626 | -
Panhandle | P7-1_E1>>T0404A-2 | Interface MW | 3239.4001 | 3241.4275 | - | - | - | - | - | 100.116 | -
Panhandle | P7-1_E1>>T0404YYY | Interface MW | 3239.4001 | 3243.158 | - | - | - | - | - | 100.1044 | -
Panhandle | P7-1_E1>>T0526 | Interface MW | 3239.4001 | 3242.7832 | - | - | - | - | - | 100.0569 | -
Panhandle | P7-1_E1>>T0726 | Interface MW | 3239.4001 | 3241.2432 | - | - | - | - | - | 100.1853 | -
Panhandle | P7-1_E1>>T6060B | Interface MW | 3239.4001 | 3245.4036 | - | - | - | - | - | 100.0314 | -
Panhandle | P7-1_E1>>T6472CX1A | Interface MW | 3239.4001 | 3240.416 | - | - | - | - | - | 100.0117 | -
Panhandle | P7-1_E1>>T6472CX1B | Interface MW | 3239.4001 | 3239.7791 | - | - | - | - | - | 100.423 | -
Panhandle | P7-1_E1>>T7475B | Interface MW | 3239.4001 | 3253.1025 | - | - | - | - | - | 100.8511 | -
Panhandle | P7-1_E1>>T9797B | Interface MW | 3239.4001 | 3266.9719 | - | - | - | - | - | 100.0861 | -
Panhandle | P7-1_E1>T0202F-1 | Interface MW | 3239.4001 | 3242.1877 | - | - | - | - | - | 100.0162 | -
Panhandle | P7-1_E1>T0202GX | Interface MW | 3239.4001 | 3239.9236 | - | - | - | - | - | 100.3592 | -
Panhandle | P7-1_E1>T6060F | Interface MW | 3239.4001 | 3251.0364 | - | - | - | - | - | 100.2128 | -
Panhandle | PINEFOREST_CON | Interface MW | 3239.4001 | 3246.2922 | - | - | - | - | - | - | -
Panhandle | Prong Moss-Falcon Seaboard Dbl Ckt 345 kV ONCOR WTIP RPG Submittal | Interface MW | 3239.4001 | 3239.9756 | - | - | - | - | - | 100.0178 | -
Panhandle | QUANT_CON | Interface MW | 3239.4001 | 3245.094 | - | - | - | - | - | 100.1758 | -
Panhandle | R4U2A5C1_1_B | Interface MW | 3239.4001 | 3252.1748 | - | - | - | - | - | 100.3944 | -
Panhandle | RAT_SNAKE-SNDY_CREEK_5 (SINGLE B TO B) | Interface MW | 3239.4001 | 3262.595 | - | - | - | - | - | 100.716 | -
Panhandle | RILEY - TESLA & TESLA - SALVARE | Interface MW | 3239.4001 | 3242.0789 | - | - | - | - | - | 100.0827 | -
Panhandle | SAM_NAV_P7F1 | Interface MW | 3239.4001 | 3246.3984 | - | - | - | - | - | 100.216 | -
Panhandle | SAN_PAT_CON | Interface MW | 3239.4001 | 3249.1831 | - | - | - | - | - | 100.302 | -
Panhandle | SKYSLY_CON | Interface MW | 3239.4001 | 3244.2244 | - | - | - | - | - | 100.1489 | -
Panhandle | SOLACE_CON | Interface MW | 3239.4001 | 3244.2271 | - | - | - | - | - | 100.149 | -
Panhandle | STECL_10262 | Interface MW | 3239.4001 | 3247.396 | - | - | - | - | - | 100.2468 | -
Panhandle | STECL_10580 | Interface MW | 3239.4001 | 3241.6958 | - | - | - | - | - | 100.0709 | -
Panhandle | T_059908NOVA_345-059998NOVA8CT1 | Interface MW | 3239.4001 | 3251.3157 | - | - | - | - | - | 100.3678 | -
Panhandle | TESLA - EDITH CLARKE & TESLA - FOUR CORNERS | Interface MW | 3239.4001 | 3241.9126 | - | - | - | - | - | 100.0776 | -
Panhandle | TRICORNER - WATERMILL (DOUBLE B TO B) B | Interface MW | 3239.4001 | 3240.5308 | - | - | - | - | - | 100.0349 | -
Panhandle | TRIFECTA_CON | Interface MW | 3239.4001 | 3249.9851 | - | - | - | - | - | 100.3268 | -
Panhandle | TWIN_OAK_BKR_8995_345_OAK_GROVE_SINGLE_B_T0_B | Interface MW | 3239.4001 | 3259.7654 | - | - | - | - | - | 100.6287 | -
Panhandle | TWIN_OAK_BKR_9000_345_OAK_GROVE_SINGLE_B_T0_B | Interface MW | 3239.4001 | 3259.7651 | - | - | - | - | - | 100.6287 | -
Panhandle | U3CT1_B | Interface MW | 3239.4001 | 3240.4382 | - | - | - | - | - | 100.032 | -
Panhandle | U3GSU1_B | Interface MW | 3239.4001 | 3246.3206 | - | - | - | - | - | 100.2136 | -
Panhandle | U3GSU2_B | Interface MW | 3239.4001 | 3241.1741 | - | - | - | - | - | 100.0548 | -
Panhandle | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | Interface MW | 3239.4001 | 3239.8184 | - | - | - | 100.0129 | - | 101.263 | -
Panhandle | VENUS_S5-MDLTHELP_S5 & VENUS_N5-MDLTHELP_N5 (DOUBLE B TO B) | Interface MW | 3239.4001 | 3280.3142 | - | - | - | 100.0129 | - | 101.263 | -
Panhandle | VIKING_CON | Interface MW | 3239.4001 | 3242.2776 | - | - | - | - | - | 100.0888 | -
Panhandle | WILLOW CREEK - WISE TRACTEBEL 345 KV (DOUBLE B TO B) | Interface MW | 3239.4001 | 3258.9395 | - | - | - | - | - | 100.6032 | -
Panhandle | WOLF HOLLOW-WOLF HOLLOW_C0_C1_TRAIN 345 KV (SINGLE B TO B) | Interface MW | 3239.4001 | 3250.7568 | - | - | - | - | - | 100.3506 | -
Panhandle | WOLF HOLLOW-WOLF HOLLOW_C2_345 KV (SINGLE B TO B) | Interface MW | 3239.4001 | 3242.3464 | - | - | - | - | - | 100.091 | -
Panhandle | XFMR-CALFRESTN_5-4 | Interface MW | 3239.4001 | 3239.5039 | - | - | - | - | - | 100.0032 | -
Panhandle | XFMR-CALFRESTN_5-5 | Interface MW | 3239.4001 | 3239.5034 | - | - | - | - | - | 100.0032 | -
Panhandle | XFMR-CALFRESTN_5-6 | Interface MW | 3239.4001 | 3240.1648 | - | - | - | - | - | 100.0236 | -
Panhandle | XFMR-ENNSTRAC_8-1 | Interface MW | 3239.4001 | 3241.6804 | - | - | - | - | - | 100.0704 | -
Panhandle | XFMR-GRHAMSES1_8-1 | Interface MW | 3239.4001 | 3242.4468 | - | - | - | - | - | 100.094 | -
Panhandle | XFMR-HANDLEYC_8-1 | Interface MW | 3239.4001 | 3246.9722 | - | - | - | - | - | 100.2337 | -
Panhandle | XFMR-HANDLEYC_8-3 | Interface MW | 3239.4001 | 3248.8333 | - | - | - | - | - | 100.2912 | -
Panhandle | XFMR-HANDLEYD_8-2 | Interface MW | 3239.4001 | 3248.9775 | - | - | - | - | - | 100.2957 | -
Panhandle | XFMR-LKHB_1T8-1 | Interface MW | 3239.4001 | 3247.5166 | - | - | - | - | - | 100.2506 | -
Panhandle | XFMR-LKHB_2T8-2 | Interface MW | 3239.4001 | 3251.5647 | - | - | - | - | - | 100.3755 | -
Panhandle | XFMR-MARTINLK_5-1 | Interface MW | 3239.4001 | 3257.615 | - | - | - | - | - | 100.5623 | -
Panhandle | XFMR-MARTINLK_5-2 | Interface MW | 3239.4001 | 3257.6318 | - | - | - | - | - | 100.5628 | -
Panhandle | XFMR-MARTINLK_5-3 | Interface MW | 3239.4001 | 3257.8005 | - | - | - | - | - | 100.568 | -
Panhandle | XFMR-MDLTHELP_5-5 | Interface MW | 3239.4001 | 3242.7808 | - | - | - | - | - | 100.1044 | -
Panhandle | XFMR-MDLTHELP_5-6 | Interface MW | 3239.4001 | 3242.8389 | - | - | - | - | - | 100.1062 | -
Panhandle | XFMR-MDLTHELP_N5-3 | Interface MW | 3239.4001 | 3242.9707 | - | - | - | - | - | 100.1102 | -
Panhandle | XFMR-MDLTHELP_N5-4 | Interface MW | 3239.4001 | 3242.9692 | - | - | - | - | - | 100.1102 | -
Panhandle | XFMR-MDLTHELP_S5-1 | Interface MW | 3239.4001 | 3242.417 | - | - | - | - | - | 100.0931 | -
Panhandle | XFMR-MDLTHELP_S5-2 | Interface MW | 3239.4001 | 3242.9004 | - | - | - | - | - | 100.1081 | -
Panhandle | XFMR-MTCK_8T8-8 | Interface MW | 3239.4001 | 3253.3135 | - | - | - | - | - | 100.4295 | -
Panhandle | XFMR-MTENTRPR_5G-1 | Interface MW | 3239.4001 | 3239.6028 | - | - | - | - | - | 100.0063 | -
Panhandle | XFMR-MTENTRPR_5G-3 | Interface MW | 3239.4001 | 3239.5208 | - | - | - | - | - | 100.0037 | -
Panhandle | XFMR-MTENTRPR_5G-4 | Interface MW | 3239.4001 | 3246.3608 | - | - | - | - | - | 100.2149 | -
Panhandle | XFMR-SANDYCRK_5-01 | Interface MW | 3239.4001 | 3262.595 | - | - | - | - | - | 100.716 | -
Panhandle | XFMR-STRYKER_8-2 | Interface MW | 3239.4001 | 3249.1724 | - | - | - | - | - | 100.3017 | -
Panhandle | XFMR-STRYKERND_8-1 | Interface MW | 3239.4001 | 3239.8989 | - | - | - | - | - | 100.0154 | -
Panhandle | XFMR-WHCCS2_4-1 | Interface MW | 3239.4001 | 3245.332 | - | - | - | - | - | 100.1831 | -
Panhandle | XFMR-WHCCS2_5-1 | Interface MW | 3239.4001 | 3258.9939 | - | - | - | - | - | 100.6049 | -
Panhandle | XFMR-WLFHMDPT_5-1 | Interface MW | 3239.4001 | 3250.7568 | - | - | - | - | - | 100.3506 | -
Panhandle | XFMR-WLFHOSTR-3 | Interface MW | 3239.4001 | 3242.3464 | - | - | - | - | - | 100.091 | -
Panhandle | YELLOW_WOLF_CON | Interface MW | 3239.4001 | 3245.082 | - | - | - | - | - | 100.1754 | -
South Texas Export Pawnee-Spruce | BEPC_001 | Interface MW | 540.6 | 542.8284 | - | 100.4122 | - | - | - | - | -
South Texas Export Pawnee-Spruce | Pre-contingency | Interface | 540.6 | 682.9294 | 126.328 | - | - | - | - | - | -

## Unsolved
Zones | Contingency | Duplicate Con Name | 2026sum | 2027min | 2027sum | 2029sum | 2030sum | 2030sum_EHV | Notes
COAST | E_FORMOSA_CC1_TRAIN | P1.1 | X | X | X | X | X | - | -
COAST | L_008715RADIANT7A-008728COBRA7AC1 | P1.2 | - | - | - | - | X | - | -
COAST | L_110120DOWGEN_1_8-110128DOWGEN_3_8CSG | P1.2 | X | X | X | X | X | X | -
COAST | L_110127DOWGEN_2_8-110128DOWGEN_3_8CSG | P1.2 | X | - | X | X | - | - | -
COAST | P7-1_E1>>T6060E | P7.1 | - | - | X | X | X | X | -
COAST, SOUTH_CE | E5DVA1C1_1_B_2 | P7.1 | - | - | - | - | X | - | -
COAST, SOUTH_CE | G8DVA1C1_B | P7.1 | - | CON Skipped | - | CON Skipped | X | - | -
COAST, SOUTH_CE | P7-1_E1>>T1827GX_ERC | P7.1 | CON Skipped | CON Skipped | CON Skipped | - | X | - | -
COAST, SOUTHERN | L_008728COBRA7A-081003HABER7AC1 | P1.2 | - | - | - | - | X | - | -
EAST | BRYN_9995DC | P7.1 | - | - | - | - | X | X | -
EAST | L_032851BRYN_LENRDRD-032862BRYN_ATK138C1 | P1.2 | - | - | - | - | X | X | -
EAST | MARTIN LAKE - ELKTON - & MARTIN LAKE - TYLER GRANDE (DOUBLE B TO B)-2 | P7.1 | - | - | - | - | X | - | -
EAST | ML-SHAM*AUT (DOUBLE B TO B) | P7.1 | - | - | - | - | X | X | -
EAST, NORTH_CE | TR-TC1 (DOUBLE B TO B)_B | P7.1 | - | - | - | - | X | - | -
FAR_WEST | COALSON DRAW - SAND LAKE DCKT 138 KV SUM 2025 - FUTURE (DOUBLE B TO B) | P7.1 | - | - | X | X | X | X | -
FAR_WEST | L_001323BIGSPRIG_9-001351BSPGGULF_9C1 | P1.2 | X | - | X | X | X | X | -
FAR_WEST | L_006535BIGLAKE4A-900052Other_115C1 | P1.2 | - | - | - | X | X | X | -
FAR_WEST | L_010035LONGSHRE_8-023853EILAND_8C1 | P1.2 | CON not in case | CON not in case | X | X | X | X | -
FAR_WEST | L_010035LONGSHRE_8-900100Other_131C1 | P1.2 | CON not in case | CON not in case | X | X | X | X | -
FAR_WEST | L_011083RIVERTON_8-011180ARYOBLUFF_T8C1 | P1.2 | - | - | - | X | X | - | -
FAR_WEST | L_023853EILAND_8-900100Other_131C1 | P1.2 | X | X | CON not in case | CON not in case | CON not in case | CON not in case | -
FAR_WEST | L_038430TNWHITEBKR1-131453KEO_2_8C1 | P1.2 | X | X | X | X | X | X | -
FAR_WEST | L201000320-A | P1.2,P2.2_HV | CON not in case | - | X | X | X | X | -
FAR_WEST | New Girvin - Whitebk double Ckt | P7.1 | X | X | X | X | X | X | -
FAR_WEST | T_006628FTST2A-006630FTST4AC1 | P1.3 | - | - | - | X | X | X | -
FAR_WEST, WEST | CHAMPION CREEK - SWEETWATER EAST & BITTER CREEK - CATTLEMEN 345 KV SUM 2026 - FUTURE (DOUBLE B TO B) | P7.1 | CON not in case | X | X | X | X | X | -
FAR_WEST, WEST | L_006036YUCCA4A-006525ESMERALD4AC1 | P1.2 | - | - | - | X | X | X | -
NORTH | AJSWOPE-DEAFSMITH/WINDMILL (DOUBLE B TO B) SUM 2028 - FUTURE | P7.1 | CON Skipped | CON not in case | X | X | X | X | -
NORTH | P7/C5-ONCOR-7 A SUM 2028 -FUTURE | P7.1 | X | CON Skipped | CON Skipped | CON Skipped | CON Skipped | CON Skipped | -
NORTH_CE | Batchler Rd Switch-Elrod Switch/Big Onion Levee Switch 345 kV Line(Double B TO B) new load | P7.1 | - | - | - | - | X | - | -
NORTH_CE | Batchler Rd Switch-Watermill Switch 345 kV Line(Double B TO B) new load | P7.1 | - | - | - | - | X | - | -
NORTH_CE | BEPC_306 | P1.2 | - | - | X | X | X | X | -
NORTH_CE | KNOBCRK_SS_5-SALADO_SS_5 & TEMP_SS_8-BELL_CNTY_8 (LCRA) (DOUBLE B TO B) | P7.1 | - | - | - | - | X | - | -
NORTH_CE | L_000442RAILPORT-001303FORBESRD_8C1 | P1.2 | - | - | - | X | X | X | -
NORTH_CE | L_000442RAILPORT-001908VENUSC1 | P1.2 | - | - | - | X | X | X | -
NORTH_CE | L_001908VENUS-002303KEMPRNCH_8C1 | P1.2 | - | - | X | X | X | X | -
NORTH_CE | L_037245BRDG_RC-037280TNCLIMAX__0C1 | P1.2 | - | - | - | X | X | X | -
NORTH_CE | L_037255TNTHISTLE_1-037260TNCLIMAX__1C1 | P1.2 | X | - | X | X | X | X | -
NORTH_CE | L_888888FEWELL_S1-003634GROES_SE1_8C1 | P1.2 | X | - | X | X | X | X | -
NORTH_CE | SAM VENUS/FORT SMITH DCKT (DOUBLE B TO B) new load | P7.1 | - | - | - | - | X | - | -
NORTH_CE | STERRETT-SARDIS/DESOTO 138KV DCKT (DOULBE B TO B) | P7.1 | - | - | - | - | X | X | -
NORTH_CE | T_037280TNCLIMAX__0-037260TNCLIMAX__1C2 | P1.3 | X | - | X | X | X | X | -
NORTH_CE | TRICORNER - WATERMILL (DOUBLE B TO B) B | P7.1 | CON Skipped | CON Skipped | CON Skipped | CON Skipped | X | - | -
NORTH_CE | VENUS - SAM/FORT SMITH DCKT (DOUBLE B TO B) new load | P7.1 | - | - | - | - | X | - | -
NORTH_CE, SOUTH_CE | HUTTO SS - SALADO SS_5 (DOUBLE B TO B ) | P7.1 | - | - | - | - | X | - | -
NORTH_CE, SOUTH_CE | KNOBCRK_SS_5-SALADO_SS_5 & BELL_CNTY_8 (LCRA) - GABRIEL_8 (LCRA) (DOUBLE B TO B) B | P7.1 | - | - | - | - | X | - | -
SOUTH_CE | E5DVA1C1_1_B | P7.1 | - | - | - | - | X | - | -
SOUTHERN | Haber - Coleto Creek | P7.1 | CON not in case | CON not in case | CON not in case | - | X | - | -
SOUTHERN | L_008318RIOHONDO7A-008704GULCH7AC1 | P1.2 | - | - | - | X | X | X | -
SOUTHERN | L_008535POMPANO4A-079601STILLMANC1 | P1.2 | - | - | - | X | X | X | -
SOUTHERN | L_008704GULCH7A-08709CANDELA7AC1 | P1.2 | CON not in case | CON not in case | - | X | X | X | -